## Front
SUBMITTAL DATA
Moduleflex eFurnaceTM
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Unit Size
|  | AEFE3A00S1HH2 | AEFE4B00S1HG2 | AEFE5C00S1HR2 | AEFE5D00S1HT2
Blower Data: | Motor Type | 5-speed ECM motor | 5-speed ECM motor | 5-speed ECM motor | 5-speed ECM motor
| Motor H.P. | 1/2 | 3/4 | 1 | 1
| F.L.A. | 5.8 | 8.7 | 11.1 | 11.1
Nominal CFM |  | 400 - 1200 | 800 - 1600 | 1000 - 1800 | 1200 - 2000
Max Unit Weight (lbs) |  | 84 | 105 | 80 | 80
Available Voltages |  | 120 V, 60 Hz, 1 Ph | 120 V, 60 Hz, 1 Ph | 120 V, 60 Hz, 1 Ph | 120 V, 60 Hz, 1 Ph
Transformer Size and Type |  | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2
Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
True Replacement for an existing gas furnace
Multi-position- Up-flow downflow, and horizontal left or right airflow
Industry standard A,B,C,D cabinet widths
Compact design for tight spaces – only 30” tall
120 Volt to use existing service in a gas furnace replacement
Perfectly matches ADP multi-position, downflow, and horizontal cased coils.
Bottom and side return capable (both sides)
Painted front panel available to match coil color
Cabinet lined with high quality 5/8" foil faced insulation
Slide-out blower assemblies for easy access to blower motor
Certified to 1.4% or less cabinet air leakage as per ASHRAE 193-210
Dynamically balanced blowers for quiet, vibration-free operation
120V 60Hz, 1 Phase, 5-speed high-efficiency ECM motor
Terminal board with screw down connections for thermostat wiring
10-year limited warranty available.
Product registration required.
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
Moduleflex eFurnaceTM
Dimensions
Air Handler Size | Cabinet Width (in) |  |  | Inlet Width (in) |  |  | Outlet Width (in)
AEFE3A00S1HH2 | 36 |  |  | 22 |  |  | 15
AEFE4B00S1HG2 | 36 |  |  | 22 |  |  | 15
AEFE5C00S1HR2 | 41 |  |  | 22 |  |  | 18.5
AEFE5D00S1HT2 | 41 |  |  | 22 |  |  | 18.5
Airflow (CFM) vs. External Static Pressure (inches W.C.)
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
AEFE3A00S1HH2 | 1 | 692 | 642 | 588 | 538 | 491 | 414 | 353 | 298 | 263 | -
| 2 | 876 | 831 | 797 | 757 | 716 | 675 | 635 | 596 | 554 | 498
| 3 | 1066 | 1029 | 994 | 966 | 935 | 903 | 869 | 839 | 806 | 773
| 4+ | 1189 | 1151 | 1117 | 1091 | 1065 | 1041 | 1010 | 981 | 953 | 923
| 5* | 1378 | 1343 | 1314 | 1288 | 1263 | 1246 | 1218 | 1195 | 1169 | 1145
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
AEFE4B00S1HG2 | 1 | 1097 | 1048 | 996 | 953 | 909 | 861 | 815 | 765 | 716 | 656
| 2 | 1307 | 1259 | 1214 | 1181 | 1142 | 1105 | 1064 | 1025 | 989 | 950
| 3 | 1481 | 1438 | 1397 | 1363 | 1335 | 1303 | 1266 | 1234 | 1202 | 1168
| 4+ | 1656 | 1614 | 1582 | 1555 | 1523 | 1490 | 1460 | 1429 | 1399 | 1371
| 5* | 1767 | 1727 | 1692 | 1655 | 1623 | 1592 | 1564 | 1533 | 1502 | 1471
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
AEFE5C00S1HR2 | 1 | 1525 | 1458 | 1394 | 1339 | 1286 | 1228 | 1167 | 1106 | 1038 | 962
| 2 | 1693 | 1638 | 1584 | 1530 | 1475 | 1420 | 1372 | 1316 | 1259 | 1207
| 3 | 2079 | 2033 | 1982 | 1951 | 1905 | 1858 | 1820 | 1781 | 1741 | 1698
| 4+ | 1845 | 1795 | 1743 | 1691 | 1639 | 1592 | 1542 | 1491 | 1439 | 1388
| 5* | 2223 | 2156 | 2104 | 2055 | 2011 | 1981 | 1930 | 1887 | 1847 | 1801
Unit Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
AEFE5D00S1HT2 | 1 | 1438 | 1388 | 1335 | 1286 | 1240 | 1192 | 1138 | 1088 | 1033 | 978
| 2 | 1610 | 1560 | 1522 | 1480 | 1430 | 1381 | 1340 | 1292 | 1245 | 1201
| 3 | 1964 | 1922 | 1886 | 1866 | 1831 | 1791 | 1760 | 1724 | 1688 | 1651
| 4+ | 1779 | 1740 | 1705 | 1664 | 1624 | 1578 | 1544 | 1504 | 1460 | 1416
| 5* | 2089 | 2037 | 1997 | 1959 | 1924 | 1898 | 1859 | 1822 | 1783 | 1747
1. All data is given while modular blower is operating without a DX coil and without filter.
2. Speed tap 3 is factory set cooling speed.
3. Speed taps marked with an asterisk (*) denote highest cooling speeds.
4. Speed taps marketed with a plus sign (+) denote highest heating speed

## Nomenclature (hidden)
AEF | E |  | 3 |  | A |  | 00 |  | S | 1 |  | H |  | H |  | 2
Series | Blower Motor |  | Size / Airflow |  | Cabinet Width |  | Electric Heat |  | Line Voltage Connection | Voltage |  | Cabinet Color | Revision | Front Panel Color | Revision | Revision | Revision
AEF | E: | 5-speed ECM motor | 3: | 3 Ton / 600-1200 CFM | A: | 14.25" | 00: | No heat | S: Stripped wire | 1: | 120 V, 60 Hz, 1 ph. | H: | Galvanized | H: | Galvanized
|  |  | 4: | 4 Ton / 1000-1600 CFM | B: | 17.5" | [7 empty] | A: | Armstrong
|  |  | 5: | 5 Ton / 1400-2000 CFM | C: | 21.0" | [7 empty] | G: | ICP
[5 empty] | D: | 24.5" | [7 empty] | J: | Goodman/Amana
[14 empty] | N: | Nordyne
[14 empty] | P: | Carrier/Bryant/Payne
[14 empty] | R: | Rheem/Ruud
[14 empty] | T: | Trane/American Std.
[14 empty] | Y: | York/Luxaire/Coleman

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model) | Width | Side Color | Front Color
AEFE3A00S1HH2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Galvanized
AEFE3A00S1HA2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Armstrong
AEFE3A00S1HG2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | ICP
AEFE3A00S1HJ2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Goodman/Amana
AEFE3A00S1HN2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Nordyne
AEFE3A00S1HP2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Carrier/Bryant/Payne
AEFE3A00S1HR2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Rheem/Ruud
AEFE3A00S1HT2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | Trane/American std.
AEFE3A00S1HY2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 3 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1/2 | 5.8 | 400 - 1200 | 84 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 14.25 | Galvanized | York/Luxaire/Coleman
AEFE4B00S1HH2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Galvanized
AEFE4B00S1HA2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Armstrong
AEFE4B00S1HG2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | ICP
AEFE4B00S1HJ2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Goodman/Amana
AEFE4B00S1HN2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Nordyne
AEFE4B00S1HP2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Carrier/Bryant/Payne
AEFE4B00S1HR2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Rheem/Ruud
AEFE4B00S1HT2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | Trane/American std.
AEFE4B00S1HY2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 4 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 3/4 | 8.7 | 800 - 1600 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 17.5 | Galvanized | York/Luxaire/Coleman
AEFE5C00S1HH2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Galvanized
AEFE5C00S1HA2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Armstrong
AEFE5C00S1HG2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | ICP
AEFE5C00S1HJ2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Goodman/Amana
AEFE5C00S1HN2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Nordyne
AEFE5C00S1HP2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 105 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Carrier/Bryant/Payne
AEFE5C00S1HR2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Rheem/Ruud
AEFE5C00S1HT2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | Trane/American std.
AEFE5C00S1HY2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1000 - 1800 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 21 | Galvanized | York/Luxaire/Coleman
AEFE5D00S1HH2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Galvanized
AEFE5D00S1HA2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Armstrong
AEFE5D00S1HG2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | ICP
AEFE5D00S1HJ2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Goodman/Amana
AEFE5D00S1HN2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Nordyne
AEFE5D00S1HP2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Carrier/Bryant/Payne
AEFE5D00S1HR2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Rheem/Ruud
AEFE5D00S1HT2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | Trane/American std.
AEFE5D00S1HY2 | AEF Series | 5-speed ECM motor | N/A | N/A | N/A | 5 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (ECM only) | 2 | N/A | N/A | 1 | 11.1 | 1200 - 2000 | 80 | 120 V, 60 Hz, 1 Ph | none | 40 VA, Class 2 | N/A | N/A | 1 | 24.5 | Galvanized | York/Luxaire/Coleman

## Airflow (hidden)
ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Voltage/Motor
3_14.25_120 V, 60 Hz, 1 ph. (ECM only)_1 | AEFE3A* | 1 | 692 | 642 | 588 | 538 | 491 | 414 | 353 | 298 | 263 | - | 208/240 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
3_14.25_120 V, 60 Hz, 1 ph. (ECM only)_2 |  | 2 | 876 | 831 | 797 | 757 | 716 | 675 | 635 | 596 | 554 | 498 | 120 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
3_14.25_120 V, 60 Hz, 1 ph. (ECM only)_3 |  | 3 | 1066 | 1029 | 994 | 966 | 935 | 903 | 869 | 839 | 806 | 773 | 208/240 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
3_14.25_120 V, 60 Hz, 1 ph. (ECM only)_4 |  | 4+ | 1189 | 1151 | 1117 | 1091 | 1065 | 1041 | 1010 | 981 | 953 | 923 | 120 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1.0
3_14.25_120 V, 60 Hz, 1 ph. (ECM only)_5 |  | 5* | 1378 | 1343 | 1314 | 1288 | 1263 | 1246 | 1218 | 1195 | 1169 | 1145
4_17.5_120 V, 60 Hz, 1 ph. (ECM only)_1 | AEFE4B* | 1 | 1097 | 1048 | 996 | 953 | 909 | 861 | 815 | 765 | 716 | 656
4_17.5_120 V, 60 Hz, 1 ph. (ECM only)_2 |  | 2 | 1307 | 1259 | 1214 | 1181 | 1142 | 1105 | 1064 | 1025 | 989 | 950
4_17.5_120 V, 60 Hz, 1 ph. (ECM only)_3 |  | 3 | 1481 | 1438 | 1397 | 1363 | 1335 | 1303 | 1266 | 1234 | 1202 | 1168
4_17.5_120 V, 60 Hz, 1 ph. (ECM only)_4 |  | 4+ | 1656 | 1614 | 1582 | 1555 | 1523 | 1490 | 1460 | 1429 | 1399 | 1371
4_17.5_120 V, 60 Hz, 1 ph. (ECM only)_5 |  | 5* | 1767 | 1727 | 1692 | 1655 | 1623 | 1592 | 1564 | 1533 | 1502 | 1471
5_21_120 V, 60 Hz, 1 ph. (ECM only)_1 | AEFE5C* | 1 | 1525 | 1458 | 1394 | 1339 | 1286 | 1228 | 1167 | 1106 | 1038 | 962
5_21_120 V, 60 Hz, 1 ph. (ECM only)_2 |  | 2 | 1693 | 1638 | 1584 | 1530 | 1475 | 1420 | 1372 | 1316 | 1259 | 1207
5_21_120 V, 60 Hz, 1 ph. (ECM only)_3 |  | 3 | 2079 | 2033 | 1982 | 1951 | 1905 | 1858 | 1820 | 1781 | 1741 | 1698
5_21_120 V, 60 Hz, 1 ph. (ECM only)_4 |  | 4+ | 1845 | 1795 | 1743 | 1691 | 1639 | 1592 | 1542 | 1491 | 1439 | 1388
5_21_120 V, 60 Hz, 1 ph. (ECM only)_5 |  | 5* | 2223 | 2156 | 2104 | 2055 | 2011 | 1981 | 1930 | 1887 | 1847 | 1801
5_24.5_120 V, 60 Hz, 1 ph. (ECM only)_1 | AEFE5C* | 1 | 1438 | 1388 | 1335 | 1286 | 1240 | 1192 | 1138 | 1088 | 1033 | 978
5_24.5_120 V, 60 Hz, 1 ph. (ECM only)_2 |  | 2 | 1610 | 1560 | 1522 | 1480 | 1430 | 1381 | 1340 | 1292 | 1245 | 1201
5_24.5_120 V, 60 Hz, 1 ph. (ECM only)_3 |  | 3 | 1964 | 1922 | 1886 | 1866 | 1831 | 1791 | 1760 | 1724 | 1688 | 1651
5_24.5_120 V, 60 Hz, 1 ph. (ECM only)_4 |  | 4+ | 1779 | 1740 | 1705 | 1664 | 1624 | 1578 | 1544 | 1504 | 1460 | 1416
5_24.5_120 V, 60 Hz, 1 ph. (ECM only)_5 |  | 5* | 2089 | 2037 | 1997 | 1959 | 1924 | 1898 | 1859 | 1822 | 1783 | 1747

## Dim (hidden)
Unit size | Cabinet Width | Inlet Width | Outlet Width
3_14.25 | 36 | 22 | 15
4_17.5 | 36 | 22 | 15
5_21 | 41 | 22 | 18.5
5_24.5 | 41 | 22 | 18.5