{"text_format":"1","workbook":"xlsx","n_sheets":23,"sheets":["notes","Options","Calcs","AL8B_24","AL8B_36","AL8B_48","AL8B_60","TCJD_18","TCJD_24","TCJD_30","TCJD_36","TCJD_42","TCJD_48","TCJD_60","TCJF_24","TCJF_30","TCJF_36","TCJF_42","TCJF_48","TCJF_60","Form","Instructions","Prompt"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":0,"defined_names":7,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"notes","index":0,"n_rows":65,"n_cols":16,"rows_kept":65,"cut":false,"hidden":true,"merged":[]}
[]
[null,null,null,null,null,null,null,{"$f":"SUM(H3:H8)","v":0}]
[null,null,600,24,600,1000,{"$f":"IF(Form!$D$4=D3,1,0)","v":0},{"$f":"IF(G3=1,IF(OR(E3>Form!M$5,F3<Form!M$5),1,0),0)","v":0}]
[null,null,800,30,800,1200,{"$f":"IF(Form!$D$4=D4,1,0)","v":0},{"$f":"IF(G4=1,IF(OR(E4>Form!M$5,F4<Form!M$5),1,0),0)","v":0}]
[null,null,1000,36,1000,1400,{"$f":"IF(Form!$D$4=D5,1,0)","v":0},{"$f":"IF(G5=1,IF(OR(E5>Form!M$5,F5<Form!M$5),1,0),0)","v":0}]
[null,null,1200,42,1200,1600,{"$f":"IF(Form!$D$4=D6,1,0)","v":0},{"$f":"IF(G6=1,IF(OR(E6>Form!M$5,F6<Form!M$5),1,0),0)","v":0}]
[null,null,1400,48,1400,1800,{"$f":"IF(Form!$D$4=D7,1,0)","v":0},{"$f":"IF(G7=1,IF(OR(E7>Form!M$5,F7<Form!M$5),1,0),0)","v":0}]
[null,null,1600,60,1600,2000,{"$f":"IF(Form!$D$4=D8,1,0)","v":0},{"$f":"IF(G8=1,IF(OR(E8>Form!M$5,F8<Form!M$5),1,0),0)","v":0}]
[null,null,1800]
[null,null,2000]
[]
[]
[null,null,null,"Total"]
[null,{"$f":"Form!M5+Form!M6","v":0},null,null,{"$f":"E31","v":0},{"$f":"F31","v":0},0,0,0,0,0,{"$f":"SUM(E14:K14)","v":0},null,null,null,58]
[null,null,null,null,{"$f":"Form!C27","v":65},{"$f":"Form!E27","v":75},{"$f":"Form!G27","v":85},{"$f":"Form!I27","v":95},{"$f":"Form!K27","v":105},{"$f":"Form!M27","v":115},{"$f":"Form!O27","v":125}]
[{"$f":"C16+D16","v":0},{"$f":"P16","v":0},{"$f":"Form!A31","v":0},{"$f":"Form!B31","v":0},{"$f":"Form!C31","v":0},{"$f":"Form!E31","v":0},{"$f":"Form!G31","v":0},{"$f":"Form!I31","v":0},{"$f":"Form!K31","v":0},{"$f":"Form!M31","v":0},{"$f":"Form!O31","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C16+D16=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A16<L16,1,0)","v":0},{"$f":"IF(A16>L16,2,0)","v":0},{"$f":"IF(AND(N16=1,N17=0),1,0)+IF(AND(O15=0,O16=2),2,0)","v":0}]
[{"$f":"C17+D17","v":0},{"$f":"P17","v":0},{"$f":"C16","v":0},{"$f":"Form!B32","v":0},{"$f":"Form!C32","v":0},{"$f":"Form!E32","v":0},{"$f":"Form!G32","v":0},{"$f":"Form!I32","v":0},{"$f":"Form!K32","v":0},{"$f":"Form!M32","v":0},{"$f":"Form!O32","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C17+D17=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A17<L17,1,0)","v":0},{"$f":"IF(A17>L17,2,0)","v":0},{"$f":"IF(AND(N17=1,N18=0),1,0)+IF(AND(O16=0,O17=2),2,0)","v":0}]
[0,0,{"$f":"C17","v":0},{"$f":"Form!B33","v":0},{"$f":"Form!C33","v":0},{"$f":"Form!E33","v":0},{"$f":"Form!G33","v":0},{"$f":"Form!I33","v":0},{"$f":"Form!K33","v":0},{"$f":"Form!M33","v":0},{"$f":"Form!O33","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C18+D18=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A18>L18,2,0)","v":0},{"$f":"IF(AND(N18=1,N19=0),1,0)+IF(AND(O17=0,O18=2),2,0)","v":0}]
[0,0,{"$f":"C18","v":0},{"$f":"Form!B34","v":0},{"$f":"Form!C34","v":0},{"$f":"Form!E34","v":0},{"$f":"Form!G34","v":0},{"$f":"Form!I34","v":0},{"$f":"Form!K34","v":0},{"$f":"Form!M34","v":0},{"$f":"Form!O34","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C19+D19=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A19>L19,2,0)","v":0},{"$f":"IF(AND(N19=1,N20=0),1,0)+IF(AND(O18=0,O19=2),2,0)","v":0}]
[0,0,{"$f":"Form!A35","v":0},{"$f":"Form!B35","v":0},{"$f":"Form!C35","v":0},{"$f":"Form!E35","v":0},{"$f":"Form!G35","v":0},{"$f":"Form!I35","v":0},{"$f":"Form!K35","v":0},{"$f":"Form!M35","v":0},{"$f":"Form!O35","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C20+D20=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A20>L20,2,0)","v":0},{"$f":"IF(AND(N20=1,N21=0),1,0)+IF(AND(O19=0,O20=2),2,0)","v":0}]
[0,0,{"$f":"C20","v":0},{"$f":"Form!B36","v":0},{"$f":"Form!C36","v":0},{"$f":"Form!E36","v":0},{"$f":"Form!G36","v":0},{"$f":"Form!I36","v":0},{"$f":"Form!K36","v":0},{"$f":"Form!M36","v":0},{"$f":"Form!O36","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C21+D21=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A21>L21,2,0)","v":0},{"$f":"IF(AND(N21=1,N22=0),1,0)+IF(AND(O20=0,O21=2),2,0)","v":0}]
[0,0,{"$f":"C21","v":0},{"$f":"Form!B37","v":0},{"$f":"Form!C37","v":0},{"$f":"Form!E37","v":0},{"$f":"Form!G37","v":0},{"$f":"Form!I37","v":0},{"$f":"Form!K37","v":0},{"$f":"Form!M37","v":0},{"$f":"Form!O37","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C22+D22=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C22","v":0},{"$f":"Form!B38","v":0},{"$f":"Form!C38","v":0},{"$f":"Form!E38","v":0},{"$f":"Form!G38","v":0},{"$f":"Form!I38","v":0},{"$f":"Form!K38","v":0},{"$f":"Form!M38","v":0},{"$f":"Form!O38","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C23+D23=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"Form!A39","v":0},{"$f":"Form!B39","v":0},{"$f":"Form!C39","v":0},{"$f":"Form!E39","v":0},{"$f":"Form!G39","v":0},{"$f":"Form!I39","v":0},{"$f":"Form!K39","v":0},{"$f":"Form!M39","v":0},{"$f":"Form!O39","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C24+D24=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C24","v":0},{"$f":"Form!B40","v":0},{"$f":"Form!C40","v":0},{"$f":"Form!E40","v":0},{"$f":"Form!G40","v":0},{"$f":"Form!I40","v":0},{"$f":"Form!K40","v":0},{"$f":"Form!M40","v":0},{"$f":"Form!O40","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C25+D25=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C25","v":0},{"$f":"Form!B41","v":0},{"$f":"Form!C41","v":0},{"$f":"Form!E41","v":0},{"$f":"Form!G41","v":0},{"$f":"Form!I41","v":0},{"$f":"Form!K41","v":0},{"$f":"Form!M41","v":0},{"$f":"Form!O41","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C26+D26=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C26","v":0},{"$f":"Form!B42","v":0},{"$f":"Form!C42","v":0},{"$f":"Form!E42","v":0},{"$f":"Form!G42","v":0},{"$f":"Form!I42","v":0},{"$f":"Form!K42","v":0},{"$f":"Form!M42","v":0},{"$f":"Form!O42","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C27+D27=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,{"$f":"SUM(B16:B27)","v":0}]
[null,null,null,null,null,{"$f":"IF(AND(F15>Form!$M$4,E15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(G15>Form!$M$4,F15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(H15>Form!$M$4,G15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(I15>Form!$M$4,H15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(J15>Form!$M$4,I15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(K15>Form!$M$4,J15<Form!$M$4),2,0)","v":0}]
[null,null,{"$f":"HLOOKUP(1,E14:K15,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"IF(F29=2,1,0)","v":0},{"$f":"IF(G29=2,1,0)","v":0},0,0,0,0,0]
[null,null,{"$f":"HLOOKUP(2,E14:K15,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"SUM(E29:E30)","v":0},0,0,0,0,0,0]
[null,{"$f":"(VLOOKUP(1,B14:K27,3,FALSE))","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B32),0,B32)","v":0},null,{"$f":"(C34-C35)/(C32-C33)*(Form!$M$6-C33)+C35","v":{"$error":"#N/A"}},{"$f":"(C36-C37)/(C32-C33)*(Form!M6-C33)+C37","v":{"$error":"#N/A"}}]
[null,{"$f":"VLOOKUP(2,B14:K27,3,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B33),0,B33)","v":0},null,{"$f":"IF(AND(B28=0,L14=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A14:K27,MATCH(1,notes!A14:K14,FALSE),FALSE),0)","v":0},{"$f":"IF(AND(B28=0,L14=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A14:K27,MATCH(2,notes!A14:K14,FALSE),FALSE),0)","v":0},null,null,"exactly"]
[null,{"$f":"VLOOKUP(1,B14:K27,MATCH(1,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B34,B36)","v":{"$error":"#N/A"}},null,{"$f":"IF(ISERROR(E32),E33,E32)","v":0},{"$f":"IF(ISERROR(F32),F33,F32)","v":0},null,null,"x","y","err1","err2","err3","ans"]
[null,{"$f":"VLOOKUP(2,B14:K27,MATCH(1,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B35,B37)","v":{"$error":"#N/A"}},null,{"$f":"MIN(E34:F34)","v":0},{"$f":"MAX(E34:F34)","v":0},null,null,"y","y",{"$f":"IF(ISERROR(VLOOKUP(Form!$M$5+Form!$M$6,notes!A15:K27,MATCH(Form!$M$4,notes!A15:K15,FALSE),FALSE)),0,VLOOKUP(Form!$M$5+Form!$M$6,notes!A15:K27,MATCH(Form!$M$4,notes!A15:K15,FALSE),FALSE))","v":0},null,null,{"$f":"SUM(K35:M35)","v":0}]
[null,{"$f":"VLOOKUP(1,B14:K27,MATCH(2,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B36,B34)","v":{"$error":"#N/A"}},null,{"$f":"(E35-F35)/(C31-C30)*(Form!$M$4-C30)+F35","v":{"$error":"#N/A"}},null,null,null,"y","n",null,null,null,{"$f":"SUM(K36:M36)","v":0}]
[null,{"$f":"VLOOKUP(2,B14:K27,MATCH(2,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B35,B37)","v":{"$error":"#N/A"}},null,null,null,null,null,"n","n",{"$f":"IF(OR(E36>100000,E36<=0),0,E36)","v":{"$error":"#N/A"}},{"$f":"IF(K37<>0,0,MIN(E32:F32))","v":{"$error":"#N/A"}},{"$f":"IF(AND(L37=0,K37=0),C34,0)","v":{"$error":"#N/A"}},{"$f":"SUM(K37:M37)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(ISERROR(N37),N35,N37)","v":0}]
[]
[]
["sens",null,null,null,{"$f":"E58","v":0},{"$f":"F58","v":0},0,0,0,0,0,{"$f":"SUM(E41:K41)","v":0}]
[null,null,null,null,{"$f":"E15","v":65},{"$f":"F15","v":75},85,95,105,115,125]
[{"$f":"C43+D43","v":0},{"$f":"P43","v":0},{"$f":"C16","v":0},{"$f":"D16","v":0},{"$f":"Form!D31","v":0},{"$f":"Form!F31","v":0},{"$f":"Form!H31","v":0},{"$f":"Form!J31","v":0},{"$f":"Form!L31","v":0},{"$f":"Form!N31","v":0},{"$f":"Form!P31","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C43+D43=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A43<L43,1,0)","v":0},{"$f":"IF(A43>L43,2,0)","v":0},{"$f":"IF(AND(N43=1,N44=0),1,0)+IF(AND(O42=0,O43=2),2,0)","v":0}]
[{"$f":"C44+D44","v":0},{"$f":"P44","v":0},{"$f":"C17","v":0},{"$f":"D17","v":0},{"$f":"Form!D32","v":0},{"$f":"Form!F32","v":0},{"$f":"Form!H32","v":0},{"$f":"Form!J32","v":0},{"$f":"Form!L32","v":0},{"$f":"Form!N32","v":0},{"$f":"Form!P32","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C44+D44=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A44<L44,1,0)","v":0},{"$f":"IF(A44>L44,2,0)","v":0},{"$f":"IF(AND(N44=1,N45=0),1,0)+IF(AND(O43=0,O44=2),2,0)","v":0}]
[{"$f":"C45+D45","v":0},0,0,0,{"$f":"Form!D33","v":0},{"$f":"Form!F33","v":0},{"$f":"Form!H33","v":0},{"$f":"Form!J33","v":0},{"$f":"Form!L33","v":0},{"$f":"Form!N33","v":0},{"$f":"Form!P33","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C45+D45=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A45>L45,2,0)","v":0},{"$f":"IF(AND(N45=1,N46=0),1,0)+IF(AND(O44=0,O45=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D34","v":0},{"$f":"Form!F34","v":0},{"$f":"Form!H34","v":0},{"$f":"Form!J34","v":0},{"$f":"Form!L34","v":0},{"$f":"Form!N34","v":0},{"$f":"Form!P34","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C46+D46=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A46>L46,2,0)","v":0},{"$f":"IF(AND(N46=1,N47=0),1,0)+IF(AND(O45=0,O46=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D35","v":0},{"$f":"Form!F35","v":0},{"$f":"Form!H35","v":0},{"$f":"Form!J35","v":0},{"$f":"Form!L35","v":0},{"$f":"Form!N35","v":0},{"$f":"Form!P35","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C47+D47=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A47>L47,2,0)","v":0},{"$f":"IF(AND(N47=1,N48=0),1,0)+IF(AND(O46=0,O47=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D36","v":0},{"$f":"Form!F36","v":0},{"$f":"Form!H36","v":0},{"$f":"Form!J36","v":0},{"$f":"Form!L36","v":0},{"$f":"Form!N36","v":0},{"$f":"Form!P36","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C48+D48=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A48>L48,2,0)","v":0},{"$f":"IF(AND(N48=1,N49=0),1,0)+IF(AND(O47=0,O48=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D37","v":0},{"$f":"Form!F37","v":0},{"$f":"Form!H37","v":0},{"$f":"Form!J37","v":0},{"$f":"Form!L37","v":0},{"$f":"Form!N37","v":0},{"$f":"Form!P37","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C49+D49=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D38","v":0},{"$f":"Form!F38","v":0},{"$f":"Form!H38","v":0},{"$f":"Form!J38","v":0},{"$f":"Form!L38","v":0},{"$f":"Form!N38","v":0},{"$f":"Form!P38","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C50+D50=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D39","v":0},{"$f":"Form!F39","v":0},{"$f":"Form!H39","v":0},{"$f":"Form!J39","v":0},{"$f":"Form!L39","v":0},{"$f":"Form!N39","v":0},{"$f":"Form!P39","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C51+D51=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D40","v":0},{"$f":"Form!F40","v":0},{"$f":"Form!H40","v":0},{"$f":"Form!J40","v":0},{"$f":"Form!L40","v":0},{"$f":"Form!N40","v":0},{"$f":"Form!P40","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C52+D52=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D41","v":0},{"$f":"Form!F41","v":0},{"$f":"Form!H41","v":0},{"$f":"Form!J41","v":0},{"$f":"Form!L41","v":0},{"$f":"Form!N41","v":0},{"$f":"Form!P41","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C53+D53=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D42","v":0},{"$f":"Form!F42","v":0},{"$f":"Form!H42","v":0},{"$f":"Form!J42","v":0},{"$f":"Form!L42","v":0},{"$f":"Form!N42","v":0},{"$f":"Form!P42","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C54+D54=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,{"$f":"SUM(B43:B54)","v":0}]
[null,null,null,null,null,{"$f":"IF(AND(F42>Form!$M$4,E42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(G42>Form!$M$4,F42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(H42>Form!$M$4,G42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(I42>Form!$M$4,H42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(J42>Form!$M$4,I42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(K42>Form!$M$4,J42<Form!$M$4),2,0)","v":0}]
[null,null,{"$f":"HLOOKUP(1,E41:K42,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"IF(F56=2,1,0)","v":0},{"$f":"IF(G56=2,1,0)","v":0},0,0,0,0,0]
[null,null,{"$f":"HLOOKUP(2,E41:K42,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"SUM(E56:E57)","v":0},0,0,0,0,0,0]
[null,{"$f":"(VLOOKUP(1,B41:K54,3,FALSE))","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B59),0,B59)","v":0},null,{"$f":"(C61-C62)/(C59-C60)*(Form!$M$6-C60)+C62","v":{"$error":"#N/A"}},{"$f":"(C63-C64)/(C59-C60)*(Form!M6-C60)+C64","v":{"$error":"#N/A"}}]
[null,{"$f":"VLOOKUP(2,B41:K54,3,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B60),0,B60)","v":0},null,{"$f":"IF(AND(B55=0,L41=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A41:K54,MATCH(1,notes!A41:K41,FALSE),FALSE),0)","v":0},{"$f":"IF(AND(B55=0,L41=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A41:K54,MATCH(2,notes!A41:K41,FALSE),FALSE),0)","v":0},null,null,"exactly"]
[null,{"$f":"VLOOKUP(1,B41:K54,MATCH(1,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B61,B63)","v":{"$error":"#N/A"}},null,{"$f":"IF(ISERROR(E59),E60,E59)","v":0},{"$f":"IF(ISERROR(F59),F60,F59)","v":0},null,null,"x","y","err1","err2","err3","ans"]
[null,{"$f":"VLOOKUP(2,B41:K54,MATCH(1,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B62,B64)","v":{"$error":"#N/A"}},null,{"$f":"MIN(E61:F61)","v":0},{"$f":"MAX(E61:F61)","v":0},null,null,"y","y",{"$f":"IF(ISERROR(VLOOKUP(Form!$M$5+Form!$M$6,notes!A42:K54,MATCH(Form!$M$4,notes!A42:K42,FALSE),FALSE)),0,VLOOKUP(Form!$M$5+Form!$M$6,notes!A42:K54,MATCH(Form!$M$4,notes!A42:K42,FALSE),FALSE))","v":0},null,null,{"$f":"SUM(K62:M62)","v":0}]
[null,{"$f":"VLOOKUP(1,B41:K54,MATCH(2,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B63,B61)","v":{"$error":"#N/A"}},null,{"$f":"(E62-F62)/(C58-C57)*(Form!$M$4-C57)+F62","v":{"$error":"#N/A"}},null,null,null,"y","n",null,null,null,{"$f":"SUM(K63:M63)","v":0}]
[null,{"$f":"VLOOKUP(2,B41:K54,MATCH(2,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B62,B64)","v":{"$error":"#N/A"}},null,null,null,null,null,"n","n",{"$f":"IF(OR(E63>100000,E63<=0),0,E63)","v":{"$error":"#N/A"}},{"$f":"IF(K64<>0,0,MIN(E59:F59))","v":{"$error":"#N/A"}},{"$f":"IF(AND(L64=0,K64=0),C61,0)","v":{"$error":"#N/A"}},{"$f":"SUM(K64:M64)","v":{"$error":"#N/A"}}]
[null,{"$f":"VLOOKUP(Form!M32+Form!M33,A41:K54,MATCH(2,A41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(ISERROR(N64),N62,N64)","v":0}]

{"sheet":"Options","index":1,"n_rows":3,"n_cols":1,"rows_kept":3,"cut":false,"hidden":true,"merged":[]}
["AL8B"]
["TCJD"]
["TCJF"]

{"sheet":"Calcs","index":2,"n_rows":21,"n_cols":7,"rows_kept":21,"cut":false,"hidden":true,"merged":[[0,4,0,9],[1,4,1,9]]}
[null,null,null,"York Condenser :  ","TCGD36"]
[null,null,null,"ADP Evaporator:  "]
[null,null,null,"Condenser Entering Air Temperature: ",100,"(°F) Dry Bulb, 65°F to 125°F"]
[null,null,null,"Evaporator Air Flow:",1265,"CFM"]
[null,null,null,"Entering Evaporator Air (DB):  ",77.5,"(°F) Dry Bulb"]
[null,null,null,"Entering Evaporator Air (WB):  ",60.6,"(°F) Wet Bulb, 57°F to 72°F"]
[]
[]
["Total"]
[28.549999999999997,"1200 60.6"]
[]
[null,"Diff 200",{"$f":"A10-A14","v":0.30799999999999983},"Diff 1 cfm",{"$f":"C12/200","v":1.5399999999999991E-3},"  1265 total",{"$f":"A10-(65*E12)","v":28.449899999999996}]
[]
[28.241999999999997,"1400 60.6"]
[]
["Sens"]
[25.319999999999997,"1200 60.6"]
[]
[null,"Diff 200",{"$f":"A17-A21","v":0.55439999999999756},"Diff 1 cfm",{"$f":"C19/200","v":2.771999999999988E-3},"  1265 Sens",{"$f":"A17-(65*E19)","v":25.139819999999997}]
[]
[24.765599999999999,"1400 60.6"]

{"sheet":"AL8B_24","index":3,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["AL8B24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":22.463414634146339},{"$f":"IF(AM8>C8,C8,AM8)","v":10.609756097560973},{"$f":"S8*$I$13","v":21.365853658536583},{"$f":"IF(AN8>E8,E8,AN8)","v":10.24390243902439},{"$f":"T8*$I$13","v":20.268292682926827},{"$f":"IF(AO8>G8,G8,AO8)","v":9.9512195121951201},{"$f":"U8*$I$13","v":19.170731707317071},{"$f":"IF(AP8>I8,I8,AP8)","v":9.5853658536585353},{"$f":"V8*$I$13","v":17.926829268292682},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.2195121951219505},{"$f":"W8*$I$13","v":16.756097560975608},{"$f":"IF(AR8>M8,M8,AR8)","v":8.7804878048780477},{"$f":"X8*$I$13","v":15.585365853658537},{"$f":"IF(AS8>O8,O8,AS8)","v":8.4146341463414647},null,1.2479674796747966,1.186991869918699,1.1260162601626016,1.065040650406504,0.99593495934959342,0.93089430894308933,0.86585365853658536,0.47231270358306188,0.47945205479452058,0.49097472924187724,0.5,0.51428571428571423,0.5240174672489083,0.539906103286385,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.609756097560973},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.24390243902439},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.9512195121951201},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.5853658536585353},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.2195121951219505},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.7804878048780477},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.4146341463414647}]
[null,67,20.926829268292682,13.390243902439025,19.829268292682926,{"$f":"IF(AN9>E9,E9,AN9)","v":13.024390243902438},18.73170731707317,{"$f":"IF(AO9>G9,G9,AO9)","v":12.658536585365853},{"$f":"U9*$I$13","v":17.560975609756099},{"$f":"IF(AP9>I9,I9,AP9)","v":12.29268292682927},16.536585365853657,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.926829268292682},15.512195121951217,{"$f":"IF(AR9>M9,M9,AR9)","v":11.560975609756097},14.487804878048779,{"$f":"IF(AS9>O9,O9,AS9)","v":11.195121951219511},null,1.1626016260162602,1.1016260162601625,1.0406504065040649,0.97560975609756095,0.91869918699186992,0.86178861788617878,0.80487804878048774,0.6398601398601399,0.65682656826568264,0.67578125,0.70000000000000007,0.72123893805309736,0.74528301886792458,0.77272727272727271,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.390243902439025},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.024390243902438},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.658536585365853},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.29268292682927},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.926829268292682},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.560975609756097},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.195121951219511}]
[null,62,18.804878048780488,15.658536585365852,17.780487804878049,15.292682926829269,16.756097560975608,14.92682926829268,{"$f":"U10*$I$13","v":15.73170731707317},14.634146341463413,14.853658536585366,13.902439024390244,14.048780487804876,13.24390243902439,13.170731707317072,12.585365853658535,null,1.0447154471544715,0.98780487804878048,0.93089430894308933,0.8739837398373983,0.82520325203252032,0.7804878048780487,0.73170731707317072,0.83268482490272366,0.86008230452674894,0.89082969432314407,0.93023255813953487,0.93596059113300489,0.94270833333333348,0.95555555555555549,1.06,1.06,1.06,1.06,1.06,1.06,1.06,15.658536585365852,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.292682926829269},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.92682926829268},14.634146341463413,13.902439024390244,13.24390243902439,12.585365853658535]
[null,57,16.902439024390244,16.536585365853657,16.463414634146339,16.024390243902435,15.95121951219512,15.585365853658535,{"$f":"U11*$I$13","v":15.512195121951217},15.073170731707316,14.707317073170733,14.268292682926829,13.902439024390244,13.536585365853659,13.097560975609754,12.73170731707317,null,0.9390243902439025,0.91463414634146334,0.88617886178861782,0.86178861788617878,0.81707317073170738,0.77235772357723576,0.72764227642276413,0.97835497835497831,0.97333333333333327,0.97706422018348627,0.97169811320754729,0.9701492537313432,0.97368421052631582,0.97206703910614523,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.536585365853657,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.024390243902435},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":15.585365853658535},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.073170731707316},14.268292682926829,13.536585365853659,12.73170731707317]
[800,72,22.756097560975608,11.195121951219512,21.73170731707317,10.829268292682928,20.634146341463413,10.463414634146341,{"$f":"U12*$I$13","v":19.536585365853657},10.024390243902438,18.292682926829265,9.6585365853658516,17.121951219512191,9.2195121951219487,15.95121951219512,8.8536585365853657,null,1.2642276422764227,1.2073170731707317,1.1463414634146341,1.0853658536585364,1.0162601626016259,0.9512195121951218,0.88617886178861782,0.49196141479099681,0.49831649831649838,0.50709219858156029,0.51310861423220977,0.52800000000000002,0.53846153846153844,0.55504587155963303,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.195121951219512},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.829268292682928},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.463414634146341},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.024390243902438},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.6585365853658516},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.2195121951219487},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.8536585365853657}]
[null,67,21.073170731707314,13.975609756097562,20.048780487804876,13.682926829268292,19.024390243902438,13.463414634146339,18,13.170731707317072,16.829268292682926,12.658536585365853,15.73170731707317,12.219512195121951,14.634146341463413,11.780487804878048,null,1.1707317073170731,1.1138211382113821,1.056910569105691,1,0.93495934959349591,0.8739837398373983,0.81300813008130079,0.66319444444444453,0.68248175182481752,0.70769230769230762,0.73170731707317072,0.75217391304347825,0.77674418604651163,0.80500000000000005,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.975609756097562},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.682926829268292},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.463414634146339},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.170731707317072},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.658536585365853},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.219512195121951},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.780487804878048}]
[null,62,19.024390243902438,16.902439024390244,18.073170731707314,16.390243902439021,17.121951219512191,15.804878048780486,{"$f":"U14*$I$13","v":16.170731707317074},15.292682926829267,15.292682926829267,14.487804878048779,14.414634146341463,13.756097560975611,13.536585365853657,13.024390243902438,null,1.056910569105691,1.0040650406504064,0.9512195121951218,0.89837398373983746,0.84959349593495925,0.80081300813008127,0.75203252032520318,0.88846153846153852,0.90688259109311742,0.92307692307692324,0.94570135746606321,0.94736842105263164,0.95431472081218283,0.96216216216216222,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.902439024390244,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.390243902439021},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.804878048780486},15.292682926829267,14.487804878048779,13.756097560975611,13.024390243902438]
[null,57,17.780487804878049,17.414634146341463,17.195121951219512,16.829268292682926,16.536585365853657,16.170731707317071,15.95121951219512,15.585365853658535,15.073170731707318,14.707317073170733,14.268292682926829,13.902439024390244,13.463414634146339,13.097560975609754,null,0.98780487804878048,0.95528455284552838,0.91869918699186992,0.88617886178861782,0.83739837398373984,0.79268292682926822,0.7479674796747966,0.97942386831275718,0.97872340425531912,0.97787610619469023,0.97706422018348627,0.97572815533980584,0.97435897435897434,0.97282608695652173,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.414634146341463,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":16.829268292682926},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.170731707317071},15.585365853658535,14.707317073170733,13.902439024390244,13.097560975609754]
[900,72,23.121951219512194,11.780487804878049,22.024390243902438,11.341463414634145,20.999999999999996,10.97560975609756,19.90243902439024,10.536585365853657,18.658536585365855,10.097560975609758,17.487804878048777,9.6585365853658516,16.243902439024389,9.2195121951219505,null,1.2845528455284552,1.2235772357723578,1.1666666666666665,1.1056910569105689,1.0365853658536586,0.97154471544715437,0.90243902439024382,0.509493670886076,0.51495016611295674,0.52264808362369342,0.52941176470588236,0.54117647058823537,0.55230125523012552,0.56756756756756754,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.780487804878049},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.341463414634145},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.97560975609756},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.536585365853657},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.097560975609758},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.6585365853658516},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.2195121951219505}]
[null,67,21.146341463414629,14.634146341463412,20.195121951219509,14.414634146341459,19.317073170731703,14.195121951219509,18.439024390243901,13.975609756097562,17.195121951219512,13.463414634146339,15.95121951219512,12.878048780487804,14.780487804878048,12.365853658536585,null,1.1747967479674795,1.121951219512195,1.0731707317073169,1.024390243902439,0.95528455284552838,0.88617886178861782,0.82113821138211374,0.69204152249134954,0.71376811594202894,0.73484848484848486,0.75793650793650802,0.78297872340425523,0.80733944954128445,0.8366336633663366,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.634146341463412},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.414634146341459},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.195121951219509},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.975609756097562},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.463414634146339},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.878048780487804},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.365853658536585}]
[null,62,19.243902439024389,18.146341463414632,18.365853658536583,17.414634146341459,17.414634146341463,16.609756097560975,16.463414634146339,15.878048780487802,15.658536585365852,14.999999999999998,14.780487804878048,14.195121951219511,13.975609756097562,13.390243902439025,null,1.0691056910569106,1.0203252032520325,0.9674796747967479,0.91463414634146334,0.86991869918699172,0.82113821138211374,0.77642276422764234,0.94296577946768056,0.94820717131474097,0.95378151260504196,0.96444444444444444,0.95794392523364491,0.96039603960396036,0.95811518324607325,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.146341463414632,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.414634146341459},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":16.609756097560975},15.878048780487802,14.999999999999998,14.195121951219511,13.390243902439025]
[null,57,18.658536585365855,18.292682926829269,17.926829268292682,17.560975609756095,17.121951219512191,16.756097560975604,16.390243902439021,16.024390243902435,15.512195121951217,15.146341463414631,14.634146341463413,14.341463414634147,13.829268292682926,13.463414634146339,null,1.0365853658536586,0.99593495934959342,0.9512195121951218,0.91056910569105676,0.86178861788617878,0.81300813008130079,0.76829268292682917,0.98039215686274506,0.97959183673469385,0.9786324786324786,0.9776785714285714,0.97641509433962259,0.98000000000000009,0.97354497354497349,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.292682926829269,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":17.560975609756095},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":16.756097560975604},16.024390243902435,15.146341463414631,14.341463414634147,13.463414634146339]

{"sheet":"AL8B_36","index":4,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["AL8B36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1100,72,{"$f":"R8*$I$13","v":22.524590163934423},{"$f":"IF(AM8>C8,C8,AM8)","v":10.426229508196721},{"$f":"S8*$I$13","v":21.442622950819672},{"$f":"IF(AN8>E8,E8,AN8)","v":10.131147540983607},{"$f":"T8*$I$13","v":20.409836065573771},{"$f":"IF(AO8>G8,G8,AO8)","v":9.8360655737704921},{"$f":"U8*$I$13","v":19.377049180327866},{"$f":"IF(AP8>I8,I8,AP8)","v":9.5409836065573757},{"$f":"V8*$I$13","v":18.196721311475411},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.1475409836065591},{"$f":"W8*$I$13","v":17.065573770491802},{"$f":"IF(AR8>M8,M8,AR8)","v":8.8032786885245891},{"$f":"X8*$I$13","v":15.934426229508194},{"$f":"IF(AS8>O8,O8,AS8)","v":8.4590163934426226},null,1.2513661202185791,1.1912568306010929,1.1338797814207651,1.076502732240437,1.0109289617486339,0.94808743169398912,0.88524590163934413,0.46288209606986902,0.47247706422018348,0.48192771084337349,0.49238578680203043,0.50270270270270279,0.51585014409221897,0.53086419753086422,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.426229508196721},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.131147540983607},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.8360655737704921},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.5409836065573757},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.1475409836065591},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.8032786885245891},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.4590163934426226}]
[null,67,20.262295081967217,13.229508196721312,19.42622950819672,{"$f":"IF(AN9>E9,E9,AN9)","v":12.786885245901637},18.590163934426226,{"$f":"IF(AO9>G9,G9,AO9)","v":12.393442622950818},{"$f":"U9*$I$13","v":17.754098360655739},{"$f":"IF(AP9>I9,I9,AP9)","v":11.950819672131148},16.57377049180328,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.606557377049182},15.393442622950818,{"$f":"IF(AR9>M9,M9,AR9)","v":11.262295081967212},14.262295081967213,{"$f":"IF(AS9>O9,O9,AS9)","v":10.918032786885245},null,1.1256830601092898,1.0792349726775956,1.0327868852459015,0.98633879781420764,0.92076502732240439,0.85519125683060104,0.79234972677595628,0.65291262135922323,0.65822784810126578,0.66666666666666674,0.67313019390581719,0.70029673590504449,0.73162939297124596,0.76551724137931032,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.229508196721312},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.786885245901637},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.393442622950818},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.950819672131148},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.606557377049182},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.262295081967212},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":10.918032786885245}]
[null,62,18.737704918032787,15.688524590163933,17.950819672131146,15.295081967213115,17.21311475409836,14.901639344262295,{"$f":"U10*$I$13","v":16.42622950819672},14.459016393442621,15.491803278688524,13.967213114754097,14.557377049180328,13.524590163934427,13.622950819672131,13.032786885245901,null,1.040983606557377,0.99726775956284153,0.95628415300546443,0.91256830601092886,0.86065573770491799,0.80874316939890711,0.75683060109289613,0.837270341207349,0.852054794520548,0.86571428571428577,0.88023952095808378,0.90158730158730149,0.92905405405405406,0.95667870036101088,1.06,1.06,1.06,1.06,1.06,1.06,1.06,15.688524590163933,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.295081967213115},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.901639344262295},14.459016393442621,13.967213114754097,13.524590163934427,13.032786885245901]
[null,57,17.557377049180328,16.967213114754095,17.016393442622952,16.524590163934427,16.524590163934427,16.032786885245901,{"$f":"U11*$I$13","v":15.983606557377049},15.540983606557377,15.098360655737704,14.704918032786884,14.262295081967213,13.918032786885247,13.42622950819672,13.131147540983605,null,0.97540983606557385,0.94535519125683065,0.91803278688524592,0.88797814207650272,0.83879781420765021,0.79234972677595628,0.74590163934426224,0.96638655462184864,0.97109826589595372,0.97023809523809523,0.97230769230769232,0.97394136807817588,0.9758620689655173,0.97802197802197799,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.967213114754095,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.524590163934427},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.032786885245901},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.540983606557377},14.704918032786884,13.918032786885247,13.131147540983605]
[1200,72,22.672131147540984,10.868852459016395,21.590163934426229,10.524590163934425,20.557377049180328,10.131147540983608,{"$f":"U12*$I$13","v":19.475409836065577},9.7868852459016402,18.295081967213115,9.3442622950819665,17.163934426229506,8.9508196721311464,16.032786885245901,8.5573770491803263,null,1.2595628415300546,1.1994535519125682,1.1420765027322404,1.0819672131147542,1.0163934426229508,0.95355191256830596,0.89071038251366119,0.47939262472885036,0.48747152619589973,0.49282296650717711,0.50252525252525249,0.510752688172043,0.52148997134670483,0.53374233128834347,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.868852459016395},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.524590163934425},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.131147540983608},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.7868852459016402},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.3442622950819665},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.9508196721311464},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.5573770491803263}]
[null,67,20.508196721311478,13.622950819672132,19.672131147540981,13.278688524590162,18.83606557377049,12.934426229508198,18,12.590163934426229,16.819672131147541,12.196721311475409,15.639344262295081,11.754098360655735,14.508196721311476,11.360655737704921,null,1.139344262295082,1.0928961748633879,1.0464480874316939,1,0.93442622950819676,0.86885245901639341,0.80601092896174864,0.66426858513189446,0.67500000000000004,0.68668407310704971,0.69945355191256831,0.72514619883040932,0.7515723270440251,0.78305084745762721,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.622950819672132},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.278688524590162},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":12.934426229508198},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.590163934426229},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.196721311475409},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.754098360655735},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.360655737704921}]
[null,62,19.229508196721312,16.42622950819672,18.393442622950822,16.032786885245905,17.557377049180328,15.639344262295081,{"$f":"U14*$I$13","v":16.721311475409834},15.245901639344261,15.737704918032787,14.557377049180328,14.852459016393441,13.868852459016392,13.918032786885245,13.180327868852459,null,1.0683060109289617,1.0218579234972678,0.97540983606557385,0.9289617486338797,0.87431693989071035,0.82513661202185784,0.77322404371584696,0.85421994884910479,0.87165775401069523,0.89075630252100835,0.91176470588235292,0.92500000000000004,0.93377483443708609,0.94699646643109536,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.42622950819672,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.032786885245905},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.639344262295081},15.245901639344261,14.557377049180328,13.868852459016392,13.180327868852459]
[null,57,18.295081967213115,17.754098360655735,17.655737704918032,17.114754098360653,17.016393442622952,16.524590163934427,16.377049180327866,15.885245901639342,15.491803278688524,15.049180327868852,14.606557377049178,14.262295081967212,13.770491803278688,13.42622950819672,null,1.0163934426229508,0.98087431693989058,0.94535519125683065,0.90983606557377039,0.86065573770491799,0.81147540983606548,0.76502732240437155,0.97043010752688164,0.96935933147632303,0.97109826589595372,0.96996996996996998,0.97142857142857142,0.97643097643097643,0.97499999999999998,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.754098360655735,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.114754098360653},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.524590163934427},15.885245901639342,15.049180327868852,14.262295081967212,13.42622950819672]
[1300,72,22.770491803278688,11.262295081967213,21.737704918032787,10.868852459016393,20.655737704918032,10.42622950819672,19.573770491803277,9.9836065573770494,18.393442622950822,9.5409836065573774,17.21311475409836,9.0983606557377055,16.081967213114755,8.6557377049180317,null,1.2650273224043715,1.2076502732240437,1.1475409836065573,1.0874316939890709,1.0218579234972678,0.95628415300546443,0.89344262295081966,0.49460043196544279,0.5,0.50476190476190474,0.51005025125628145,0.51871657754010692,0.52857142857142858,0.53822629969418956,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.262295081967213},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.868852459016393},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.42622950819672},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":9.9836065573770494},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":9.5409836065573774},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.0983606557377055},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":8.6557377049180317}]
[null,67,20.704918032786885,13.967213114754097,19.868852459016392,13.721311475409834,19.032786885245901,13.475409836065571,18.245901639344261,13.22950819672131,17.065573770491802,12.737704918032785,15.885245901639342,12.245901639344261,14.754098360655739,11.803278688524593,null,1.1502732240437159,1.1038251366120218,1.0573770491803278,1.0136612021857923,0.94808743169398912,0.88251366120218566,0.81967213114754101,0.67458432304037996,0.69059405940594054,0.70801033591731255,0.72506738544474392,0.74639769452449556,0.77089783281733748,0.8,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":13.967213114754097},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":13.721311475409834},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.475409836065571},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.22950819672131},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":12.737704918032785},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.245901639344261},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":11.803278688524593}]
[null,62,19.721311475409834,17.213114754098356,18.78688524590164,16.770491803278691,17.901639344262293,16.377049180327866,16.967213114754099,15.934426229508196,16.032786885245901,15.049180327868852,15.098360655737704,14.21311475409836,14.163934426229508,13.327868852459016,null,1.0956284153005464,1.0437158469945356,0.99453551912568294,0.94262295081967207,0.89071038251366119,0.83879781420765021,0.78688524590163933,0.87281795511221938,0.89267015706806285,0.9148351648351648,0.9391304347826086,0.93865030674846628,0.94136807817589574,0.94097222222222221,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.213114754098356,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":16.770491803278691},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":16.377049180327866},15.934426229508196,15.049180327868852,14.21311475409836,13.327868852459016]
[null,57,18.983606557377051,18.442622950819676,18.245901639344261,17.704918032786882,17.459016393442621,16.967213114754095,16.721311475409834,16.229508196721309,15.786885245901638,15.393442622950818,14.950819672131146,14.557377049180328,14.065573770491802,13.770491803278686,null,1.0546448087431695,1.0136612021857923,0.9699453551912568,0.9289617486338797,0.87704918032786883,0.83060109289617479,0.78142076502732238,0.97150259067357514,0.97035040431266839,0.971830985915493,0.97058823529411764,0.97507788161993769,0.97368421052631593,0.97902097902097895,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.442622950819676,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":17.704918032786882},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":16.967213114754095},16.229508196721309,15.393442622950818,14.557377049180328,13.770491803278686]

{"sheet":"AL8B_48","index":5,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["AL8B48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1500,72,{"$f":"R8*$I$13","v":21.832258064516129},{"$f":"IF(AM8>C8,C8,AM8)","v":11.496774193548386},{"$f":"S8*$I$13","v":20.748387096774195},{"$f":"IF(AN8>E8,E8,AN8)","v":11.109677419354838},{"$f":"T8*$I$13","v":19.703225806451609},{"$f":"IF(AO8>G8,G8,AO8)","v":10.761290322580644},{"$f":"U8*$I$13","v":18.658064516129034},{"$f":"IF(AP8>I8,I8,AP8)","v":10.412903225806451},{"$f":"V8*$I$13","v":17.49677419354839},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.9870967741935495},{"$f":"W8*$I$13","v":16.412903225806449},{"$f":"IF(AR8>M8,M8,AR8)","v":9.638709677419353},{"$f":"X8*$I$13","v":15.329032258064517},{"$f":"IF(AS8>O8,O8,AS8)","v":9.2516129032258068},null,1.2129032258064516,1.1526881720430109,1.0946236559139784,1.0365591397849463,0.97204301075268829,0.91182795698924723,0.85161290322580652,0.52659574468085102,0.53544776119402981,0.5461689587426326,0.55809128630705385,0.57079646017699115,0.58726415094339623,0.60353535353535348,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.496774193548386},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.109677419354838},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.761290322580644},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.412903225806451},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.9870967741935495},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.638709677419353},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.2516129032258068}]
[null,67,20.593548387096774,14.670967741935483,19.703225806451609,{"$f":"IF(AN9>E9,E9,AN9)","v":14.245161290322576},18.812903225806451,{"$f":"IF(AO9>G9,G9,AO9)","v":13.819354838709678},{"$f":"U9*$I$13","v":17.92258064516129},{"$f":"IF(AP9>I9,I9,AP9)","v":13.393548387096775},16.838709677419352,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.967741935483868},15.75483870967742,{"$f":"IF(AR9>M9,M9,AR9)","v":12.541935483870967},14.670967741935485,{"$f":"IF(AS9>O9,O9,AS9)","v":12.116129032258067},null,1.1440860215053763,1.0946236559139784,1.0451612903225806,0.99569892473118271,0.93548387096774188,0.87526881720430116,0.81505376344086022,0.71240601503759393,0.72298624754420426,0.73456790123456794,0.74730021598272145,0.77011494252873558,0.79606879606879599,0.8258575197889183,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":14.670967741935483},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":14.245161290322576},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.819354838709678},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":13.393548387096775},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.967741935483868},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.541935483870967},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.116129032258067}]
[null,62,19.316129032258061,17.380645161290321,18.464516129032258,16.954838709677418,17.612903225806452,16.490322580645163,{"$f":"U10*$I$13","v":16.8},16.06451612903226,15.870967741935484,15.212903225806452,14.980645161290322,14.4,14.090322580645161,13.587096774193549,null,1.0731182795698924,1.0258064516129033,0.978494623655914,0.93333333333333335,0.88172043010752688,0.83225806451612905,0.78279569892473111,0.8997995991983968,0.91823899371069173,0.93626373626373627,0.95622119815668205,0.95853658536585362,0.96124031007751942,0.96428571428571441,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.380645161290321,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.954838709677418},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":16.490322580645163},16.06451612903226,15.212903225806452,14.4,13.587096774193549]
[null,57,18.851612903225806,18.58064516129032,18.116129032258062,17.883870967741935,17.41935483870968,17.148387096774194,{"$f":"U11*$I$13","v":16.683870967741935},16.412903225806449,15.75483870967742,15.522580645161291,14.903225806451614,14.670967741935485,14.012903225806452,13.819354838709678,null,1.0473118279569893,1.0064516129032257,0.967741935483871,0.92688172043010753,0.87526881720430116,0.82795698924731187,0.77849462365591404,0.98562628336755642,0.98717948717948734,0.98444444444444434,0.98375870069605564,0.98525798525798525,0.98441558441558441,0.98618784530386738,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.58064516129032,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.883870967741935},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.148387096774194},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.412903225806449},15.522580645161291,14.670967741935485,13.819354838709678]
[1600,72,21.987096774193546,11.729032258064516,20.903225806451616,11.341935483870969,19.858064516129033,10.993548387096775,{"$f":"U12*$I$13","v":18.774193548387096},10.606451612903225,17.574193548387097,10.180645161290323,16.451612903225804,9.7935483870967737,15.329032258064517,9.4064516129032274,null,1.221505376344086,1.1612903225806452,1.1032258064516129,1.043010752688172,0.97634408602150535,0.91397849462365588,0.85161290322580652,0.53345070422535212,0.54259259259259263,0.5536062378167641,0.56494845360824741,0.57929515418502209,0.59529411764705886,0.61363636363636365,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.729032258064516},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.341935483870969},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.993548387096775},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.606451612903225},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.180645161290323},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.7935483870967737},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.4064516129032274}]
[null,67,21.058064516129033,15.096774193548388,20.051612903225806,14.670967741935483,19.006451612903227,14.206451612903226,18,13.780645161290323,16.916129032258066,13.316129032258065,15.832258064516129,12.89032258064516,14.787096774193548,12.464516129032258,null,1.1698924731182796,1.1139784946236559,1.0559139784946237,1,0.93978494623655917,0.87956989247311823,0.82150537634408605,0.71691176470588236,0.73166023166023164,0.74745417515274948,0.7655913978494624,0.78718535469107542,0.81418092909535444,0.84293193717277493,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":15.096774193548388},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.670967741935483},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.206451612903226},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.780645161290323},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.316129032258065},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.89032258064516},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.464516129032258}]
[null,62,19.509677419354837,17.92258064516129,18.658064516129034,17.419354838709676,17.845161290322583,16.916129032258066,{"$f":"U14*$I$13","v":16.993548387096773},16.412903225806453,16.064516129032256,15.522580645161289,15.135483870967743,14.632258064516128,14.24516129032258,13.780645161290323,null,1.0838709677419354,1.0365591397849463,0.99139784946236564,0.94408602150537635,0.89247311827956988,0.84086021505376352,0.79139784946236558,0.91865079365079361,0.93360995850622397,0.94793926247288507,0.96583143507972669,0.96626506024096392,0.96675191815856765,0.96739130434782616,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.92258064516129,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.419354838709676},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.916129032258066},16.412903225806453,15.522580645161289,14.632258064516128,13.780645161290323]
[null,57,19.2,18.929032258064513,18.425806451612903,18.154838709677417,17.651612903225807,17.380645161290321,16.838709677419352,16.64516129032258,15.948387096774194,15.716129032258065,15.058064516129033,14.864516129032259,14.167741935483871,13.974193548387097,null,1.0666666666666667,1.0236559139784946,0.98064516129032264,0.93548387096774188,0.88602150537634417,0.83655913978494623,0.7870967741935484,0.98588709677419351,0.98529411764705876,0.98464912280701744,0.9885057471264368,0.9854368932038835,0.98714652956298199,0.98633879781420764,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.929032258064513,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18.154838709677417},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.380645161290321},16.64516129032258,15.716129032258065,14.864516129032259,13.974193548387097]
[1700,72,22.14193548387097,11.961290322580647,21.058064516129033,11.574193548387095,19.974193548387095,11.187096774193547,18.890322580645158,10.799999999999999,17.651612903225807,10.374193548387098,16.451612903225804,9.9483870967741925,15.290322580645162,9.5225806451612911,null,1.2301075268817205,1.1698924731182796,1.1096774193548387,1.0494623655913977,0.98064516129032264,0.91397849462365588,0.84946236559139787,0.54020979020979021,0.54963235294117641,0.56007751937984496,0.57172131147540983,0.58771929824561409,0.6047058823529412,0.62278481012658227,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.961290322580647},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.574193548387095},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.187096774193547},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.799999999999999},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.374193548387098},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.9483870967741925},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.5225806451612911}]
[null,67,21.483870967741936,15.522580645161291,20.322580645161292,15.058064516129033,19.2,14.593548387096774,18.038709677419355,14.129032258064516,16.993548387096773,13.664516129032256,15.948387096774194,13.238709677419354,14.864516129032259,12.812903225806453,null,1.1935483870967742,1.1290322580645162,1.0666666666666667,1.0021505376344086,0.94408602150537635,0.88602150537634417,0.82580645161290323,0.72252252252252258,0.74095238095238092,0.76008064516129037,0.78326180257510725,0.80410022779043278,0.83009708737864074,0.86197916666666674,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.522580645161291},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.058064516129033},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.593548387096774},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.129032258064516},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.664516129032256},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.238709677419354},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.812903225806453}]
[null,62,19.703225806451609,18.4258064516129,18.890322580645158,17.883870967741935,18.038709677419355,17.341935483870966,17.187096774193549,16.761290322580646,16.219354838709677,15.793548387096774,15.290322580645162,14.864516129032259,14.361290322580645,13.93548387096774,null,1.0946236559139784,1.0494623655913977,1.0021505376344086,0.95483870967741935,0.90107526881720423,0.84946236559139787,0.7978494623655914,0.93516699410609039,0.94672131147540994,0.9613733905579398,0.97522522522522515,0.97374701670644392,0.97215189873417718,0.97035040431266839,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.4258064516129,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.883870967741935},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.341935483870966},16.761290322580646,15.793548387096774,14.864516129032259,13.93548387096774]
[null,57,19.548387096774192,19.238709677419354,18.696774193548386,18.425806451612903,17.883870967741938,17.651612903225811,17.032258064516128,16.838709677419356,16.103225806451615,15.909677419354841,15.21290322580645,15.019354838709676,14.283870967741933,14.129032258064514,null,1.086021505376344,1.0387096774193547,0.99354838709677429,0.94623655913978499,0.89462365591397852,0.84516129032258058,0.79354838709677411,0.98415841584158426,0.98550724637681164,0.98701298701298701,0.98863636363636365,0.98798076923076927,0.98727735368956748,0.98915989159891604,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.238709677419354,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.425806451612903},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.651612903225811},16.838709677419356,15.909677419354841,15.019354838709676,14.129032258064514]

{"sheet":"AL8B_60","index":6,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["AL8B60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":22.065517241379307},{"$f":"IF(AM8>C8,C8,AM8)","v":11.296551724137931},{"$f":"S8*$I$13","v":21.165517241379312},{"$f":"IF(AN8>E8,E8,AN8)","v":10.8},{"$f":"T8*$I$13","v":20.26551724137931},{"$f":"IF(AO8>G8,G8,AO8)","v":10.27241379310345},{"$f":"U8*$I$13","v":19.365517241379308},{"$f":"IF(AP8>I8,I8,AP8)","v":9.775862068965516},{"$f":"V8*$I$13","v":18.093103448275858},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3413793103448253},{"$f":"W8*$I$13","v":16.851724137931033},{"$f":"IF(AR8>M8,M8,AR8)","v":8.9068965517241363},{"$f":"X8*$I$13","v":15.610344827586205},{"$f":"IF(AS8>O8,O8,AS8)","v":8.503448275862068},null,1.2258620689655171,1.1758620689655173,1.1258620689655172,1.0758620689655172,1.0051724137931033,0.93620689655172407,0.86724137931034473,0.51195499296765123,0.51026392961876832,0.50689127105666165,0.50480769230769229,0.516295025728988,0.52854511970534068,0.54473161033797213,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.296551724137931},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.8},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.27241379310345},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.775862068965516},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3413793103448253},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.9068965517241363},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.503448275862068}]
[null,67,20.544827586206896,13.872413793103448,19.675862068965518,{"$f":"IF(AN9>E9,E9,AN9)","v":13.531034482758622},18.806896551724137,{"$f":"IF(AO9>G9,G9,AO9)","v":13.189655172413792},{"$f":"U9*$I$13","v":17.937931034482759},{"$f":"IF(AP9>I9,I9,AP9)","v":12.879310344827587},16.727586206896554,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.351724137931036},15.579310344827586,{"$f":"IF(AR9>M9,M9,AR9)","v":11.855172413793104},14.399999999999999,{"$f":"IF(AS9>O9,O9,AS9)","v":11.358620689655172},null,1.1413793103448275,1.0931034482758621,1.0448275862068965,0.99655172413793103,0.92931034482758623,0.86551724137931041,0.79999999999999993,0.67522658610271902,0.68769716088328081,0.70132013201320131,0.7179930795847751,0.73840445269016697,0.76095617529880477,0.78879310344827591,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.872413793103448},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.531034482758622},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.189655172413792},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.879310344827587},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.351724137931036},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.855172413793104},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.358620689655172}]
[null,62,18.931034482758619,16.665517241379309,18.155172413793103,16.293103448275861,17.348275862068967,15.920689655172415,{"$f":"U10*$I$13","v":16.541379310344826},15.548275862068966,15.455172413793102,14.80344827586207,14.36896551724138,14.089655172413794,13.282758620689654,13.282758620689654,null,1.0517241379310345,1.0086206896551724,0.96379310344827585,0.91896551724137931,0.85862068965517235,0.7982758620689655,0.73793103448275854,0.88032786885245906,0.89743589743589747,0.91771019677996424,0.93996247654784248,0.95783132530120496,0.98056155507559395,1.0093457943925235,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.665517241379309,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.293103448275861},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.920689655172415},15.548275862068966,14.80344827586207,14.089655172413794,13.406896551724138]
[null,57,17.720689655172414,17.720689655172414,17.162068965517239,17.162068965517239,16.634482758620692,16.634482758620692,{"$f":"U11*$I$13","v":16.075862068965517},16.075862068965517,15.082758620689656,15.082758620689656,14.151724137931035,14.151724137931035,13.220689655172414,13.220689655172414,null,0.98448275862068968,0.95344827586206893,0.92413793103448283,0.89310344827586197,0.83793103448275863,0.78620689655172415,0.73448275862068968,1.0175131348511384,1.0180831826401446,1.0167910447761195,1.0173745173745175,1.0185185185185184,1.0175438596491226,1.0187793427230045,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.031034482758621,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.472413793103446},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.913793103448278},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.355172413793102},15.36206896551724,14.399999999999999,13.468965517241378]
[1850,72,22.406896551724142,11.358620689655176,21.382758620689657,10.831034482758621,20.327586206896555,10.27241379310345,{"$f":"U12*$I$13","v":19.30344827586207},9.7448275862068972,18.062068965517245,9.3413793103448306,16.851724137931033,9,15.641379310344828,8.6275862068965523,null,1.2448275862068967,1.1879310344827587,1.1293103448275863,1.0724137931034483,1.0034482758620691,0.93620689655172407,0.86896551724137927,0.50692520775623273,0.50653120464441215,0.5053435114503817,0.50482315112540188,0.51718213058419249,0.53406998158379382,0.55158730158730163,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.358620689655176},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.831034482758621},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.27241379310345},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.7448275862068972},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.3413793103448306},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.6275862068965523}]
[null,67,20.731034482758616,14.213793103448273,19.831034482758621,13.841379310344829,18.900000000000002,13.500000000000002,18,13.127586206896551,16.789655172413795,12.600000000000003,15.610344827586205,12.072413793103447,14.431034482758621,11.544827586206898,null,1.1517241379310343,1.1017241379310345,1.05,1,0.9327586206896552,0.86724137931034473,0.80172413793103448,0.68562874251497008,0.69796557120500791,0.7142857142857143,0.72931034482758617,0.75046210720887252,0.77335984095427435,0.8,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.213793103448273},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.841379310344829},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.500000000000002},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.127586206896551},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.600000000000003},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.072413793103447},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.544827586206898}]
[null,62,19.055172413793102,16.975862068965515,18.248275862068965,16.603448275862071,17.441379310344828,16.262068965517241,{"$f":"U14*$I$13","v":16.634482758620692},15.920689655172414,15.548275862068966,15.113793103448277,14.493103448275862,14.337931034482759,13.437931034482759,13.437931034482759,null,1.0586206896551724,1.0137931034482759,0.96896551724137936,0.92413793103448283,0.86379310344827587,0.80517241379310345,0.74655172413793103,0.89087947882736163,0.90986394557823136,0.93238434163701056,0.95708955223880587,0.97205588822355293,0.98929336188436834,1.0092378752886837,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.975862068965515,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.603448275862071},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.262068965517241},15.920689655172414,15.113793103448277,14.337931034482759,13.562068965517243]
[null,57,18,18,17.379310344827587,17.379310344827587,16.789655172413795,16.789655172413795,16.2,16.2,15.237931034482758,15.237931034482758,14.306896551724137,14.306896551724137,13.375862068965517,13.375862068965517,null,1,0.96551724137931039,0.9327586206896552,0.9,0.84655172413793101,0.79482758620689653,0.74310344827586206,1.0172413793103448,1.0178571428571428,1.0184842883548983,1.0172413793103448,1.0183299389002036,1.0173535791757049,1.0185614849187934,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.310344827586206,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.689655172413794},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.100000000000001},16.479310344827585,15.517241379310343,14.555172413793102,13.624137931034481]
[1950,72,22.748275862068965,11.420689655172412,21.568965517241381,10.831034482758621,20.420689655172414,10.241379310344829,19.241379310344826,9.6827586206896541,18.031034482758621,9.341379310344827,16.820689655172416,9.0310344827586206,15.641379310344828,8.7517241379310349,null,1.2637931034482759,1.1982758620689655,1.1344827586206896,1.0689655172413792,1.0017241379310344,0.93448275862068975,0.86896551724137927,0.50204638472032737,0.50215827338129493,0.50151975683890582,0.50322580645161286,0.51807228915662651,0.53690036900368998,0.55952380952380953,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.420689655172412},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.831034482758621},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.241379310344829},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":9.6827586206896541},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":9.341379310344827},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.0310344827586206},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":8.7517241379310349}]
[null,67,20.886206896551727,14.524137931034485,19.955172413793104,14.151724137931037,18.993103448275864,13.779310344827588,18.062068965517245,13.406896551724142,16.820689655172416,12.817241379310344,15.641379310344828,12.289655172413795,14.431034482758621,11.73103448275862,null,1.1603448275862069,1.1086206896551725,1.0551724137931036,1.0034482758620691,0.93448275862068975,0.86896551724137927,0.80172413793103448,0.6953937592867756,0.70917573872472794,0.72549019607843135,0.74226804123711343,0.76199261992619916,0.78571428571428581,0.81290322580645158,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.524137931034485},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.151724137931037},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.779310344827588},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.406896551724142},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":12.817241379310344},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.289655172413795},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":11.73103448275862}]
[null,62,19.117241379310347,17.255172413793105,18.341379310344831,16.913793103448278,17.53448275862069,16.572413793103447,16.727586206896554,16.262068965517244,15.641379310344828,15.393103448275863,14.617241379310345,14.555172413793102,13.562068965517241,13.562068965517241,null,1.0620689655172415,1.0189655172413794,0.97413793103448276,0.92931034482758623,0.86896551724137927,0.81206896551724139,0.75344827586206897,0.90259740259740262,0.92216582064297803,0.94513274336283182,0.9721706864564007,0.98412698412698418,0.99575371549893832,1.0091533180778032,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.255172413793105,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":16.913793103448278},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":16.572413793103447},16.262068965517244,15.393103448275863,14.555172413793102,13.686206896551724]
[null,57,18.248275862068965,18.248275862068965,17.596551724137932,17.596551724137932,16.944827586206898,16.944827586206898,16.324137931034482,16.324137931034482,15.362068965517242,15.362068965517242,14.431034482758621,14.431034482758621,13.5,13.5,null,1.0137931034482759,0.97758620689655173,0.94137931034482758,0.90689655172413797,0.85344827586206895,0.80172413793103448,0.75,1.0170068027210883,1.0176366843033511,1.0183150183150182,1.0171102661596958,1.0181818181818181,1.0193548387096774,1.018390804597701,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.558620689655172,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":17.906896551724142},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.255172413793105},16.603448275862068,15.641379310344826,14.710344827586207,13.748275862068963]

{"sheet":"TCJD_18","index":7,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[450,72,{"$f":"R8*$I$13","v":20.468571428571426},{"$f":"IF(AM8>C8,C8,AM8)","v":9.5657142857142858},{"$f":"S8*$I$13","v":19.748571428571431},{"$f":"IF(AN8>E8,E8,AN8)","v":9.1542857142857166},{"$f":"T8*$I$13","v":19.028571428571428},{"$f":"IF(AO8>G8,G8,AO8)","v":8.8457142857142852},{"$f":"U8*$I$13","v":18.205714285714283},{"$f":"IF(AP8>I8,I8,AP8)","v":8.4342857142857124},{"$f":"V8*$I$13","v":16.971428571428572},{"$f":"IF(AQ8>K8,K8,AQ8)","v":8.1257142857142863},{"$f":"W8*$I$13","v":15.84},{"$f":"IF(AR8>M8,M8,AR8)","v":7.8171428571428558},{"$f":"X8*$I$13","v":14.605714285714285},{"$f":"IF(AS8>O8,O8,AS8)","v":7.508571428571428},null,1.137142857142857,1.0971428571428572,1.0571428571428572,1.0114285714285713,0.94285714285714284,0.88,0.81142857142857139,0.46733668341708551,0.46354166666666669,0.46486486486486484,0.4632768361581921,0.47878787878787882,0.49350649350649345,0.5140845070422535,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":9.5657142857142858},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":9.1542857142857166},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":8.8457142857142852},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":8.4342857142857124},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":8.1257142857142863},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":7.8171428571428558},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":7.508571428571428}]
[null,67,19.851428571428574,12.342857142857143,18.925714285714285,{"$f":"IF(AN9>E9,E9,AN9)","v":11.931428571428572},17.897142857142857,{"$f":"IF(AO9>G9,G9,AO9)","v":11.52},{"$f":"U9*$I$13","v":16.868571428571428},{"$f":"IF(AP9>I9,I9,AP9)","v":11.005714285714285},15.531428571428572,{"$f":"IF(AQ9>K9,K9,AQ9)","v":10.594285714285716},14.194285714285714,{"$f":"IF(AR9>M9,M9,AR9)","v":10.08},12.857142857142858,{"$f":"IF(AS9>O9,O9,AS9)","v":9.668571428571429},null,1.102857142857143,1.0514285714285714,0.99428571428571422,0.93714285714285706,0.86285714285714288,0.78857142857142859,0.7142857142857143,0.62176165803108807,0.63043478260869568,0.64367816091954022,0.65243902439024393,0.68211920529801329,0.71014492753623193,0.752,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.342857142857143},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":11.931428571428572},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":11.52},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.005714285714285},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":10.594285714285716},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":10.08},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":9.668571428571429}]
[null,62,18.30857142857143,14.194285714285716,17.28,13.988571428571428,16.251428571428573,13.782857142857143,{"$f":"U10*$I$13","v":15.222857142857144},13.474285714285715,14.091428571428571,12.857142857142856,12.959999999999999,12.24,11.725714285714286,11.52,null,1.0171428571428571,0.96000000000000008,0.90285714285714291,0.84571428571428575,0.78285714285714281,0.72,0.65142857142857147,0.7752808988764045,0.80952380952380942,0.84810126582278478,0.88513513513513509,0.91240875912408759,0.94444444444444453,0.98245614035087714,1.06,1.06,1.06,1.06,1.06,1.06,1.06,14.194285714285716,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":13.988571428571428},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":13.782857142857143},13.474285714285715,12.857142857142856,12.24,11.52]
[null,57,16.148571428571429,16.148571428571429,15.428571428571427,15.428571428571427,14.605714285714285,14.605714285714285,{"$f":"U11*$I$13","v":13.885714285714286},13.885714285714286,12.959999999999999,12.959999999999999,11.931428571428571,11.931428571428571,11.005714285714285,11.005714285714285,null,0.89714285714285713,0.8571428571428571,0.81142857142857139,0.77142857142857146,0.72,0.66285714285714281,0.61142857142857143,1.0191082802547771,1.02,1.0211267605633803,1.0222222222222224,1.015873015873016,1.0258620689655173,1.0280373831775702,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.457142857142859,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":15.737142857142857},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":14.914285714285713},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":14.194285714285718},13.165714285714287,12.24,11.314285714285715]
[600,72,20.777142857142856,10.08,19.954285714285714,9.8742857142857137,19.131428571428572,9.668571428571429,{"$f":"U12*$I$13","v":18.411428571428569},9.36,17.177142857142858,9.0514285714285734,15.942857142857143,8.8457142857142852,14.708571428571428,8.5371428571428574,null,1.1542857142857141,1.1085714285714285,1.0628571428571429,1.0228571428571427,0.95428571428571429,0.88571428571428568,0.81714285714285717,0.48514851485148519,0.49484536082474229,0.5053763440860215,0.5083798882681565,0.52694610778443118,0.55483870967741933,0.58041958041958042,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.08},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":9.8742857142857137},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":9.668571428571429},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.36},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.0514285714285734},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.8457142857142852},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.5371428571428574}]
[null,67,20.057142857142857,13.37142857142857,19.131428571428572,13.165714285714285,18.205714285714283,12.959999999999997,18,12.754285714285714,15.942857142857143,12.240000000000002,14.605714285714285,11.931428571428571,13.26857142857143,11.52,null,1.1142857142857143,1.0628571428571429,1.0114285714285713,1,0.88571428571428568,0.81142857142857139,0.73714285714285721,0.66666666666666663,0.68817204301075263,0.71186440677966101,0.70857142857142863,0.76774193548387104,0.81690140845070425,0.86821705426356577,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.37142857142857},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.165714285714285},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":12.959999999999997},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.754285714285714},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.240000000000002},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.931428571428571},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.52}]
[null,62,18.925714285714285,16.354285714285716,18,16.045714285714286,17.074285714285715,15.737142857142857,{"$f":"U14*$I$13","v":16.148571428571429},15.428571428571429,15.017142857142858,14.502857142857144,13.885714285714286,13.577142857142857,12.754285714285714,12.651428571428571,null,1.0514285714285714,1,0.94857142857142862,0.89714285714285713,0.8342857142857143,0.77142857142857146,0.70857142857142863,0.86413043478260876,0.89142857142857146,0.92168674698795172,0.95541401273885351,0.96575342465753422,0.97777777777777775,0.99193548387096775,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.354285714285716,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.045714285714286},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.737142857142857},15.428571428571429,14.502857142857144,13.577142857142857,12.651428571428571]
[null,57,17.382857142857141,17.382857142857141,16.662857142857142,16.662857142857142,15.942857142857143,15.942857142857143,15.222857142857144,15.222857142857144,14.194285714285714,14.194285714285714,13.062857142857142,13.062857142857142,12.034285714285712,12.034285714285712,null,0.96571428571428564,0.92571428571428571,0.88571428571428568,0.84571428571428575,0.78857142857142859,0.72571428571428565,0.66857142857142848,1.0236686390532546,1.0246913580246915,1.0258064516129033,1.027027027027027,1.0217391304347825,1.0314960629921259,1.0341880341880343,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.794285714285714,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.074285714285715},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.354285714285716},15.634285714285715,14.50285714285714,13.474285714285713,12.445714285714285]
[750,72,20.982857142857142,10.697142857142859,20.160000000000004,10.594285714285716,19.337142857142858,10.388571428571428,18.514285714285712,10.285714285714285,17.28,10.080000000000002,16.045714285714286,9.8742857142857154,14.811428571428571,9.668571428571429,null,1.1657142857142857,1.1200000000000001,1.0742857142857143,1.0285714285714285,0.96000000000000008,0.89142857142857146,0.82285714285714284,0.50980392156862753,0.52551020408163263,0.5372340425531914,0.55555555555555558,0.58333333333333337,0.61538461538461542,0.65277777777777779,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":10.697142857142859},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.594285714285716},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.388571428571428},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.285714285714285},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.080000000000002},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.8742857142857154},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.668571428571429}]
[null,67,20.160000000000004,14.297142857142859,19.337142857142858,14.297142857142859,18.617142857142859,14.297142857142857,17.794285714285717,14.4,16.457142857142856,13.988571428571428,15.017142857142858,13.680000000000001,13.68,13.268571428571429,null,1.1200000000000001,1.0742857142857143,1.0342857142857145,0.98857142857142866,0.91428571428571426,0.8342857142857143,0.76,0.70918367346938771,0.73936170212765961,0.7679558011049723,0.80924855491329473,0.85,0.91095890410958913,0.96992481203007519,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.297142857142859},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.297142857142859},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.297142857142857},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.4},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.988571428571428},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.680000000000001},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.268571428571429}]
[null,62,19.439999999999998,18.411428571428569,18.72,18.102857142857143,17.897142857142857,17.69142857142857,17.074285714285715,17.074285714285715,15.942857142857143,15.942857142857143,14.914285714285715,14.914285714285715,13.782857142857143,13.782857142857143,null,1.0799999999999998,1.04,0.99428571428571422,0.94857142857142862,0.88571428571428568,0.82857142857142863,0.76571428571428568,0.94708994708994709,0.96703296703296715,0.9885057471264368,1.0180722891566263,1.0129032258064516,1.0068965517241379,1.0074626865671641,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.411428571428569,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.102857142857143},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.69142857142857},17.382857142857141,16.148571428571429,15.017142857142858,13.885714285714284]
[null,57,18.514285714285712,18.514285714285712,17.897142857142857,17.897142857142857,17.28,17.28,16.560000000000002,16.560000000000002,15.428571428571427,15.428571428571427,14.194285714285714,14.194285714285714,13.062857142857142,13.062857142857142,null,1.0285714285714285,0.99428571428571422,0.96000000000000008,0.92,0.8571428571428571,0.78857142857142859,0.72571428571428565,1.0277777777777777,1.0287356321839081,1.0238095238095237,1.031055900621118,1.0266666666666666,1.036231884057971,1.0314960629921259,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.028571428571425,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.411428571428573},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.69142857142857},17.074285714285715,15.839999999999998,14.708571428571428,13.474285714285713]

{"sheet":"TCJD_24","index":8,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[600,72,{"$f":"R8*$I$13","v":22.724999999999998},{"$f":"IF(AM8>C8,C8,AM8)","v":10.35},{"$f":"S8*$I$13","v":21.975000000000001},{"$f":"IF(AN8>E8,E8,AN8)","v":10.050000000000001},{"$f":"T8*$I$13","v":21.225000000000001},{"$f":"IF(AO8>G8,G8,AO8)","v":9.6750000000000007},{"$f":"U8*$I$13","v":20.399999999999999},{"$f":"IF(AP8>I8,I8,AP8)","v":9.3000000000000007},{"$f":"V8*$I$13","v":18.600000000000001},{"$f":"IF(AQ8>K8,K8,AQ8)","v":8.6999999999999993},{"$f":"W8*$I$13","v":16.875},{"$f":"IF(AR8>M8,M8,AR8)","v":8.1000000000000014},{"$f":"X8*$I$13","v":15.075000000000001},{"$f":"IF(AS8>O8,O8,AS8)","v":7.5749999999999993},null,1.2625,1.2208333333333334,1.1791666666666667,1.1333333333333333,1.0333333333333334,0.9375,0.83750000000000002,0.45544554455445546,0.45733788395904434,0.45583038869257952,0.45588235294117652,0.46774193548387094,0.48000000000000004,0.50248756218905466,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.35},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.050000000000001},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.6750000000000007},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.3000000000000007},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":8.6999999999999993},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.1000000000000014},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":7.5749999999999993}]
[null,67,21.825000000000003,12.75,20.549999999999997,{"$f":"IF(AN9>E9,E9,AN9)","v":12.374999999999998},19.349999999999998,{"$f":"IF(AO9>G9,G9,AO9)","v":11.924999999999999},{"$f":"U9*$I$13","v":17.850000000000001},{"$f":"IF(AP9>I9,I9,AP9)","v":11.55},16.274999999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":10.799999999999999},14.475000000000001,{"$f":"IF(AR9>M9,M9,AR9)","v":10.125},12.600000000000001,{"$f":"IF(AS9>O9,O9,AS9)","v":9.3750000000000018},null,1.2125000000000001,1.1416666666666666,1.075,0.9916666666666667,0.90416666666666667,0.8041666666666667,0.70000000000000007,0.58419243986254288,0.6021897810218978,0.61627906976744184,0.6470588235294118,0.66359447004608296,0.69948186528497402,0.74404761904761907,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.75},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.374999999999998},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":11.924999999999999},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.55},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":10.799999999999999},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":10.125},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":9.3750000000000018}]
[null,62,20.549999999999997,14.924999999999997,18.975000000000001,14.475000000000001,17.399999999999999,13.950000000000001,{"$f":"U10*$I$13","v":15.825000000000001},13.5,14.25,12.450000000000001,12.75,11.475,11.175000000000001,10.425000000000001,null,1.1416666666666666,1.0541666666666667,0.96666666666666667,0.87916666666666676,0.79166666666666663,0.70833333333333337,0.62083333333333335,0.72627737226277367,0.76284584980237158,0.80172413793103459,0.85308056872037907,0.87368421052631584,0.9,0.93288590604026844,1.06,1.06,1.06,1.06,1.06,1.06,1.06,14.924999999999997,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":14.475000000000001},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":13.950000000000001},13.5,12.450000000000001,11.475,10.425000000000001]
[null,57,16.5,16.5,15.375,15.375,14.25,14.25,{"$f":"U11*$I$13","v":13.125},13.125,12.149999999999999,12.074999999999999,11.100000000000001,11.100000000000001,10.125,10.125,null,0.91666666666666663,0.85416666666666663,0.79166666666666663,0.72916666666666663,0.67499999999999993,0.6166666666666667,0.5625,1,1,1,1,0.99382716049382724,1,1,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.5,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":15.375},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":14.25},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":13.125},12.074999999999999,11.100000000000001,10.125]
[800,72,23.774999999999999,11.1,23.024999999999999,10.8,22.275000000000002,10.575000000000001,{"$f":"U12*$I$13","v":21.524999999999999},10.274999999999999,19.725000000000001,9.75,17.924999999999997,9.2999999999999989,16.2,8.7749999999999986,null,1.3208333333333333,1.2791666666666666,1.2375,1.1958333333333333,1.0958333333333334,0.99583333333333324,0.9,0.46687697160883285,0.46905537459283392,0.47474747474747475,0.47735191637630658,0.49429657794676807,0.51882845188284521,0.54166666666666663,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.1},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.8},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.575000000000001},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.274999999999999},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.75},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.2999999999999989},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.7749999999999986}]
[null,67,22.799999999999997,14.1,21.674999999999997,13.799999999999997,20.549999999999997,13.5,18,12.600000000000001,17.475000000000001,12.450000000000003,15.600000000000001,11.775,13.725000000000001,11.025,null,1.2666666666666666,1.2041666666666666,1.1416666666666666,1,0.97083333333333333,0.8666666666666667,0.76250000000000007,0.61842105263157898,0.63667820069204151,0.65693430656934315,0.70000000000000007,0.71244635193133055,0.75480769230769229,0.80327868852459006,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.1},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.799999999999997},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.5},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.600000000000001},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.450000000000003},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.775},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.025}]
[null,62,21.599999999999998,17.174999999999997,20.175000000000001,16.575000000000003,18.75,15.9,{"$f":"U14*$I$13","v":17.324999999999999},15.225,15.75,13.950000000000001,14.174999999999999,12.75,12.674999999999999,11.55,null,1.2,1.1208333333333333,1.0416666666666667,0.96250000000000002,0.875,0.78749999999999998,0.70416666666666661,0.79513888888888884,0.82156133828996292,0.84799999999999998,0.87878787878787878,0.88571428571428579,0.89947089947089953,0.91124260355029596,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.174999999999997,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.575000000000003},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.9},15.225,13.950000000000001,12.75,11.55]
[null,57,18.224999999999998,18.149999999999995,17.25,17.100000000000001,16.274999999999999,16.049999999999997,15.299999999999999,15,14.025,13.799999999999999,12.825000000000001,12.6,11.625,11.324999999999999,null,1.0125,0.95833333333333337,0.90416666666666667,0.85,0.77916666666666667,0.71250000000000002,0.64583333333333337,0.99588477366255135,0.99130434782608701,0.98617511520737322,0.98039215686274517,0.98395721925133683,0.98245614035087714,0.97419354838709671,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.149999999999995,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.100000000000001},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.049999999999997},15,13.799999999999999,12.6,11.324999999999999]
[1000,72,24.900000000000002,11.775,24.150000000000002,11.625,23.400000000000002,11.475000000000001,22.574999999999999,11.324999999999999,20.774999999999999,10.875,19.05,10.425000000000001,17.324999999999999,9.9749999999999996,null,1.3833333333333335,1.3416666666666668,1.3,1.2541666666666667,1.1541666666666666,1.0583333333333333,0.96250000000000002,0.47289156626506018,0.48136645962732916,0.49038461538461542,0.50166112956810627,0.52346570397111913,0.547244094488189,0.5757575757575758,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.775},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.625},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.475000000000001},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.324999999999999},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.875},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.425000000000001},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.9749999999999996}]
[null,67,23.849999999999998,15.450000000000001,22.799999999999997,15.225,21.674999999999997,15,20.625,14.774999999999999,18.674999999999997,14.1,16.725000000000001,13.350000000000001,14.850000000000001,12.675000000000001,null,1.325,1.2666666666666666,1.2041666666666666,1.1458333333333333,1.0374999999999999,0.9291666666666667,0.82500000000000007,0.64779874213836486,0.66776315789473695,0.69204152249134954,0.71636363636363631,0.7550200803212852,0.7982062780269058,0.85353535353535348,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.450000000000001},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.225},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.774999999999999},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.1},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.350000000000001},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.675000000000001}]
[null,62,22.574999999999999,19.5,21.3,18.675000000000001,20.025000000000002,17.775000000000002,18.75,16.95,17.174999999999997,15.45,15.674999999999999,14.024999999999999,14.174999999999999,12.6,null,1.2541666666666667,1.1833333333333333,1.1125,1.0416666666666667,0.95416666666666661,0.87083333333333324,0.78749999999999998,0.86378737541528239,0.87676056338028163,0.88764044943820219,0.90400000000000003,0.89956331877729268,0.89473684210526316,0.88888888888888895,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.5,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.675000000000001},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.775000000000002},16.95,15.45,14.024999999999999,12.6]
[null,57,19.950000000000003,19.8,19.125,18.825000000000003,18.299999999999997,17.924999999999997,17.475000000000001,16.950000000000003,15.975000000000001,15.450000000000003,14.549999999999999,14.024999999999999,13.125,12.600000000000001,null,1.1083333333333334,1.0625,1.0166666666666666,0.97083333333333333,0.88750000000000007,0.80833333333333324,0.72916666666666663,0.99248120300751874,0.98431372549019613,0.97950819672131151,0.96995708154506444,0.96713615023474186,0.96391752577319589,0.96000000000000008,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.8,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.825000000000003},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.924999999999997},16.950000000000003,15.450000000000003,14.024999999999999,12.600000000000001]

{"sheet":"TCJD_30","index":9,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[800,72,{"$f":"R8*$I$13","v":21.351724137931033},{"$f":"IF(AM8>C8,C8,AM8)","v":9.9310344827586192},{"$f":"S8*$I$13","v":20.23448275862069},{"$f":"IF(AN8>E8,E8,AN8)","v":9.5586206896551715},{"$f":"T8*$I$13","v":19.179310344827588},{"$f":"IF(AO8>G8,G8,AO8)","v":9.1241379310344843},{"$f":"U8*$I$13","v":18.062068965517245},{"$f":"IF(AP8>I8,I8,AP8)","v":8.7517241379310349},{"$f":"V8*$I$13","v":16.324137931034482},{"$f":"IF(AQ8>K8,K8,AQ8)","v":8.1931034482758616},{"$f":"W8*$I$13","v":14.586206896551722},{"$f":"IF(AR8>M8,M8,AR8)","v":7.6344827586206883},{"$f":"X8*$I$13","v":12.848275862068965},{"$f":"IF(AS8>O8,O8,AS8)","v":7.0758620689655167},null,1.1862068965517241,1.1241379310344828,1.0655172413793104,1.0034482758620691,0.90689655172413797,0.81034482758620685,0.71379310344827585,0.46511627906976744,0.47239263803680981,0.47572815533980584,0.48453608247422675,0.50190114068441061,0.52340425531914891,0.55072463768115942,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":9.9310344827586192},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":9.5586206896551715},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.1241379310344843},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":8.7517241379310349},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":8.1931034482758616},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":7.6344827586206883},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":7.0758620689655167}]
[null,67,20.544827586206896,13.158620689655171,19.179310344827588,{"$f":"IF(AN9>E9,E9,AN9)","v":12.600000000000003},17.875862068965517,{"$f":"IF(AO9>G9,G9,AO9)","v":12.041379310344826},{"$f":"U9*$I$13","v":16.572413793103447},{"$f":"IF(AP9>I9,I9,AP9)","v":11.482758620689655},14.710344827586207,{"$f":"IF(AQ9>K9,K9,AQ9)","v":10.799999999999999},12.972413793103449,{"$f":"IF(AR9>M9,M9,AR9)","v":10.179310344827586},11.23448275862069,{"$f":"IF(AS9>O9,O9,AS9)","v":9.4965517241379303},null,1.1413793103448275,1.0655172413793104,0.99310344827586206,0.92068965517241375,0.8172413793103448,0.72068965517241379,0.62413793103448278,0.6404833836858006,0.65695792880258908,0.67361111111111105,0.69288389513108617,0.73417721518987333,0.78468899521531099,0.84530386740331487,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.158620689655171},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.600000000000003},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.041379310344826},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.482758620689655},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":10.799999999999999},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":10.179310344827586},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":9.4965517241379303}]
[null,62,19.489655172413791,16.013793103448275,17.875862068965517,15.33103448275862,16.324137931034482,14.648275862068965,{"$f":"U10*$I$13","v":14.772413793103448},13.96551724137931,13.531034482758622,12.848275862068967,12.289655172413793,11.73103448275862,11.110344827586205,10.675862068965516,null,1.0827586206896551,0.99310344827586206,0.90689655172413797,0.82068965517241377,0.75172413793103454,0.6827586206896552,0.61724137931034473,0.82165605095541405,0.85763888888888884,0.89733840304182511,0.94537815126050417,0.94954128440366969,0.95454545454545447,0.96089385474860334,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.013793103448275,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.33103448275862},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.648275862068965},13.96551724137931,12.848275862068967,11.73103448275862,10.675862068965516]
[null,57,17.627586206896552,17.627586206896552,16.386206896551723,16.386206896551723,15.144827586206894,15.144827586206894,{"$f":"U11*$I$13","v":13.903448275862068},13.903448275862068,12.724137931034482,12.724137931034482,11.544827586206898,11.544827586206898,10.427586206896553,10.427586206896553,null,0.97931034482758617,0.91034482758620683,0.84137931034482749,0.77241379310344827,0.7068965517241379,0.64137931034482765,0.57931034482758625,1.0140845070422535,1.018939393939394,1.0204918032786885,1.0223214285714286,1.024390243902439,1.0268817204301075,1.0297619047619047,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.875862068965517,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.696551724137933},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":15.4551724137931},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":14.213793103448277},13.034482758620689,11.855172413793104,10.737931034482759]
[1000,72,21.413793103448278,10.613793103448277,20.358620689655169,10.179310344827584,19.241379310344826,9.8068965517241367,{"$f":"U12*$I$13","v":18.186206896551727},9.3724137931034495,16.386206896551723,8.8758620689655174,14.586206896551722,8.3793103448275854,12.848275862068965,7.8206896551724139,null,1.1896551724137931,1.1310344827586205,1.0689655172413792,1.010344827586207,0.91034482758620683,0.81034482758620685,0.71379310344827585,0.4956521739130435,0.5,0.50967741935483868,0.51535836177474403,0.54166666666666674,0.57446808510638303,0.60869565217391308,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.613793103448277},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.179310344827584},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":9.8068965517241367},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.3724137931034495},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":8.8758620689655174},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.3793103448275854},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":7.8206896551724139}]
[null,67,20.731034482758616,14.027586206896551,19.489655172413791,13.655172413793103,18.186206896551727,13.282758620689657,18,13.158620689655173,15.082758620689656,12.227586206896552,13.282758620689654,11.544827586206896,11.482758620689657,10.924137931034485,null,1.1517241379310343,1.0827586206896551,1.010344827586207,1,0.83793103448275863,0.73793103448275854,0.63793103448275867,0.67664670658682646,0.7006369426751593,0.7303754266211604,0.73103448275862071,0.81069958847736623,0.86915887850467299,0.9513513513513514,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.027586206896551},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.655172413793103},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.282758620689657},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.158620689655173},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.227586206896552},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.544827586206896},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":10.924137931034485}]
[null,62,19.737931034482759,17.50344827586207,18.434482758620689,16.820689655172416,17.068965517241381,16.137931034482758,{"$f":"U14*$I$13","v":15.703448275862071},15.455172413793104,14.337931034482759,14.089655172413792,13.03448275862069,12.724137931034484,11.73103448275862,11.420689655172412,null,1.096551724137931,1.0241379310344827,0.94827586206896552,0.87241379310344835,0.79655172413793107,0.72413793103448276,0.65172413793103445,0.88679245283018859,0.91245791245791252,0.94545454545454544,0.98418972332015797,0.9826839826839826,0.97619047619047616,0.97354497354497349,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.50344827586207,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.820689655172416},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.137931034482758},15.455172413793104,14.089655172413792,12.724137931034484,11.420689655172412]
[null,57,18.49655172413793,18.49655172413793,17.317241379310342,17.317241379310342,16.137931034482758,16.137931034482758,15.020689655172413,15.020689655172413,13.655172413793103,13.655172413793103,12.351724137931033,12.351724137931033,11.048275862068966,11.048275862068966,null,1.0275862068965518,0.9620689655172413,0.89655172413793105,0.83448275862068966,0.75862068965517238,0.68620689655172407,0.61379310344827587,1.0201342281879193,1.021505376344086,1.0230769230769232,1.0247933884297522,1.0272727272727273,1.0301507537688444,1.0337078651685392,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.868965517241374,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.68965517241379},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.510344827586209},15.393103448275864,14.027586206896553,12.724137931034482,11.420689655172412]
[1200,72,21.53793103448276,11.234482758620691,20.420689655172414,10.86206896551724,19.365517241379308,10.427586206896553,18.248275862068965,10.055172413793104,16.386206896551723,9.5586206896551733,14.648275862068967,9.1241379310344826,12.848275862068965,8.6275862068965523,null,1.1965517241379311,1.1344827586206896,1.0758620689655172,1.0137931034482759,0.91034482758620683,0.81379310344827593,0.71379310344827585,0.52161383285302598,0.53191489361702127,0.53846153846153855,0.55102040816326536,0.58333333333333337,0.62288135593220328,0.6714975845410629,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.234482758620691},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.86206896551724},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.427586206896553},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.055172413793104},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":9.5586206896551733},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.1241379310344826},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":8.6275862068965523}]
[null,67,20.917241379310344,14.896551724137929,19.737931034482759,14.710344827586207,18.49655172413793,14.524137931034481,17.317241379310342,14.337931034482757,15.393103448275863,13.655172413793103,13.531034482758622,12.972413793103449,11.66896551724138,11.66896551724138,null,1.1620689655172414,1.096551724137931,1.0275862068965518,0.9620689655172413,0.85517241379310349,0.75172413793103454,0.64827586206896559,0.71216617210682487,0.74528301886792447,0.78523489932885904,0.82795698924731187,0.88709677419354838,0.95871559633027514,1.053191489361702,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.896551724137929},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.710344827586207},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.524137931034481},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.337931034482757},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.655172413793103},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.972413793103449},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.289655172413793}]
[null,62,20.048275862068962,19.055172413793102,18.931034482758619,18.310344827586206,17.813793103448276,17.627586206896552,16.69655172413793,16.69655172413793,15.206896551724139,15.206896551724139,13.779310344827586,13.779310344827586,12.351724137931033,12.165517241379311,null,1.1137931034482758,1.0517241379310345,0.98965517241379308,0.92758620689655169,0.84482758620689657,0.76551724137931032,0.68620689655172407,0.95046439628482982,0.96721311475409832,0.98954703832752611,1.0148698884758365,1.0081632653061223,1,0.98492462311557805,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.055172413793102,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.310344827586206},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.627586206896552},16.944827586206895,15.33103448275862,13.779310344827586,12.165517241379311]
[null,57,19.365517241379308,19.365517241379308,18.310344827586206,18.310344827586206,17.193103448275863,17.193103448275863,16.137931034482758,16.137931034482758,14.648275862068967,14.648275862068967,13.158620689655173,13.158620689655173,11.73103448275862,11.73103448275862,null,1.0758620689655172,1.0172413793103448,0.95517241379310347,0.89655172413793105,0.81379310344827593,0.73103448275862071,0.65172413793103445,1.0224358974358974,1.0237288135593221,1.0252707581227436,1.0269230769230768,1.0296610169491525,1.0377358490566038,1.0370370370370372,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.799999999999997,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.744827586206899},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.627586206896552},16.572413793103447,15.082758620689656,13.655172413793103,12.165517241379311]

{"sheet":"TCJD_36","index":10,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1000,72,{"$f":"R8*$I$13","v":19.182857142857141},{"$f":"IF(AM8>C8,C8,AM8)","v":9.4628571428571426},{"$f":"S8*$I$13","v":18.822857142857146},{"$f":"IF(AN8>E8,E8,AN8)","v":9.5657142857142876},{"$f":"T8*$I$13","v":18.411428571428569},{"$f":"IF(AO8>G8,G8,AO8)","v":9.668571428571429},{"$f":"U8*$I$13","v":18},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7714285714285705},{"$f":"V8*$I$13","v":16.714285714285715},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.4628571428571426},{"$f":"W8*$I$13","v":15.48},{"$f":"IF(AR8>M8,M8,AR8)","v":9.1542857142857148},{"$f":"X8*$I$13","v":14.194285714285714},{"$f":"IF(AS8>O8,O8,AS8)","v":8.8457142857142852},null,1.0657142857142856,1.0457142857142858,1.0228571428571427,1,0.9285714285714286,0.86,0.78857142857142859,0.49329758713136729,0.50819672131147542,0.52513966480446939,0.54285714285714282,0.56615384615384612,0.59136212624584716,0.62318840579710144,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":9.4628571428571426},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":9.5657142857142876},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.668571428571429},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7714285714285705},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.4628571428571426},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.1542857142857148},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.8457142857142852}]
[null,67,19.234285714285711,13.114285714285714,18.462857142857139,{"$f":"IF(AN9>E9,E9,AN9)","v":13.165714285714285},17.69142857142857,{"$f":"IF(AO9>G9,G9,AO9)","v":13.268571428571427},{"$f":"U9*$I$13","v":16.971428571428572},{"$f":"IF(AP9>I9,I9,AP9)","v":13.37142857142857},15.325714285714286,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.857142857142858},13.782857142857143,{"$f":"IF(AR9>M9,M9,AR9)","v":12.394285714285715},12.188571428571429,{"$f":"IF(AS9>O9,O9,AS9)","v":11.931428571428572},null,1.0685714285714285,1.0257142857142856,0.98285714285714276,0.94285714285714284,0.85142857142857142,0.76571428571428568,0.67714285714285716,0.68181818181818188,0.71309192200557114,0.75,0.78787878787878785,0.83892617449664431,0.89925373134328357,0.97890295358649793,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.114285714285714},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.165714285714285},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.268571428571427},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":13.37142857142857},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.857142857142858},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.394285714285715},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.931428571428572}]
[null,62,18.565714285714286,16.971428571428572,17.845714285714287,16.714285714285712,17.074285714285715,16.457142857142856,{"$f":"U10*$I$13","v":16.302857142857142},16.2,14.811428571428571,14.811428571428571,13.371428571428572,13.371428571428572,11.931428571428571,11.931428571428571,null,1.0314285714285714,0.99142857142857155,0.94857142857142862,0.90571428571428569,0.82285714285714284,0.74285714285714288,0.66285714285714281,0.91412742382271461,0.93659942363112381,0.96385542168674687,0.99369085173501581,1.0034722222222221,1.0115384615384615,1.0258620689655173,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.971428571428572,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.714285714285712},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":16.457142857142856},16.2,14.862857142857141,13.525714285714285,12.24]
[null,57,17.845714285714287,17.639999999999997,17.28,17.125714285714285,16.662857142857142,16.559999999999999,{"$f":"U11*$I$13","v":16.09714285714286},15.994285714285716,14.348571428571429,14.348571428571429,12.651428571428571,12.651428571428571,10.954285714285714,10.954285714285714,null,0.99142857142857155,0.96000000000000008,0.92571428571428571,0.89428571428571435,0.79714285714285715,0.70285714285714285,0.60857142857142854,0.98847262247838596,0.99107142857142849,0.99382716049382724,0.99361022364217255,1.0286738351254481,1.0691056910569106,1.1220657276995305,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.639999999999997,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.125714285714285},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.559999999999999},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.994285714285716},14.760000000000002,13.525714285714285,12.29142857142857]
[1200,72,19.285714285714285,9.2571428571428562,18.822857142857146,9.257142857142858,18.36,9.2571428571428562,{"$f":"U12*$I$13","v":17.897142857142857},9.257142857142858,16.560000000000002,8.8971428571428586,15.325714285714286,8.5371428571428591,14.040000000000001,8.1771428571428579,null,1.0714285714285714,1.0457142857142858,1.02,0.99428571428571422,0.92,0.85142857142857142,0.78,0.48,0.49180327868852458,0.50420168067226889,0.51724137931034486,0.53726708074534157,0.5570469798657719,0.58241758241758246,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":9.2571428571428562},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":9.257142857142858},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":9.2571428571428562},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.257142857142858},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":8.8971428571428586},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.5371428571428591},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.1771428571428579}]
[null,67,19.028571428571428,12.651428571428573,18.257142857142856,12.6,17.537142857142857,12.497142857142858,18,12.805714285714286,15.12,11.931428571428571,13.525714285714287,11.417142857142858,11.931428571428571,10.902857142857142,null,1.0571428571428572,1.0142857142857142,0.97428571428571431,1,0.84,0.75142857142857145,0.66285714285714281,0.66486486486486496,0.6901408450704225,0.71260997067448684,0.71142857142857141,0.78911564625850339,0.844106463878327,0.91379310344827591,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":12.651428571428573},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":12.6},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":12.497142857142858},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.805714285714286},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":11.931428571428571},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.417142857142858},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":10.902857142857142}]
[null,62,18.257142857142856,15.942857142857141,17.434285714285714,15.737142857142858,16.611428571428572,15.531428571428572,{"$f":"U14*$I$13","v":15.788571428571428},15.274285714285714,14.297142857142857,13.988571428571428,12.908571428571429,12.754285714285714,11.468571428571428,11.468571428571428,null,1.0142857142857142,0.96857142857142853,0.92285714285714282,0.87714285714285711,0.79428571428571426,0.71714285714285719,0.63714285714285712,0.87323943661971826,0.90265486725663724,0.93498452012383904,0.96742671009771986,0.97841726618705027,0.98804780876494025,1.0044843049327354,1.06,1.06,1.06,1.06,1.06,1.06,1.06,15.942857142857141,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":15.737142857142858},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.531428571428572},15.274285714285714,13.988571428571428,12.754285714285714,11.52]
[null,57,17.382857142857141,17.125714285714285,16.765714285714289,16.508571428571432,16.09714285714286,15.891428571428573,15.48,15.274285714285714,13.885714285714286,13.885714285714286,12.291428571428572,12.291428571428572,10.748571428571427,10.748571428571427,null,0.96571428571428564,0.93142857142857149,0.89428571428571435,0.86,0.77142857142857146,0.68285714285714283,0.59714285714285709,0.98520710059171601,0.98466257668711654,0.98722044728434499,0.98671096345514941,1.0111111111111111,1.0418410041841004,1.0765550239234452,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.125714285714285,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":16.508571428571432},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":15.891428571428573},15.274285714285714,14.04,12.805714285714286,11.571428571428571]
[1400,72,19.337142857142858,9.1028571428571432,18.822857142857146,9,18.257142857142856,8.8971428571428568,17.742857142857144,8.7942857142857154,16.405714285714286,8.331428571428571,15.171428571428571,7.919999999999999,13.885714285714286,7.5085714285714289,null,1.0742857142857143,1.0457142857142858,1.0142857142857142,0.98571428571428577,0.91142857142857137,0.84285714285714286,0.77142857142857146,0.4707446808510638,0.47814207650273222,0.48732394366197185,0.4956521739130435,0.50783699059561127,0.52203389830508473,0.54074074074074074,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":9.1028571428571432},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":9},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":8.8971428571428568},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":8.7942857142857154},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":8.331428571428571},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":7.919999999999999},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":7.5085714285714289}]
[null,67,18.822857142857146,12.137142857142861,18.051428571428573,11.982857142857144,17.331428571428575,11.777142857142858,16.560000000000002,11.571428571428571,14.914285714285715,11.005714285714285,13.32,10.440000000000001,11.674285714285714,9.8742857142857154,null,1.0457142857142858,1.0028571428571429,0.96285714285714297,0.92,0.82857142857142863,0.74,0.64857142857142858,0.64480874316939896,0.66381766381766383,0.67952522255192871,0.69875776397515521,0.73793103448275854,0.78378378378378388,0.8458149779735683,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":12.137142857142861},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":11.982857142857144},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":11.777142857142858},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":11.571428571428571},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":11.005714285714285},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":10.440000000000001},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":9.8742857142857154}]
[null,62,17.948571428571427,14.965714285714286,17.074285714285715,14.759999999999998,16.2,14.554285714285713,15.325714285714286,14.348571428571427,13.834285714285715,13.165714285714287,12.394285714285715,11.982857142857144,10.954285714285714,10.799999999999999,null,0.99714285714285711,0.94857142857142862,0.9,0.85142857142857142,0.76857142857142857,0.68857142857142861,0.60857142857142854,0.83381088825214911,0.86445783132530107,0.89841269841269844,0.93624161073825496,0.95167286245353166,0.96680497925311204,0.9859154929577465,1.06,1.06,1.06,1.06,1.06,1.06,1.06,14.965714285714286,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":14.759999999999998},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":14.554285714285713},14.348571428571427,13.165714285714287,11.982857142857144,10.799999999999999]
[null,57,16.919999999999998,16.611428571428569,16.2,15.942857142857141,15.531428571428572,15.222857142857146,14.862857142857141,14.554285714285715,13.371428571428572,13.268571428571429,11.982857142857142,11.982857142857142,10.542857142857143,10.542857142857143,null,0.94,0.9,0.86285714285714288,0.82571428571428562,0.74285714285714288,0.6657142857142857,0.58571428571428574,0.98176291793313064,0.98412698412698407,0.98013245033112595,0.97923875432525964,0.99230769230769234,1.0085836909871244,1.0292682926829269,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.611428571428569,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":15.942857142857141},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":15.222857142857146},14.554285714285715,13.268571428571429,12.085714285714284,10.851428571428572]

{"sheet":"TCJD_42","index":11,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[77,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1200,72,{"$f":"R8*$I$13","v":20.785714285714285},{"$f":"IF(AM8>C8,C8,AM8)","v":5.3982857142857137},{"$f":"S8*$I$13","v":19.971428571428572},{"$f":"IF(AN8>E8,E8,AN8)","v":5.3125714285714301},{"$f":"T8*$I$13","v":19.114285714285714},{"$f":"IF(AO8>G8,G8,AO8)","v":5.2697142857142856},{"$f":"U8*$I$13","v":18.300000000000004},{"$f":"IF(AP8>I8,I8,AP8)","v":5.1840000000000019},{"$f":"V8*$I$13","v":16.585714285714285},{"$f":"IF(AQ8>K8,K8,AQ8)","v":4.5839999999999987},{"$f":"W8*$I$13","v":14.914285714285713},{"$f":"IF(AR8>M8,M8,AR8)","v":3.9839999999999991},{"$f":"X8*$I$13","v":13.242857142857142},{"$f":"IF(AS8>O8,O8,AS8)","v":3.3840000000000012},null,1.1547619047619047,1.1095238095238096,1.0619047619047619,1.0166666666666668,0.92142857142857149,0.82857142857142851,0.73571428571428565,0.44329896907216493,0.4570815450643777,0.47533632286995514,0.49180327868852458,0.50645994832041341,0.52298850574712641,0.54368932038834961,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":5.3982857142857137},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":5.3125714285714301},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":5.2697142857142856},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":5.1840000000000019},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":4.5839999999999987},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":3.9839999999999991},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":3.3840000000000012}]
[null,67,20.142857142857142,8.4839999999999982,19.328571428571429,{"$f":"IF(AN9>E9,E9,AN9)","v":8.3982857142857164},18.557142857142857,{"$f":"IF(AO9>G9,G9,AO9)","v":8.2697142857142865},{"$f":"U9*$I$13","v":17.785714285714285},{"$f":"IF(AP9>I9,I9,AP9)","v":8.1839999999999975},16.028571428571428,{"$f":"IF(AQ9>K9,K9,AQ9)","v":7.4982857142857133},14.314285714285713,{"$f":"IF(AR9>M9,M9,AR9)","v":6.8554285714285692},12.6,{"$f":"IF(AS9>O9,O9,AS9)","v":6.2125714285714286},null,1.1190476190476191,1.0738095238095238,1.0309523809523808,0.98809523809523814,0.89047619047619042,0.79523809523809519,0.7,0.61063829787234036,0.63192904656319293,0.65127020785219403,0.67469879518072284,0.70588235294117641,0.74550898203592808,0.79591836734693877,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":8.4839999999999982},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":8.3982857142857164},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":8.2697142857142865},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":8.1839999999999975},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":7.4982857142857133},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":6.8554285714285692},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":6.2125714285714286}]
[null,62,19.5,11.441142857142857,18.385714285714286,11.269714285714286,17.271428571428569,11.055428571428571,{"$f":"U10*$I$13","v":16.157142857142858},10.883999999999997,14.871428571428572,9.9411428571428573,13.585714285714285,9.0411428571428587,12.342857142857143,8.1411428571428566,null,1.0833333333333333,1.0214285714285714,0.95952380952380945,0.89761904761904765,0.82619047619047625,0.75476190476190474,0.68571428571428572,0.78241758241758241,0.8205128205128206,0.86104218362282892,0.90981432360742687,0.9250720461095101,0.94637223974763407,0.96874999999999989,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.441142857142857,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":11.269714285714286},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":11.055428571428571},10.883999999999997,9.9411428571428573,9.0411428571428587,8.1411428571428566]
[null,57,19.028571428571428,13.969714285714286,18.128571428571426,13.069714285714284,17.228571428571428,12.126857142857144,{"$f":"U11*$I$13","v":16.371428571428574},11.184000000000001,15.128571428571426,10.026857142857139,13.885714285714284,8.9125714285714253,12.685714285714287,7.7982857142857158,null,1.0571428571428572,1.0071428571428571,0.95714285714285718,0.90952380952380962,0.84047619047619038,0.77142857142857135,0.70476190476190481,0.93468468468468469,0.9314420803782506,0.92537313432835822,0.91623036649214651,0.91501416430594895,0.91666666666666663,0.91554054054054057,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.969714285714286,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":13.069714285714284},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":12.126857142857144},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":11.184000000000001},10.026857142857139,8.9125714285714253,7.7982857142857158]
[1400,72,21.342857142857142,5.3622857142857132,20.528571428571428,5.1479999999999997,19.671428571428571,4.9765714285714289,{"$f":"U12*$I$13","v":18.857142857142858},4.805142857142858,17.057142857142857,4.290857142857142,15.3,3.8194285714285705,13.585714285714285,3.3051428571428572,null,1.1857142857142857,1.1404761904761904,1.0928571428571427,1.0476190476190477,0.94761904761904758,0.85000000000000009,0.75476190476190474,0.45983935742971888,0.46764091858037576,0.47930283224400871,0.49090909090909096,0.51256281407035176,0.54061624649859941,0.57097791798107256,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":5.3622857142857132},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":5.1479999999999997},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":4.9765714285714289},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":4.805142857142858},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":4.290857142857142},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":3.8194285714285705},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":3.3051428571428572}]
[null,67,20.785714285714285,8.4908571428571431,19.971428571428572,8.4480000000000022,19.157142857142858,8.4051428571428559,18,8.1479999999999997,16.542857142857144,7.7194285714285726,14.828571428571429,7.1194285714285712,13.071428571428571,6.5194285714285716,null,1.1547619047619047,1.1095238095238096,1.0642857142857143,1,0.91904761904761911,0.82380952380952388,0.72619047619047616,0.62268041237113403,0.64592274678111594,0.67114093959731536,0.7,0.73575129533678751,0.78034682080924855,0.83934426229508197,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":8.4908571428571431},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":8.4480000000000022},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":8.4051428571428559},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":8.1479999999999997},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":7.7194285714285726},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":7.1194285714285712},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":6.5194285714285716}]
[null,62,19.928571428571431,11.619428571428573,18.985714285714288,11.576571428571429,18.042857142857144,11.533714285714286,{"$f":"U14*$I$13","v":17.099999999999998},11.533714285714284,15.728571428571431,10.333714285714287,14.4,9.2194285714285709,13.071428571428571,8.105142857142857,null,1.1071428571428572,1.0547619047619048,1.0023809523809524,0.95,0.87380952380952392,0.8,0.72619047619047616,0.80645161290322576,0.84424379232505642,0.88598574821852727,0.93483709273182958,0.94005449591280643,0.94940476190476186,0.96065573770491808,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.619428571428573,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":11.576571428571429},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":11.533714285714286},11.533714285714284,10.333714285714287,9.2194285714285709,8.105142857142857]
[null,57,19.671428571428571,13.933714285714286,18.942857142857143,13.162285714285714,18.171428571428571,12.390857142857142,17.442857142857143,11.619428571428569,16.071428571428573,10.333714285714288,14.785714285714285,9.0908571428571427,13.457142857142857,7.8480000000000008,null,1.0928571428571427,1.0523809523809524,1.0095238095238095,0.96904761904761916,0.8928571428571429,0.8214285714285714,0.74761904761904763,0.934640522875817,0.92986425339366519,0.92688679245283012,0.92137592137592128,0.92,0.91594202898550725,0.9140127388535032,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.933714285714286,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":13.162285714285714},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":12.390857142857142},11.619428571428569,10.333714285714288,9.0908571428571427,7.8480000000000008]
[1600,72,21.900000000000002,5.3262857142857145,21.042857142857144,5.0262857142857156,20.228571428571428,4.7262857142857131,19.414285714285715,4.4262857142857142,17.528571428571428,3.9977142857142853,15.728571428571431,3.612000000000001,13.928571428571429,3.2262857142857131,null,1.2166666666666668,1.1690476190476191,1.1238095238095238,1.0785714285714285,0.97380952380952379,0.87380952380952392,0.77380952380952384,0.47553816046966729,0.48065173116089616,0.48516949152542366,0.49006622516556292,0.51833740831295838,0.55313351498637597,0.59692307692307689,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":5.3262857142857145},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":5.0262857142857156},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":4.7262857142857131},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":4.4262857142857142},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":3.9977142857142853},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":3.612000000000001},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":3.2262857142857131}]
[null,67,21.471428571428572,8.4977142857142844,20.614285714285714,8.5405714285714289,19.714285714285715,8.5405714285714289,18.814285714285717,8.5834285714285734,17.057142857142857,7.9834285714285711,15.3,7.3834285714285715,13.585714285714285,6.8262857142857145,null,1.1928571428571428,1.1452380952380952,1.0952380952380953,1.0452380952380953,0.94761904761904758,0.85000000000000009,0.75476190476190474,0.63273453093812371,0.66112266112266116,0.69130434782608696,0.72665148063781315,0.76633165829145733,0.81512605042016806,0.87697160883280756,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":8.4977142857142844},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":8.5405714285714289},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":8.5405714285714289},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":8.5834285714285734},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":7.9834285714285711},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":7.3834285714285715},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":6.8262857142857145}]
[null,62,20.357142857142858,11.797714285714285,19.585714285714289,11.926285714285715,18.814285714285717,12.054857142857145,18.042857142857144,12.183428571428568,16.628571428571426,10.769142857142857,15.214285714285714,9.397714285714283,13.8,8.0262857142857129,null,1.1309523809523809,1.0880952380952382,1.0452380952380953,1.0023809523809524,0.92380952380952375,0.84523809523809523,0.76666666666666672,0.82947368421052625,0.86870897155361049,0.91116173120728927,0.9572446555819476,0.95360824742268047,0.95211267605633798,0.95031055900621109,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.797714285714285,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":11.926285714285715},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":12.054857142857145},12.183428571428568,10.769142857142857,9.397714285714283,8.0262857142857129]
[null,57,20.357142857142858,13.940571428571428,19.714285714285715,13.297714285714285,19.114285714285714,12.697714285714284,18.514285714285716,12.054857142857141,17.057142857142857,10.64057142857143,15.642857142857142,9.2691428571428567,14.22857142857143,7.8548571428571412,null,1.1309523809523809,1.0952380952380953,1.0619047619047619,1.0285714285714287,0.94761904761904758,0.86904761904761907,0.79047619047619055,0.93473684210526309,0.93260869565217386,0.93049327354260092,0.92592592592592582,0.92211055276381926,0.9178082191780822,0.90963855421686735,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.940571428571428,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":13.297714285714285},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":12.697714285714284},12.054857142857141,10.64057142857143,9.2691428571428567,7.8548571428571412]

{"sheet":"TCJD_48","index":12,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":20.474999999999998},{"$f":"IF(AM8>C8,C8,AM8)","v":9.7874999999999996},{"$f":"S8*$I$13","v":19.649999999999999},{"$f":"IF(AN8>E8,E8,AN8)","v":9.5249999999999986},{"$f":"T8*$I$13","v":18.825000000000003},{"$f":"IF(AO8>G8,G8,AO8)","v":9.3000000000000007},{"$f":"U8*$I$13","v":17.962499999999999},{"$f":"IF(AP8>I8,I8,AP8)","v":9.0375000000000014},{"$f":"V8*$I$13","v":16.350000000000001},{"$f":"IF(AQ8>K8,K8,AQ8)","v":8.5874999999999986},{"$f":"W8*$I$13","v":14.737499999999999},{"$f":"IF(AR8>M8,M8,AR8)","v":8.1},{"$f":"X8*$I$13","v":13.162500000000001},{"$f":"IF(AS8>O8,O8,AS8)","v":7.65},null,1.1375,1.0916666666666666,1.0458333333333334,0.99791666666666667,0.90833333333333333,0.81874999999999998,0.73125000000000007,0.47802197802197804,0.48473282442748089,0.49402390438247012,0.50313152400835082,0.52522935779816504,0.54961832061068705,0.58119658119658113,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":9.7874999999999996},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":9.5249999999999986},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.3000000000000007},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.0375000000000014},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":8.5874999999999986},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.1},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":7.65}]
[null,67,20.924999999999997,13.499999999999998,19.837499999999999,{"$f":"IF(AN9>E9,E9,AN9)","v":13.087499999999999},18.712499999999999,{"$f":"IF(AO9>G9,G9,AO9)","v":12.674999999999999},{"$f":"U9*$I$13","v":17.625},{"$f":"IF(AP9>I9,I9,AP9)","v":12.262500000000001},15.899999999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.587499999999999},14.25,{"$f":"IF(AR9>M9,M9,AR9)","v":10.95},12.5625,{"$f":"IF(AS9>O9,O9,AS9)","v":10.3125},null,1.1624999999999999,1.1020833333333333,1.0395833333333333,0.97916666666666663,0.8833333333333333,0.79166666666666663,0.69791666666666663,0.64516129032258063,0.6597353497164461,0.67735470941883769,0.69574468085106389,0.72877358490566035,0.76842105263157889,0.82089552238805974,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.499999999999998},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.087499999999999},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.674999999999999},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.262500000000001},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.587499999999999},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":10.95},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":10.3125}]
[null,62,19.274999999999999,16.162499999999998,18.224999999999998,15.749999999999996,17.174999999999997,15.374999999999998,{"$f":"U10*$I$13","v":16.087499999999999},14.962499999999999,14.774999999999999,13.875,13.4625,12.825000000000003,12.149999999999999,11.774999999999999,null,1.0708333333333333,1.0125,0.95416666666666661,0.89374999999999993,0.8208333333333333,0.74791666666666667,0.67499999999999993,0.83852140077821014,0.86419753086419748,0.89519650655021843,0.93006993006993011,0.93908629441624369,0.95264623955431771,0.96913580246913578,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.162499999999998,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.749999999999996},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.374999999999998},14.962499999999999,13.875,12.825000000000003,11.774999999999999]
[null,57,18.637499999999999,17.7,17.8125,16.837499999999999,17.024999999999999,16.012499999999999,{"$f":"U11*$I$13","v":16.2},15.149999999999999,14.924999999999999,13.9125,13.6875,12.712499999999999,12.4125,11.512499999999999,null,1.0354166666666667,0.98958333333333337,0.9458333333333333,0.9,0.82916666666666661,0.76041666666666663,0.68958333333333333,0.94969818913480886,0.94526315789473681,0.94052863436123357,0.93518518518518512,0.9321608040201006,0.92876712328767119,0.9274924471299093,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.7,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.837499999999999},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.012499999999999},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.149999999999999},13.9125,12.712499999999999,11.512499999999999]
[1600,72,20.774999999999999,10.35,19.912499999999998,10.050000000000001,19.05,9.75,{"$f":"U12*$I$13","v":18.149999999999999},9.4499999999999993,16.5,8.9624999999999986,14.924999999999999,8.5124999999999993,13.3125,8.0625,null,1.1541666666666666,1.10625,1.0583333333333333,1.0083333333333333,0.91666666666666663,0.82916666666666661,0.73958333333333337,0.49819494584837548,0.50470809792843696,0.51181102362204722,0.52066115702479343,0.5431818181818181,0.57035175879396982,0.60563380281690138,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.35},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.050000000000001},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":9.75},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.4499999999999993},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":8.9624999999999986},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.5124999999999993},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.0625}]
[null,67,21.150000000000002,14.025000000000002,20.100000000000001,13.6875,19.05,13.387500000000003,18,12.975,16.274999999999999,12.375,14.5875,11.737500000000001,12.9,11.100000000000001,null,1.175,1.1166666666666667,1.0583333333333333,1,0.90416666666666667,0.81041666666666667,0.71666666666666667,0.66312056737588654,0.68097014925373134,0.70275590551181111,0.72083333333333333,0.76036866359447008,0.80462724935732655,0.86046511627906985,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.025000000000002},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.6875},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.387500000000003},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.975},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.375},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.737500000000001},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.100000000000001}]
[null,62,19.912499999999998,17.212499999999995,18.862499999999997,16.799999999999997,17.850000000000001,16.387500000000003,{"$f":"U14*$I$13","v":16.837499999999999},15.975,15.412500000000001,14.737500000000001,14.0625,13.5,12.674999999999999,12.262500000000001,null,1.10625,1.0479166666666666,0.9916666666666667,0.93541666666666667,0.85625000000000007,0.78125,0.70416666666666661,0.86440677966101687,0.89065606361829031,0.91806722689075637,0.94877505567928733,0.95620437956204374,0.96,0.96745562130177531,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.212499999999995,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.799999999999997},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.387500000000003},15.975,14.737500000000001,13.5,12.262500000000001]
[null,57,19.5,18.450000000000003,18.674999999999997,17.625,17.8125,16.762500000000003,16.987500000000001,15.9,15.600000000000001,14.5875,14.287500000000001,13.312500000000002,12.9375,12.037500000000001,null,1.0833333333333333,1.0374999999999999,0.98958333333333337,0.94374999999999998,0.8666666666666667,0.79375000000000007,0.71875,0.94615384615384623,0.9437751004016065,0.94105263157894747,0.9359823399558499,0.93509615384615374,0.93175853018372701,0.93043478260869572,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.450000000000003,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.625},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.762500000000003},15.9,14.5875,13.312500000000002,12.037500000000001]
[1800,72,21.112499999999997,10.875,20.175000000000001,10.537500000000001,19.274999999999999,10.199999999999999,18.337500000000002,9.8625000000000025,16.6875,9.375,15.075000000000001,8.9250000000000007,13.5,8.4375,null,1.1729166666666666,1.1208333333333333,1.0708333333333333,1.01875,0.92708333333333337,0.83750000000000002,0.75,0.51509769094138547,0.52230483271375472,0.52918287937743191,0.53783231083844585,0.5617977528089888,0.59203980099502485,0.625,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":10.875},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.537500000000001},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.199999999999999},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":9.8625000000000025},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":9.375},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":8.9250000000000007},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":8.4375}]
[null,67,21.337499999999999,14.549999999999999,20.362499999999997,14.324999999999999,19.387500000000003,14.100000000000003,18.412500000000001,13.875,16.649999999999999,13.1625,14.924999999999999,12.487499999999999,13.200000000000001,11.850000000000001,null,1.1854166666666666,1.1312499999999999,1.0770833333333334,1.0229166666666667,0.92499999999999993,0.82916666666666661,0.73333333333333339,0.68189806678383125,0.70349907918968702,0.72727272727272729,0.75356415478615069,0.79054054054054057,0.83668341708542715,0.89772727272727271,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.549999999999999},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.324999999999999},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.100000000000003},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.875},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.1625},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.487499999999999},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":11.850000000000001}]
[null,62,20.512500000000003,18.262500000000003,19.537500000000001,17.850000000000001,18.524999999999999,17.4375,17.55,17.025000000000002,16.087499999999999,15.562499999999998,14.6625,14.137500000000001,13.237499999999999,12.75,null,1.1395833333333334,1.0854166666666667,1.0291666666666666,0.97499999999999998,0.89374999999999993,0.81458333333333333,0.73541666666666661,0.89031078610603287,0.91362763915547029,0.94129554655870451,0.97008547008547008,0.96736596736596736,0.96419437340153458,0.96317280453257803,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.262500000000003,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.850000000000001},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.4375},17.025000000000002,15.562499999999998,14.137500000000001,12.75]
[null,57,20.399999999999999,19.2,19.5,18.375,18.637499999999999,17.549999999999997,17.774999999999999,16.6875,16.3125,15.299999999999999,14.887500000000001,13.950000000000001,13.4625,12.5625,null,1.1333333333333333,1.0833333333333333,1.0354166666666667,0.98749999999999993,0.90625,0.82708333333333339,0.74791666666666667,0.94117647058823539,0.94230769230769229,0.94164989939637811,0.93881856540084396,0.93793103448275861,0.93702770780856426,0.93314763231197773,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.2,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.375},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.549999999999997},16.6875,15.299999999999999,13.950000000000001,12.5625]

{"sheet":"TCJD_60","index":13,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJD60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1600,72,{"$f":"R8*$I$13","v":22.705263157894741},{"$f":"IF(AM8>C8,C8,AM8)","v":10.768421052631581},{"$f":"S8*$I$13","v":22.010526315789473},{"$f":"IF(AN8>E8,E8,AN8)","v":10.578947368421051},{"$f":"T8*$I$13","v":21.347368421052629},{"$f":"IF(AO8>G8,G8,AO8)","v":10.389473684210525},{"$f":"U8*$I$13","v":20.684210526315791},{"$f":"IF(AP8>I8,I8,AP8)","v":10.199999999999999},{"$f":"V8*$I$13","v":18.978947368421053},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.378947368421052},{"$f":"W8*$I$13","v":17.305263157894736},{"$f":"IF(AR8>M8,M8,AR8)","v":8.621052631578948},{"$f":"X8*$I$13","v":15.600000000000001},{"$f":"IF(AS8>O8,O8,AS8)","v":7.863157894736843},null,1.26140350877193,1.2228070175438597,1.1859649122807017,1.1491228070175439,1.0543859649122806,0.96140350877192982,0.8666666666666667,0.47426981919332406,0.48063127690100427,0.48668639053254442,0.49312977099236638,0.49417637271214637,0.49817518248175185,0.50404858299595146,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.768421052631581},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.578947368421051},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.389473684210525},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.199999999999999},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.378947368421052},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.621052631578948},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":7.863157894736843}]
[null,67,20.589473684210525,12.978947368421052,19.8,{"$f":"IF(AN9>E9,E9,AN9)","v":12.631578947368419},19.042105263157893,{"$f":"IF(AO9>G9,G9,AO9)","v":12.315789473684211},{"$f":"U9*$I$13","v":17.96842105263158},{"$f":"IF(AP9>I9,I9,AP9)","v":11.968421052631578},17.052631578947366,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.526315789473683},15.852631578947371,{"$f":"IF(AR9>M9,M9,AR9)","v":11.052631578947368},14.684210526315789,{"$f":"IF(AS9>O9,O9,AS9)","v":10.610526315789475},null,1.143859649122807,1.1000000000000001,1.0578947368421052,0.99824561403508771,0.94736842105263153,0.88070175438596499,0.81578947368421051,0.63036809815950923,0.63795853269537472,0.64676616915422891,0.66608084358523723,0.67592592592592593,0.69721115537848599,0.72258064516129039,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.978947368421052},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.631578947368419},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.315789473684211},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.968421052631578},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.526315789473683},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.052631578947368},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":10.610526315789475}]
[null,62,20.147368421052629,16.294736842105262,19.294736842105262,15.915789473684208,18.442105263157895,15.56842105263158,{"$f":"U10*$I$13","v":17.589473684210528},15.189473684210528,16.484210526315792,14.494736842105263,15.410526315789474,13.831578947368421,14.336842105263157,13.168421052631579,null,1.119298245614035,1.0719298245614035,1.024561403508772,0.97719298245614039,0.9157894736842106,0.85614035087719298,0.79649122807017536,0.80877742946708475,0.82487725040916526,0.84417808219178081,0.86355475763016154,0.87931034482758608,0.89754098360655732,0.91850220264317195,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.294736842105262,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.915789473684208},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.56842105263158},15.189473684210528,14.494736842105263,13.831578947368421,13.168421052631579]
[null,57,17.621052631578948,17.273684210526319,17.96842105263158,17.02105263157895,18.315789473684212,16.800000000000004,{"$f":"U11*$I$13","v":18.663157894736845},16.547368421052632,17.810526315789474,15.694736842105264,16.989473684210527,14.873684210526317,16.168421052631579,14.052631578947368,null,0.97894736842105257,0.99824561403508771,1.0175438596491229,1.036842105263158,0.98947368421052628,0.94385964912280695,0.89824561403508774,0.98028673835125457,0.9472759226713533,0.91724137931034488,0.88663282571912005,0.88120567375886527,0.87546468401486999,0.869140625,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.273684210526319,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.02105263157895},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.800000000000004},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.547368421052632},15.694736842105264,14.873684210526317,14.052631578947368]
[1800,72,22.042105263157897,10.073684210526316,21.442105263157899,9.9473684210526319,20.810526315789474,9.8526315789473689,{"$f":"U12*$I$13","v":20.178947368421053},9.7263157894736842,18.852631578947371,9.2842105263157908,17.589473684210528,8.810526315789474,16.294736842105262,8.3684210526315788,null,1.224561403508772,1.1912280701754387,1.156140350877193,1.1210526315789473,1.0473684210526317,0.97719298245614039,0.90526315789473688,0.45702005730659023,0.46391752577319584,0.47344461305007585,0.48200312989045385,0.49246231155778891,0.50089766606822261,0.51356589147286824,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.073684210526316},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":9.9473684210526319},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":9.8526315789473689},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.7263157894736842},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.2842105263157908},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.810526315789474},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.3684210526315788}]
[null,67,21.063157894736843,13.45263157894737,20.305263157894736,13.2,19.547368421052632,12.947368421052632,18,12.252631578947366,17.589473684210528,12.221052631578948,16.389473684210525,11.778947368421052,15.221052631578949,11.336842105263157,null,1.1701754385964913,1.1280701754385964,1.0859649122807018,1,0.97719298245614039,0.91052631578947363,0.84561403508771937,0.63868065967016496,0.65007776049766719,0.66235864297253633,0.68070175438596481,0.69479353680430878,0.7186897880539499,0.74481327800829866,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.45263157894737},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.2},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":12.947368421052632},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.252631578947366},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.221052631578948},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.778947368421052},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.336842105263157}]
[null,62,20.747368421052631,17.11578947368421,19.894736842105264,16.768421052631581,19.073684210526316,16.421052631578949,{"$f":"U14*$I$13","v":18.252631578947369},16.073684210526316,17.147368421052629,15.252631578947366,16.073684210526316,14.431578947368422,15,13.642105263157895,null,1.1526315789473685,1.1052631578947369,1.0596491228070175,1.0140350877192983,0.95263157894736838,0.89298245614035088,0.83333333333333337,0.82496194824961944,0.84285714285714286,0.86092715231788086,0.88062283737024227,0.88950276243093918,0.89783889980353637,0.90947368421052632,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.11578947368421,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.768421052631581},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.421052631578949},16.073684210526316,15.252631578947366,14.431578947368422,13.642105263157895]
[null,57,19.042105263157893,18.442105263157895,18.694736842105264,17.621052631578944,18.315789473684212,16.831578947368424,17.96842105263158,16.010526315789477,17.052631578947366,15.126315789473681,16.168421052631579,14.305263157894736,15.315789473684211,13.452631578947368,null,1.0578947368421052,1.0385964912280703,1.0175438596491229,0.99824561403508771,0.94736842105263153,0.89824561403508774,0.85087719298245612,0.96849087893864017,0.94256756756756743,0.91896551724137931,0.89103690685413017,0.88703703703703696,0.88476562499999989,0.87835051546391751,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.442105263157895,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.621052631578944},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.831578947368424},16.010526315789477,15.126315789473681,14.305263157894736,13.452631578947368]
[2000,72,21.410526315789472,9.3473684210526322,20.842105263157897,9.3157894736842124,20.242105263157892,9.284210526315789,19.642105263157895,9.284210526315789,18.757894736842104,9.1578947368421044,17.873684210526314,9.0315789473684198,16.989473684210527,8.905263157894737,null,1.1894736842105262,1.1578947368421053,1.1245614035087719,1.0912280701754387,1.0421052631578946,0.99298245614035086,0.94385964912280695,0.43657817109144548,0.44696969696969696,0.45865834633385338,0.47266881028938901,0.48821548821548821,0.5053003533568905,0.52416356877323422,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":9.3473684210526322},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":9.3157894736842124},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":9.284210526315789},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":9.284210526315789},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":9.1578947368421044},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.0315789473684198},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":8.905263157894737}]
[null,67,21.536842105263158,13.957894736842105,20.810526315789474,13.768421052631577,20.084210526315786,13.54736842105263,19.326315789473686,13.357894736842104,18.126315789473686,12.915789473684212,16.926315789473684,12.505263157894737,15.726315789473682,12.094736842105261,null,1.1964912280701754,1.156140350877193,1.1157894736842104,1.0736842105263158,1.0070175438596491,0.94035087719298249,0.87368421052631573,0.64809384164222872,0.66160849772382391,0.67452830188679247,0.69117647058823517,0.71254355400696867,0.73880597014925375,0.76907630522088355,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":13.957894736842105},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":13.768421052631577},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.54736842105263},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.357894736842104},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":12.915789473684212},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.505263157894737},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.094736842105261}]
[null,62,21.315789473684209,17.936842105263153,20.494736842105269,17.589473684210532,19.705263157894738,17.273684210526319,18.884210526315787,16.926315789473684,17.778947368421051,15.978947368421052,16.736842105263158,15.063157894736841,15.694736842105264,14.115789473684211,null,1.1842105263157894,1.1385964912280704,1.0947368421052632,1.0491228070175438,0.987719298245614,0.92982456140350878,0.87192982456140355,0.84148148148148139,0.85824345146379044,0.87660256410256421,0.89632107023411378,0.89875666074600358,0.9,0.89939637826961771,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.936842105263153,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.589473684210532},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.273684210526319},16.926315789473684,15.978947368421052,15.063157894736841,14.115789473684211]
[null,57,20.463157894736842,19.610526315789475,19.389473684210525,18.221052631578949,18.347368421052632,16.86315789473684,17.273684210526319,15.473684210526319,16.294736842105262,14.589473684210526,15.378947368421054,13.736842105263159,14.431578947368422,12.852631578947369,null,1.1368421052631579,1.0771929824561404,1.0192982456140351,0.95964912280701764,0.90526315789473688,0.8543859649122808,0.80175438596491233,0.95833333333333337,0.93973941368078184,0.91910499139414792,0.89579524680073119,0.89534883720930236,0.89322381930184802,0.89059080962800874,1.06,1.06,1.06,1.06,1.06,1.06,1.06,19.610526315789475,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.221052631578949},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":16.86315789473684},15.473684210526319,14.589473684210526,13.736842105263159,12.852631578947369]

{"sheet":"TCJF_24","index":14,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJF24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[600,72,{"$f":"R8*$I$13","v":20.10483870967742},{"$f":"IF(AM8>C8,C8,AM8)","v":10.451612903225808},{"$f":"S8*$I$13","v":19.451612903225804},{"$f":"IF(AN8>E8,E8,AN8)","v":10.088709677419354},{"$f":"T8*$I$13","v":18.798387096774192},{"$f":"IF(AO8>G8,G8,AO8)","v":9.7258064516129039},{"$f":"U8*$I$13","v":18.14516129032258},{"$f":"IF(AP8>I8,I8,AP8)","v":9.362903225806452},{"$f":"V8*$I$13","v":17.201612903225804},{"$f":"IF(AQ8>K8,K8,AQ8)","v":8.8548387096774164},{"$f":"W8*$I$13","v":16.18548387096774},{"$f":"IF(AR8>M8,M8,AR8)","v":8.4193548387096762},{"$f":"X8*$I$13","v":15.169354838709676},{"$f":"IF(AS8>O8,O8,AS8)","v":7.911290322580645},null,1.1169354838709677,1.0806451612903225,1.0443548387096773,1.0080645161290323,0.95564516129032251,0.89919354838709675,0.84274193548387089,0.5198555956678701,0.51865671641791045,0.51737451737451745,0.51600000000000001,0.51476793248945141,0.52017937219730936,0.52153110047846896,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.451612903225808},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.088709677419354},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.7258064516129039},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.362903225806452},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":8.8548387096774164},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.4193548387096762},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":7.911290322580645}]
[null,67,{"$f":"R9*$I$13","v":18.653225806451609},11.685483870967742,18.072580645161288,{"$f":"IF(AN9>E9,E9,AN9)","v":11.395161290322578},17.491935483870968,{"$f":"IF(AO9>G9,G9,AO9)","v":11.104838709677418},{"$f":"U9*$I$13","v":16.911290322580648},{"$f":"IF(AP9>I9,I9,AP9)","v":10.88709677419355},15.96774193548387,{"$f":"IF(AQ9>K9,K9,AQ9)","v":10.306451612903224},15.024193548387096,{"$f":"IF(AR9>M9,M9,AR9)","v":9.7983870967741939},14.008064516129032,{"$f":"IF(AS9>O9,O9,AS9)","v":9.2903225806451619},null,1.036290322580645,1.004032258064516,0.97177419354838712,0.93951612903225812,0.88709677419354838,0.83467741935483863,0.77822580645161288,0.6264591439688717,0.63052208835341361,0.63485477178423233,0.64377682403433478,0.64545454545454539,0.65217391304347827,0.66321243523316065,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":11.685483870967742},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":11.395161290322578},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":11.104838709677418},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":10.88709677419355},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":10.306451612903224},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":9.7983870967741939},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":9.2903225806451619}]
[null,62,17.274193548387096,11.830645161290322,16.693548387096772,11.830645161290322,16.112903225806452,11.830645161290324,{"$f":"U10*$I$13","v":15.532258064516128},11.830645161290322,14.588709677419356,11.540322580645162,13.64516129032258,11.17741935483871,12.701612903225804,10.887096774193546,null,0.95967741935483875,0.92741935483870963,0.89516129032258063,0.86290322580645151,0.81048387096774199,0.75806451612903225,0.70564516129032251,0.68487394957983194,0.70869565217391306,0.73423423423423428,0.76168224299065423,0.79104477611940294,0.81914893617021278,0.8571428571428571,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.830645161290322,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":11.830645161290322},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":11.830645161290324},11.830645161290322,11.540322580645162,11.17741935483871,10.887096774193546]
[null,57,15.82258064516129,11.830645161290322,15.241935483870968,11.830645161290324,14.661290322580644,11.830645161290322,{"$f":"U11*$I$13","v":14.153225806451612},11.830645161290322,13.354838709677418,11.830645161290324,12.629032258064514,11.830645161290322,11.830645161290322,11.830645161290322,null,0.87903225806451613,0.84677419354838712,0.81451612903225801,0.78629032258064513,0.74193548387096764,0.70161290322580638,0.657258064516129,0.74770642201834858,0.77619047619047621,0.80693069306930698,0.83589743589743593,0.88586956521739146,0.93678160919540243,1,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.830645161290322,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":11.830645161290324},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":11.830645161290322},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":11.830645161290322},11.830645161290324,11.830645161290322,11.830645161290322]
[800,72,21.411290322580644,11.10483870967742,20.758064516129032,10.814516129032256,20.10483870967742,10.451612903225808,{"$f":"U12*$I$13","v":19.451612903225804},10.161290322580642,18.29032258064516,9.6532258064516121,17.201612903225804,9.1451612903225783,16.112903225806452,8.6370967741935498,null,1.189516129032258,1.153225806451613,1.1169354838709677,1.0806451612903225,1.0161290322580645,0.95564516129032251,0.89516129032258063,0.51864406779661021,0.52097902097902093,0.5198555956678701,0.52238805970149249,0.52777777777777779,0.53164556962025311,0.53603603603603611,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.10483870967742},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.814516129032256},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.451612903225808},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.161290322580642},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.6532258064516121},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.1451612903225783},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.6370967741935498}]
[null,67,20.032258064516132,11.758064516129032,19.306451612903224,11.61290322580645,18.653225806451609,11.467741935483868,18,11.32258064516129,16.983870967741936,11.104838709677422,15.895161290322578,10.814516129032256,14.806451612903224,10.596774193548386,null,1.1129032258064517,1.0725806451612903,1.036290322580645,1,0.94354838709677413,0.88306451612903214,0.82258064516129026,0.58695652173913038,0.60150375939849621,0.61478599221789887,0.62903225806451613,0.65384615384615397,0.68036529680365299,0.71568627450980393,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":11.758064516129032},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":11.61290322580645},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":11.467741935483868},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":11.32258064516129},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":11.104838709677422},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":10.814516129032256},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":10.596774193548386}]
[null,62,18.43548387096774,11.830645161290324,17.85483870967742,11.830645161290322,17.201612903225804,11.830645161290322,{"$f":"U14*$I$13","v":16.548387096774192},11.830645161290322,15.532258064516128,11.685483870967744,14.443548387096774,11.540322580645164,13.354838709677418,11.39516129032258,null,1.0241935483870968,0.99193548387096775,0.95564516129032251,0.91935483870967738,0.86290322580645151,0.80241935483870963,0.74193548387096764,0.64173228346456701,0.66260162601626016,0.68776371308016881,0.71491228070175439,0.75233644859813098,0.79899497487437199,0.85326086956521741,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.830645161290324,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":11.830645161290322},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":11.830645161290322},11.830645161290322,11.685483870967744,11.540322580645164,11.39516129032258]
[null,57,17.346774193548384,11.830645161290322,16.766129032258064,11.830645161290322,16.258064516129028,11.83064516129032,15.67741935483871,11.830645161290324,14.806451612903224,11.830645161290322,14.008064516129032,11.830645161290322,13.137096774193548,11.830645161290322,null,0.96370967741935476,0.93145161290322587,0.90322580645161277,0.87096774193548387,0.82258064516129026,0.77822580645161288,0.72983870967741937,0.68200836820083688,0.7056277056277056,0.72767857142857151,0.75462962962962965,0.7990196078431373,0.84455958549222798,0.90055248618784522,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.830645161290322,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":11.830645161290322},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":11.83064516129032},11.830645161290324,11.830645161290322,11.830645161290322,11.830645161290322]
[1000,72,22.79032258064516,11.758064516129032,22.064516129032256,11.54032258064516,21.411290322580644,11.25,20.68548387096774,10.959677419354838,19.451612903225804,10.451612903225806,18.217741935483872,9.870967741935484,16.983870967741936,9.362903225806452,null,1.2661290322580645,1.225806451612903,1.189516129032258,1.1491935483870968,1.0806451612903225,1.0120967741935485,0.94354838709677413,0.51592356687898089,0.52302631578947367,0.52542372881355937,0.52982456140350875,0.53731343283582089,0.54183266932270913,0.55128205128205132,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.758064516129032},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.54032258064516},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.25},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.959677419354838},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.451612903225806},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.870967741935484},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.362903225806452}]
[null,67,21.338709677419352,11.830645161290322,20.612903225806448,11.83064516129032,19.81451612903226,11.830645161290324,19.088709677419356,11.830645161290322,17.927419354838708,11.830645161290322,16.766129032258064,11.830645161290322,15.67741935483871,11.830645161290324,null,1.1854838709677418,1.1451612903225805,1.1008064516129032,1.060483870967742,0.99596774193548376,0.93145161290322587,0.87096774193548387,0.55442176870748305,0.573943661971831,0.59706959706959706,0.61977186311787069,0.65991902834008098,0.7056277056277056,0.75462962962962965,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":11.830645161290322},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":11.83064516129032},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":11.830645161290324},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":11.830645161290322},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":11.830645161290322},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":11.830645161290322},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":11.830645161290324}]
[null,62,19.66935483870968,11.830645161290324,18.943548387096776,11.830645161290322,18.29032258064516,11.830645161290322,17.564516129032256,11.830645161290322,16.403225806451616,11.830645161290326,15.241935483870968,11.830645161290324,14.080645161290322,11.830645161290324,null,1.092741935483871,1.0524193548387097,1.0161290322580645,0.97580645161290314,0.91129032258064524,0.84677419354838712,0.782258064516129,0.60147601476014756,0.62452107279693481,0.64682539682539686,0.67355371900826455,0.72123893805309736,0.77619047619047621,0.84020618556701043,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.830645161290324,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":11.830645161290322},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":11.830645161290322},11.830645161290322,11.830645161290326,11.830645161290324,11.830645161290324]
[null,57,18.943548387096776,11.830645161290322,18.362903225806452,11.830645161290324,17.782258064516128,11.830645161290322,17.201612903225804,11.830645161290322,16.258064516129028,11.83064516129032,15.387096774193546,11.830645161290322,14.443548387096774,11.830645161290324,null,1.0524193548387097,1.0201612903225807,0.98790322580645162,0.95564516129032251,0.90322580645161277,0.85483870967741926,0.80241935483870963,0.62452107279693481,0.64426877470355737,0.66530612244897958,0.68776371308016881,0.72767857142857151,0.76886792452830199,0.81909547738693478,1.06,1.06,1.06,1.06,1.06,1.06,1.06,11.830645161290322,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":11.830645161290324},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":11.830645161290322},11.830645161290322,11.83064516129032,11.830645161290322,11.830645161290324]

{"sheet":"TCJF_30","index":15,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJF30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[800,72,{"$f":"R8*$I$13","v":21.405405405405407},{"$f":"IF(AM8>C8,C8,AM8)","v":10.45945945945946},{"$f":"S8*$I$13","v":20.614864864864863},{"$f":"IF(AN8>E8,E8,AN8)","v":10.094594594594595},{"$f":"T8*$I$13","v":19.763513513513516},{"$f":"IF(AO8>G8,G8,AO8)","v":9.7297297297297316},{"$f":"U8*$I$13","v":18.912162162162161},{"$f":"IF(AP8>I8,I8,AP8)","v":9.3648648648648649},{"$f":"V8*$I$13","v":17.939189189189189},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.121621621621621},{"$f":"W8*$I$13","v":17.027027027027028},{"$f":"IF(AR8>M8,M8,AR8)","v":8.878378378378379},{"$f":"X8*$I$13","v":16.054054054054053},{"$f":"IF(AS8>O8,O8,AS8)","v":8.5743243243243228},null,1.1891891891891893,1.1452702702702702,1.097972972972973,1.0506756756756757,0.9966216216216216,0.94594594594594594,0.89189189189189177,0.48863636363636359,0.48967551622418887,0.49230769230769234,0.49517684887459806,0.50847457627118642,0.52142857142857146,0.53409090909090906,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.45945945945946},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.094594594594595},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.7297297297297316},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.3648648648648649},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.121621621621621},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.878378378378379},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.5743243243243228}]
[null,67,{"$f":"R9*$I$13","v":20.006756756756754},12.709459459459456,19.094594594594593,{"$f":"IF(AN9>E9,E9,AN9)","v":12.405405405405403},18.182432432432432,{"$f":"IF(AO9>G9,G9,AO9)","v":12.101351351351351},{"$f":"U9*$I$13","v":17.270270270270267},{"$f":"IF(AP9>I9,I9,AP9)","v":11.736486486486486},16.358108108108105,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.371621621621619},15.445945945945944,{"$f":"IF(AR9>M9,M9,AR9)","v":11.006756756756756},14.594594594594593,{"$f":"IF(AS9>O9,O9,AS9)","v":10.581081081081079},null,1.1114864864864864,1.0608108108108107,1.0101351351351351,0.95945945945945932,0.90878378378378366,0.858108108108108,0.81081081081081074,0.63525835866261393,0.64968152866242035,0.66555183946488294,0.67957746478873249,0.69516728624535318,0.71259842519685046,0.72499999999999998,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.709459459459456},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.405405405405403},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.101351351351351},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.736486486486486},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.371621621621619},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.006756756756756},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":10.581081081081079}]
[null,62,18.304054054054053,14.837837837837835,17.513513513513512,14.594594594594593,16.722972972972972,14.290540540540539,{"$f":"U10*$I$13","v":15.932432432432432},13.986486486486486,14.898648648648647,13.195945945945944,13.804054054054054,12.466216216216218,12.77027027027027,11.736486486486488,null,1.0168918918918919,0.97297297297297292,0.92905405405405406,0.88513513513513509,0.82770270270270263,0.76689189189189189,0.70945945945945943,0.81063122923588027,0.83333333333333326,0.8545454545454545,0.87786259541984735,0.88571428571428568,0.90308370044052866,0.91904761904761911,1.06,1.06,1.06,1.06,1.06,1.06,1.06,14.837837837837835,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":14.594594594594593},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.290540540540539},13.986486486486486,13.195945945945944,12.466216216216218,11.736486486486488]
[null,57,17.148648648648646,16.47972972972973,16.601351351351351,15.93243243243243,16.054054054054053,15.324324324324323,{"$f":"U11*$I$13","v":15.506756756756754},14.777027027027026,14.533783783783782,13.864864864864865,13.560810810810811,13.013513513513512,12.648648648648649,12.162162162162161,null,0.95270270270270263,0.92229729729729726,0.89189189189189177,0.8614864864864864,0.80743243243243235,0.7533783783783784,0.70270270270270274,0.96099290780141855,0.95970695970695963,0.95454545454545459,0.95294117647058829,0.95397489539748959,0.95964125560538105,0.96153846153846145,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.47972972972973,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":15.93243243243243},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":15.324324324324323},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":14.777027027027026},13.864864864864865,13.013513513513512,12.162162162162161]
[1000,72,22.135135135135133,11.49324324324324,21.283783783783782,11.128378378378379,20.432432432432432,10.702702702702704,{"$f":"U12*$I$13","v":19.641891891891888},10.337837837837837,18.608108108108109,10.094594594594597,17.635135135135133,9.8513513513513509,16.662162162162161,9.6081081081081088,null,1.2297297297297296,1.1824324324324325,1.1351351351351351,1.091216216216216,1.0337837837837838,0.97972972972972971,0.92567567567567555,0.51923076923076916,0.52285714285714291,0.52380952380952384,0.52631578947368429,0.54248366013071903,0.55862068965517242,0.57664233576642343,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.49324324324324},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.128378378378379},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.702702702702704},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.337837837837837},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.094594594594597},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8513513513513509},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6081081081081088}]
[null,67,20.736486486486484,14.168918918918916,19.824324324324323,13.864864864864863,18.912162162162161,13.499999999999998,18,13.135135135135135,17.027027027027028,12.831081081081084,16.114864864864863,12.466216216216216,15.141891891891889,12.16216216216216,null,1.152027027027027,1.1013513513513513,1.0506756756756757,1,0.94594594594594594,0.89527027027027017,0.84121621621621612,0.68328445747800581,0.69938650306748462,0.7138263665594855,0.72972972972972971,0.75357142857142867,0.77358490566037741,0.80321285140562249,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.168918918918916},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.864864864864863},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.499999999999998},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.135135135135135},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.831081081081084},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.466216216216216},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.16216216216216}]
[null,62,19.033783783783782,16.662162162162161,18.243243243243242,16.236486486486484,17.452702702702702,15.871621621621623,{"$f":"U14*$I$13","v":16.662162162162161},15.445945945945946,15.749999999999998,14.655405405405405,14.837837837837837,13.925675675675674,13.925675675675674,13.135135135135135,null,1.0574324324324325,1.0135135135135134,0.96959459459459452,0.92567567567567555,0.87499999999999989,0.82432432432432423,0.77364864864864857,0.87539936102236415,0.89,0.90940766550522656,0.92700729927007297,0.93050193050193064,0.93852459016393441,0.94323144104803502,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.662162162162161,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.236486486486484},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.871621621621623},15.445945945945946,14.655405405405405,13.925675675675674,13.135135135135135]
[null,57,18.121621621621621,17.695945945945944,17.513513513513512,17.027027027027025,16.905405405405403,16.358108108108105,16.297297297297298,15.75,15.385135135135135,14.898648648648647,14.472972972972974,14.108108108108109,13.560810810810811,13.317567567567567,null,1.0067567567567568,0.97297297297297292,0.93918918918918914,0.90540540540540537,0.85472972972972971,0.80405405405405406,0.7533783783783784,0.97651006711409394,0.97222222222222221,0.96762589928057552,0.96641791044776115,0.96837944664031617,0.97478991596638653,0.98206278026905824,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.695945945945944,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.027027027027025},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.358108108108105},15.75,14.898648648648647,14.108108108108109,13.317567567567567]
[1200,72,22.804054054054053,12.527027027027026,21.952702702702702,12.101351351351349,21.162162162162158,11.675675675675674,20.310810810810811,11.25,19.277027027027025,11.067567567567567,18.243243243243242,10.824324324324325,17.20945945945946,10.641891891891891,null,1.2668918918918919,1.2195945945945945,1.1756756756756754,1.1283783783783783,1.0709459459459458,1.0135135135135134,0.95608108108108103,0.54933333333333334,0.55124653739612184,0.55172413793103448,0.55389221556886226,0.57413249211356465,0.59333333333333338,0.61837455830388688,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.527027027027026},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.101351351351349},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.675675675675674},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.25},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.067567567567567},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.824324324324325},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.641891891891891}]
[null,67,21.46621621621621,15.628378378378375,20.554054054054049,15.263513513513512,19.641891891891888,14.898648648648647,18.72972972972973,14.533783783783782,17.695945945945947,14.22972972972973,16.722972972972972,13.986486486486484,15.749999999999998,13.682432432432432,null,1.1925675675675673,1.1418918918918917,1.091216216216216,1.0405405405405406,0.98310810810810811,0.92905405405405406,0.87499999999999989,0.72804532577903691,0.74260355029585812,0.75851393188854499,0.77597402597402587,0.8041237113402061,0.83636363636363631,0.86872586872586877,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.628378378378375},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.263513513513512},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.898648648648647},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.533783783783782},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.22972972972973},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.986486486486484},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.682432432432432}]
[null,62,19.763513513513516,18.486486486486488,18.972972972972972,17.939189189189186,18.121621621621621,17.452702702702702,17.331081081081081,16.966216216216214,16.601351351351351,16.175675675675674,15.810810810810809,15.385135135135133,15.081081081081081,14.594594594594593,null,1.097972972972973,1.0540540540540539,1.0067567567567568,0.96283783783783783,0.92229729729729726,0.87837837837837829,0.83783783783783783,0.93538461538461537,0.94551282051282048,0.96308724832214765,0.97894736842105257,0.97435897435897434,0.97307692307692306,0.96774193548387089,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.486486486486488,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.939189189189186},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.452702702702702},16.966216216216214,16.175675675675674,15.385135135135133,14.594594594594593]
[null,57,19.155405405405403,18.912162162162161,18.425675675675677,18.182432432432432,17.756756756756754,17.452702702702702,17.087837837837839,16.722972972972972,16.175675675675677,15.932432432432432,15.324324324324323,15.141891891891889,14.472972972972974,14.412162162162161,null,1.064189189189189,1.0236486486486487,0.9864864864864864,0.94932432432432434,0.89864864864864868,0.85135135135135132,0.80405405405405406,0.98730158730158735,0.98679867986798675,0.98287671232876717,0.97864768683274017,0.98496240601503748,0.98809523809523803,0.995798319327731,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.912162162162161,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.182432432432432},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.452702702702702},16.722972972972972,15.932432432432432,15.141891891891889,14.412162162162161]

{"sheet":"TCJF_36","index":16,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJF36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1000,72,{"$f":"R8*$I$13","v":21.121387283236995},{"$f":"IF(AM8>C8,C8,AM8)","v":10.872832369942197},{"$f":"S8*$I$13","v":20.341040462427745},{"$f":"IF(AN8>E8,E8,AN8)","v":10.508670520231213},{"$f":"T8*$I$13","v":19.612716763005782},{"$f":"IF(AO8>G8,G8,AO8)","v":10.092485549132947},{"$f":"U8*$I$13","v":18.832369942196532},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7283236994219653},{"$f":"V8*$I$13","v":17.791907514450866},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3121387283236974},{"$f":"W8*$I$13","v":16.699421965317921},{"$f":"IF(AR8>M8,M8,AR8)","v":8.8959537572254348},{"$f":"X8*$I$13","v":15.658959537572255},{"$f":"IF(AS8>O8,O8,AS8)","v":8.4277456647398843},null,1.1734104046242775,1.1300578034682081,1.0895953757225434,1.046242774566474,0.98843930635838151,0.9277456647398844,0.86994219653179194,0.51477832512315269,0.51662404092071612,0.5145888594164455,0.51657458563535907,0.52339181286549696,0.53271028037383183,0.53820598006644516,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.872832369942197},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.508670520231213},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.092485549132947},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7283236994219653},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3121387283236974},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.8959537572254348},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.4277456647398843}]
[null,67,{"$f":"R9*$I$13","v":19.508670520231213},12.901734104046243,18.884393063583815,{"$f":"IF(AN9>E9,E9,AN9)","v":12.589595375722544},18.20809248554913,{"$f":"IF(AO9>G9,G9,AO9)","v":12.277456647398845},{"$f":"U9*$I$13","v":17.531791907514453},{"$f":"IF(AP9>I9,I9,AP9)","v":11.965317919075144},16.595375722543352,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.497109826589597},15.658959537572255,{"$f":"IF(AR9>M9,M9,AR9)","v":11.080924855491329},14.722543352601157,{"$f":"IF(AS9>O9,O9,AS9)","v":10.61271676300578},null,1.0838150289017341,1.0491329479768785,1.0115606936416184,0.97398843930635848,0.9219653179190751,0.86994219653179194,0.81791907514450868,0.66133333333333333,0.66666666666666674,0.67428571428571438,0.6824925816023738,0.69278996865203768,0.70764119601328901,0.72084805653710238,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.901734104046243},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.589595375722544},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.277456647398845},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.965317919075144},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.497109826589597},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.080924855491329},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":10.61271676300578}]
[null,62,18.156069364161848,13.265895953757223,17.479768786127167,13.265895953757225,16.803468208092482,13.265895953757225,{"$f":"U10*$I$13","v":16.127167630057802},13.265895953757225,15.242774566473987,13.109826589595373,14.410404624277456,12.953757225433526,13.526011560693641,12.745664739884393,null,1.0086705202312138,0.97109826589595372,0.93352601156069348,0.89595375722543347,0.84682080924855485,0.80057803468208089,0.75144508670520227,0.7306590257879656,0.7589285714285714,0.78947368421052644,0.82258064516129037,0.86006825938566545,0.89891696750902528,0.94230769230769229,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.265895953757223,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":13.265895953757225},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":13.265895953757225},13.265895953757225,13.109826589595373,12.953757225433526,12.745664739884393]
[null,57,16.907514450867051,13.265895953757225,16.439306358381504,13.265895953757227,15.971098265895954,13.265895953757227,{"$f":"U11*$I$13","v":15.450867052023121},13.265895953757225,14.722543352601157,13.265895953757227,13.99421965317919,13.265895953757225,13.265895953757225,13.265895953757225,null,0.93930635838150289,0.91329479768786126,0.88728323699421963,0.85838150289017334,0.81791907514450868,0.7774566473988439,0.73699421965317913,0.7846153846153846,0.80696202531645567,0.83061889250814336,0.85858585858585856,0.90106007067137805,0.94795539033457255,1,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.265895953757225,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":13.265895953757227},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":13.265895953757227},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":13.265895953757225},13.265895953757227,13.265895953757225,13.265895953757225]
[1200,72,21.74566473988439,11.289017341040461,20.913294797687865,10.924855491329481,20.132947976878615,10.560693641618498,{"$f":"U12*$I$13","v":19.300578034682083},10.248554913294797,18.20809248554913,9.7283236994219635,17.115606936416182,9.2601156069364148,16.023121387283236,8.7398843930635834,null,1.2080924855491328,1.1618497109826591,1.1184971098265897,1.0722543352601157,1.0115606936416184,0.95086705202312127,0.89017341040462428,0.51913875598086123,0.52238805970149249,0.52454780361757103,0.53099730458221017,0.53428571428571425,0.54103343465045595,0.54545454545454541,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.289017341040461},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.924855491329481},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.560693641618498},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.248554913294797},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.7283236994219635},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.2601156069364148},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.7398843930635834}]
[null,67,19.97687861271676,13.109826589595373,19.300578034682083,12.953757225433526,18.676300578034681,12.797687861271678,18,12.641618497109826,17.01156069364162,12.173410404624278,16.023121387283236,11.757225433526012,15.034682080924854,11.289017341040461,null,1.1098265895953756,1.0722543352601157,1.0375722543352601,1,0.94508670520231219,0.89017341040462428,0.83526011560693636,0.65625,0.67115902964959562,0.6852367688022285,0.70231213872832365,0.71559633027522929,0.73376623376623384,0.75086505190311414,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.109826589595373},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":12.953757225433526},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":12.797687861271678},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.641618497109826},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.173410404624278},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.757225433526012},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.289017341040461}]
[null,62,18.624277456647398,13.265895953757227,17.947976878612717,13.265895953757225,17.219653179190754,13.265895953757227,{"$f":"U14*$I$13","v":16.491329479768783},13.265895953757223,15.606936416184972,13.213872832369942,14.722543352601157,13.109826589595377,13.83815028901734,13.005780346820808,null,1.0346820809248554,0.99710982658959535,0.95664739884393069,0.9161849710982658,0.86705202312138729,0.81791907514450868,0.76878612716763006,0.7122905027932962,0.73913043478260865,0.7703927492447129,0.80441640378548895,0.84666666666666657,0.89045936395759717,0.93984962406015038,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.265895953757227,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":13.265895953757225},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":13.265895953757227},13.265895953757223,13.213872832369942,13.109826589595377,13.005780346820808]
[null,57,17.791907514450866,13.265895953757225,17.271676300578036,13.265895953757225,16.751445086705203,13.265895953757225,16.23121387283237,13.265895953757225,15.450867052023121,13.265895953757225,14.670520231213873,13.265895953757227,13.890173410404623,13.265895953757225,null,0.98843930635838151,0.95953757225433534,0.93063583815028905,0.90173410404624277,0.85838150289017334,0.81502890173410403,0.7716763005780346,0.74561403508771928,0.7680722891566264,0.7919254658385092,0.81730769230769229,0.85858585858585856,0.9042553191489362,0.9550561797752809,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.265895953757225,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":13.265895953757225},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":13.265895953757225},13.265895953757225,13.265895953757225,13.265895953757227,13.265895953757225]
[1400,72,22.369942196531792,11.653179190751445,21.485549132947973,11.341040462427745,20.601156069364162,11.080924855491329,19.716763005780344,10.76878612716763,18.624277456647398,10.196531791907516,17.479768786127167,9.6242774566473965,16.335260115606935,9.0520231213872826,null,1.2427745664739884,1.1936416184971097,1.1445086705202312,1.0953757225433525,1.0346820809248554,0.97109826589595372,0.90751445086705196,0.52093023255813953,0.52784503631961266,0.53787878787878785,0.54617414248021112,0.54748603351955316,0.55059523809523803,0.55414012738853502,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.653179190751445},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.341040462427745},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.080924855491329},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.76878612716763},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.196531791907516},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.6242774566473965},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.0520231213872826}]
[null,67,20.445086705202307,13.265895953757223,19.76878612716763,13.265895953757225,19.092485549132949,13.265895953757225,18.416184971098264,13.265895953757227,17.375722543352598,12.849710982658957,16.335260115606935,12.433526011560692,15.346820809248555,12.01734104046243,null,1.1358381502890171,1.0982658959537572,1.0606936416184971,1.023121387283237,0.96531791907514441,0.90751445086705196,0.85260115606936415,0.64885496183206115,0.67105263157894735,0.69482288828337868,0.72033898305084754,0.73952095808383234,0.76114649681528657,0.78305084745762721,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":13.265895953757223},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":13.265895953757225},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.265895953757225},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.265895953757227},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":12.849710982658957},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.433526011560692},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.01734104046243}]
[null,62,19.144508670520231,13.265895953757227,18.364161849710982,13.265895953757227,17.635838150289015,13.265895953757225,16.907514450867051,13.265895953757225,15.971098265895954,13.265895953757227,15.086705202312139,13.265895953757225,14.15028901734104,13.265895953757225,null,1.0635838150289016,1.0202312138728322,0.97976878612716756,0.93930635838150289,0.88728323699421963,0.83815028901734101,0.78612716763005774,0.69293478260869568,0.72237960339943352,0.75221238938053103,0.7846153846153846,0.83061889250814336,0.87931034482758619,0.9375,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.265895953757227,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":13.265895953757227},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":13.265895953757225},13.265895953757225,13.265895953757227,13.265895953757225,13.265895953757225]
[null,57,18.624277456647398,13.265895953757227,18.104046242774565,13.265895953757227,17.531791907514453,13.265895953757227,16.959537572254337,13.265895953757227,16.127167630057802,13.265895953757225,15.294797687861271,13.265895953757227,14.462427745664741,13.265895953757225,null,1.0346820809248554,1.0057803468208091,0.97398843930635848,0.94219653179190754,0.89595375722543347,0.8497109826589595,0.80346820809248554,0.7122905027932962,0.73275862068965525,0.75667655786350141,0.78220858895705514,0.82258064516129037,0.86734693877551028,0.91726618705035967,1.06,1.06,1.06,1.06,1.06,1.06,1.06,13.265895953757227,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":13.265895953757227},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":13.265895953757227},13.265895953757227,13.265895953757225,13.265895953757227,13.265895953757225]

{"sheet":"TCJF_42","index":17,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJF42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1200,72,{"$f":"R8*$I$13","v":21.32846715328467},{"$f":"IF(AM8>C8,C8,AM8)","v":10.46715328467153},{"$f":"S8*$I$13","v":20.715328467153281},{"$f":"IF(AN8>E8,E8,AN8)","v":10.160583941605838},{"$f":"T8*$I$13","v":20.102189781021895},{"$f":"IF(AO8>G8,G8,AO8)","v":9.897810218978103},{"$f":"U8*$I$13","v":19.48905109489051},{"$f":"IF(AP8>I8,I8,AP8)","v":9.5912408759124066},{"$f":"V8*$I$13","v":18.306569343065689},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.2408759124087574},{"$f":"W8*$I$13","v":17.167883211678834},{"$f":"IF(AR8>M8,M8,AR8)","v":8.89051094890511},{"$f":"X8*$I$13","v":16.029197080291972},{"$f":"IF(AS8>O8,O8,AS8)","v":8.540145985401459},null,1.1849148418491484,1.1508515815085156,1.1167883211678831,1.0827250608272505,1.0170316301703162,0.95377128953771295,0.89051094890510951,0.4907597535934291,0.4904862579281184,0.49237472766884538,0.4921348314606741,0.50478468899521534,0.51785714285714279,0.53278688524590156,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.46715328467153},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.160583941605838},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.897810218978103},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.5912408759124066},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.2408759124087574},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.89051094890511},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.540145985401459}]
[null,67,{"$f":"R9*$I$13","v":20.058394160583941},13.313868613138686,19.226277372262771,{"$f":"IF(AN9>E9,E9,AN9)","v":12.963503649635037},18.43795620437956,{"$f":"IF(AO9>G9,G9,AO9)","v":12.65693430656934},{"$f":"U9*$I$13","v":17.649635036496349},{"$f":"IF(AP9>I9,I9,AP9)","v":12.306569343065693},16.554744525547441,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.912408759124085},15.503649635036496,{"$f":"IF(AR9>M9,M9,AR9)","v":11.518248175182483},14.452554744525548,{"$f":"IF(AS9>O9,O9,AS9)","v":11.124087591240876},null,1.1143552311435523,1.0681265206812651,1.024330900243309,0.98053527980535271,0.91970802919708017,0.86131386861313863,0.8029197080291971,0.66375545851528384,0.67425968109339418,0.68646080760095007,0.69727047146401988,0.71957671957671965,0.74293785310734473,0.76969696969696966,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.313868613138686},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.963503649635037},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.65693430656934},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.306569343065693},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.912408759124085},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.518248175182483},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.124087591240876}]
[null,62,18.700729927007298,16.072992700729927,17.868613138686129,15.591240875912408,17.036496350364963,15.153284671532846,{"$f":"U10*$I$13","v":16.204379562043798},14.67153284671533,15.284671532846716,14.189781021897812,14.40875912408759,13.708029197080291,13.48905109489051,13.226277372262771,null,1.0389294403892944,0.9927007299270072,0.94647201946472015,0.9002433090024331,0.84914841849148415,0.80048661800486609,0.74939172749391725,0.85948477751756436,0.87254901960784326,0.88946015424164526,0.90540540540540537,0.92836676217765046,0.9513677811550153,0.98051948051948046,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.072992700729927,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.591240875912408},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.153284671532846},14.67153284671533,14.189781021897812,13.708029197080291,13.226277372262771]
[null,57,17.824817518248175,17.474452554744524,17.211678832116789,16.817518248175183,16.5985401459854,16.116788321167881,{"$f":"U11*$I$13","v":15.985401459854014},15.459854014598537,15.197080291970805,14.627737226277372,14.40875912408759,13.883211678832115,13.620437956204379,13.094890510948904,null,0.99026763990267641,0.95620437956204374,0.92214111922141118,0.8880778588807785,0.84428223844282246,0.80048661800486609,0.75669099756690994,0.98034398034398029,0.97709923664122145,0.97097625329815296,0.96712328767123279,0.96253602305475494,0.96352583586626139,0.96141479099678451,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.474452554744524,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.817518248175183},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.116788321167881},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.459854014598537},14.627737226277372,13.883211678832115,13.094890510948904]
[1400,72,21.722627737226279,10.948905109489052,21.021897810218977,10.686131386861312,20.364963503649637,10.467153284671532,{"$f":"U12*$I$13","v":19.664233576642335},10.204379562043796,18.481751824817518,9.8540145985401466,17.386861313868614,9.5036496350364956,16.248175182481752,9.10948905109489,null,1.2068126520681266,1.167883211678832,1.1313868613138687,1.0924574209245741,1.02676399026764,0.96593673965936744,0.902676399026764,0.50403225806451613,0.5083333333333333,0.51397849462365586,0.51893095768374164,0.53317535545023698,0.54659949622166237,0.56064690026954178,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.948905109489052},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.686131386861312},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.467153284671532},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.204379562043796},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8540145985401466},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.5036496350364956},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.10948905109489}]
[null,67,20.45255474452555,14.233576642335766,19.62043795620438,13.927007299270075,18.788321167883211,13.664233576642335,18,13.357664233576642,16.905109489051092,12.919708029197077,15.81021897810219,12.525547445255475,14.759124087591241,12.131386861313867,null,1.1362530413625305,1.0900243309002433,1.0437956204379562,1,0.93917274939172746,0.87834549878345503,0.81995133819951338,0.69593147751605988,0.7098214285714286,0.72727272727272729,0.74209245742092456,0.76424870466321237,0.79224376731301938,0.82195845697329373,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.233576642335766},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.927007299270075},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.664233576642335},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.357664233576642},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.919708029197077},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.525547445255475},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.131386861313867}]
[null,62,19.051094890510946,17.25547445255474,18.262773722627738,16.773722627737225,17.474452554744524,16.291970802919707,{"$f":"U14*$I$13","v":16.642335766423358},15.81021897810219,15.766423357664232,15.197080291970803,14.89051094890511,14.540145985401461,14.014598540145984,13.927007299270072,null,1.0583941605839415,1.0145985401459854,0.97080291970802912,0.92457420924574207,0.87591240875912402,0.82725060827250607,0.77858880778588802,0.90574712643678157,0.91846522781774564,0.93233082706766923,0.95000000000000007,0.96388888888888902,0.9764705882352942,0.99375000000000002,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.25547445255474,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.773722627737225},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.291970802919707},15.81021897810219,15.197080291970803,14.540145985401461,13.927007299270072]
[null,57,18.481751824817518,18.175182481751822,17.868613138686129,17.518248175182482,17.211678832116789,16.861313868613141,16.5985401459854,16.204379562043794,15.766423357664232,15.32846715328467,14.934306569343065,14.496350364963503,14.102189781021899,13.708029197080291,null,1.02676399026764,0.9927007299270072,0.95620437956204374,0.92214111922141118,0.87591240875912402,0.82968369829683697,0.78345498783454992,0.9834123222748814,0.98039215686274517,0.97964376590330793,0.9762532981530343,0.97222222222222221,0.97067448680351909,0.97204968944099368,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.175182481751822,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.518248175182482},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.861313868613141},16.204379562043794,15.32846715328467,14.496350364963503,13.708029197080291]
[1600,72,22.116788321167881,11.430656934306569,21.372262773722625,11.211678832116787,20.583941605839414,11.036496350364962,19.839416058394157,10.817518248175181,18.700729927007298,10.423357664233576,17.56204379562044,10.072992700729928,16.467153284671532,9.6788321167883211,null,1.2287104622871046,1.1873479318734792,1.1435523114355231,1.1021897810218977,1.0389294403892944,0.97566909975669103,0.91484184914841848,0.51683168316831685,0.52459016393442626,0.53617021276595744,0.54525386313465785,0.55737704918032782,0.57356608478802995,0.58776595744680848,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.430656934306569},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.211678832116787},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.036496350364962},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.817518248175181},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.423357664233576},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.072992700729928},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.6788321167883211}]
[null,67,20.802919708029197,15.197080291970803,20.014598540145986,14.934306569343065,19.182481751824813,14.62773722627737,18.350364963503651,14.364963503649635,17.255474452554743,13.927007299270073,16.160583941605836,13.48905109489051,15.065693430656934,13.094890510948904,null,1.1557177615571776,1.1119221411192215,1.0656934306569341,1.0194647201946472,0.95863746958637464,0.89781021897810209,0.83698296836982966,0.73052631578947369,0.74617067833698025,0.76255707762557079,0.78281622911694504,0.80710659898477166,0.83468834688346893,0.8691860465116279,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.197080291970803},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.934306569343065},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.62773722627737},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.364963503649635},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.927007299270073},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.48905109489051},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.094890510948904}]
[null,62,19.401459854014597,18.394160583941606,18.613138686131386,17.912408759124084,17.868613138686129,17.430656934306565,17.124087591240876,16.948905109489051,16.248175182481752,16.160583941605839,15.372262773722627,15.372262773722627,14.496350364963504,14.496350364963504,null,1.0778588807785887,1.0340632603406326,0.9927007299270072,0.95133819951338194,0.902676399026764,0.85401459854014594,0.805352798053528,0.94808126410835225,0.96235294117647052,0.97549019607843135,0.98976982097186705,0.99460916442048508,1.0028490028490029,1.0090634441087611,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.394160583941606,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.912408759124084},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.430656934306565},16.948905109489051,16.160583941605839,15.416058394160583,14.62773722627737]
[null,57,19.182481751824813,18.919708029197079,18.525547445255473,18.262773722627738,17.868613138686129,17.605839416058394,17.211678832116789,16.948905109489054,16.291970802919707,16.029197080291969,15.459854014598539,15.153284671532846,14.583941605839414,14.277372262773723,null,1.0656934306569341,1.0291970802919708,0.9927007299270072,0.95620437956204374,0.9051094890510949,0.85888077858880774,0.81021897810218968,0.98630136986301387,0.98581560283687952,0.98529411764705899,0.98473282442748111,0.9838709677419355,0.9801699716713882,0.97897897897897912,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.919708029197079,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.262773722627738},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.605839416058394},16.948905109489054,16.029197080291969,15.153284671532846,14.277372262773723]

{"sheet":"TCJF_48","index":18,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJF48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":19.572413793103451},{"$f":"IF(AM8>C8,C8,AM8)","v":10.013793103448277},{"$f":"S8*$I$13","v":19.406896551724135},{"$f":"IF(AN8>E8,E8,AN8)","v":10.055172413793104},{"$f":"T8*$I$13","v":19.241379310344826},{"$f":"IF(AO8>G8,G8,AO8)","v":10.055172413793102},{"$f":"U8*$I$13","v":19.03448275862069},{"$f":"IF(AP8>I8,I8,AP8)","v":10.09655172413793},{"$f":"V8*$I$13","v":17.95862068965517},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7241379310344822},{"$f":"W8*$I$13","v":16.882758620689653},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3931034482758609},{"$f":"X8*$I$13","v":15.806896551724138},{"$f":"IF(AS8>O8,O8,AS8)","v":9.0620689655172413},null,1.0873563218390805,1.0781609195402297,1.0689655172413792,1.0574712643678161,0.99770114942528731,0.93793103448275861,0.8781609195402299,0.51162790697674421,0.51812366737739879,0.52258064516129032,0.53043478260869559,0.54147465437788023,0.55637254901960786,0.57329842931937169,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.013793103448277},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.055172413793104},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.055172413793102},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.09655172413793},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7241379310344822},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3931034482758609},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.0620689655172413}]
[null,67,{"$f":"R9*$I$13","v":19.531034482758621},12.910344827586204,18.910344827586208,{"$f":"IF(AN9>E9,E9,AN9)","v":12.951724137931034},18.248275862068965,{"$f":"IF(AO9>G9,G9,AO9)","v":12.993103448275861},{"$f":"U9*$I$13","v":17.627586206896552},{"$f":"IF(AP9>I9,I9,AP9)","v":13.03448275862069},16.468965517241379,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.620689655172415},15.351724137931035,{"$f":"IF(AR9>M9,M9,AR9)","v":12.206896551724137},14.23448275862069,{"$f":"IF(AS9>O9,O9,AS9)","v":11.751724137931035},null,1.0850574712643679,1.0505747126436782,1.0137931034482759,0.97931034482758628,0.91494252873563209,0.85287356321839081,0.79080459770114941,0.66101694915254228,0.68490153172866519,0.71201814058956914,0.73943661971830987,0.76633165829145733,0.79514824797843664,0.82558139534883723,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.910344827586204},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.951724137931034},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.993103448275861},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":13.03448275862069},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.620689655172415},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.206896551724137},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.751724137931035}]
[null,62,18.703448275862073,16.137931034482762,18,16.137931034482758,17.337931034482757,16.096551724137928,{"$f":"U10*$I$13","v":16.634482758620692},16.096551724137932,15.558620689655172,15.227586206896548,14.482758620689655,14.399999999999999,13.448275862068964,13.448275862068964,null,1.0390804597701151,1,0.9632183908045977,0.92413793103448283,0.86436781609195401,0.8045977011494253,0.74712643678160917,0.86283185840707954,0.89655172413793105,0.9284009546539379,0.96766169154228843,0.97872340425531901,0.99428571428571422,1.0123076923076924,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.137931034482762,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.137931034482758},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":16.096551724137928},16.096551724137932,15.227586206896548,14.399999999999999,13.613793103448275]
[null,57,18.248275862068965,18.082758620689656,17.627586206896552,17.544827586206896,16.96551724137931,16.96551724137931,{"$f":"U11*$I$13","v":16.344827586206897},16.344827586206897,15.351724137931035,15.351724137931035,14.441379310344827,14.399999999999999,13.489655172413794,13.406896551724138,null,1.0137931034482759,0.97931034482758628,0.94252873563218387,0.90804597701149425,0.85287356321839081,0.80229885057471262,0.74942528735632186,0.99092970521541957,0.99530516431924876,1.0024390243902439,1.0075949367088606,1.0053908355795147,0.99713467048710602,0.99386503067484655,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.082758620689656,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.544827586206896},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.006896551724136},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.468965517241376},15.434482758620687,14.399999999999999,13.406896551724138]
[1600,72,19.820689655172416,10.262068965517244,19.655172413793107,10.344827586206899,19.531034482758621,10.427586206896549,{"$f":"U12*$I$13","v":19.365517241379308},10.468965517241379,18.248275862068965,10.179310344827588,17.172413793103448,9.931034482758621,16.055172413793102,9.6413793103448278,null,1.1011494252873564,1.0919540229885059,1.0850574712643679,1.0758620689655172,1.0137931034482759,0.95402298850574707,0.89195402298850568,0.51774530271398755,0.52631578947368418,0.53389830508474567,0.54059829059829068,0.55782312925170074,0.57831325301204817,0.60051546391752586,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.262068965517244},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.344827586206899},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.427586206896549},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.468965517241379},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.179310344827588},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.931034482758621},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6413793103448278}]
[null,67,19.613793103448273,13.324137931034482,19.075862068965517,13.489655172413793,18.53793103448276,13.655172413793105,18,13.820689655172414,16.8,13.448275862068966,15.641379310344828,13.075862068965519,14.482758620689655,12.662068965517241,null,1.0896551724137931,1.0597701149425287,1.0298850574712644,1,0.93333333333333335,0.86896551724137927,0.8045977011494253,0.67932489451476796,0.70715835140997829,0.7366071428571429,0.76781609195402301,0.80049261083743839,0.83597883597883604,0.87428571428571433,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.324137931034482},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.489655172413793},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.655172413793105},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.820689655172414},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.448275862068966},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.075862068965519},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.662068965517241}]
[null,62,18.744827586206895,16.8,18.124137931034483,16.882758620689653,17.544827586206896,16.924137931034483,{"$f":"U14*$I$13","v":16.96551724137931},16.96551724137931,15.972413793103449,15.972413793103449,15.020689655172411,15.020689655172411,14.027586206896551,14.027586206896551,null,1.0413793103448274,1.0068965517241379,0.97471264367816091,0.94252873563218387,0.88735632183908053,0.83448275862068955,0.77931034482758621,0.89624724061810168,0.93150684931506844,0.964622641509434,1.0024390243902439,1.0025906735751295,1.0027548209366393,1.0058997050147493,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.8,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.882758620689653},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.924137931034483},17.006896551724136,16.013793103448275,15.062068965517241,14.110344827586207]
[null,57,18.289655172413791,18.289655172413791,17.793103448275861,17.793103448275861,17.337931034482757,17.337931034482757,16.841379310344827,16.841379310344827,15.848275862068965,15.848275862068965,14.896551724137931,14.896551724137931,13.903448275862068,13.903448275862068,null,1.0160919540229885,0.9885057471264368,0.9632183908045977,0.93563218390804603,0.88045977011494247,0.82758620689655171,0.77241379310344827,1.0022624434389138,1.0069767441860464,1.0071599045346062,1.0122850122850122,1.0078328981723239,1.0055555555555555,1.0029761904761905,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.331034482758614,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.917241379310344},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.46206896551724},17.048275862068962,15.972413793103449,14.979310344827585,13.944827586206896]
[1800,72,20.068965517241381,10.551724137931036,19.944827586206898,10.63448275862069,19.820689655172416,10.758620689655173,19.696551724137933,10.882758620689657,18.53793103448276,10.63448275862069,17.420689655172417,10.427586206896553,16.344827586206897,10.179310344827586,null,1.1149425287356323,1.1080459770114943,1.1011494252873564,1.0942528735632184,1.0298850574712644,0.96781609195402307,0.90804597701149425,0.52577319587628868,0.53319502074688796,0.54279749478079331,0.55252100840336138,0.5736607142857143,0.59857482185273159,0.62278481012658227,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":10.551724137931036},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.63448275862069},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.758620689655173},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.882758620689657},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.63448275862069},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.427586206896553},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.179310344827586}]
[null,67,19.696551724137933,13.737931034482761,19.241379310344826,14.027586206896549,18.786206896551725,14.317241379310346,18.331034482758618,14.565517241379311,17.131034482758622,14.234482758620691,15.931034482758621,13.90344827586207,14.77241379310345,13.613793103448275,null,1.0942528735632184,1.0689655172413792,1.0436781609195402,1.018390804597701,0.9517241379310345,0.88505747126436785,0.82068965517241388,0.69747899159663873,0.7290322580645161,0.76211453744493396,0.79458239277652387,0.83091787439613529,0.8727272727272728,0.92156862745098023,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":13.737931034482761},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.027586206896549},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.317241379310346},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.565517241379311},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.234482758620691},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.90344827586207},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.613793103448275}]
[null,62,18.744827586206895,17.503448275862066,18.248275862068965,17.627586206896552,17.751724137931035,17.751724137931035,17.296551724137931,17.296551724137931,16.386206896551727,16.386206896551727,15.517241379310343,15.517241379310343,14.648275862068965,14.606896551724137,null,1.0413793103448274,1.0137931034482759,0.98620689655172411,0.96091954022988502,0.91034482758620694,0.86206896551724133,0.81379310344827582,0.93377483443708609,0.96598639455782309,1,1.0334928229665072,1.0227272727272727,1.0106666666666666,0.99717514124293782,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.503448275862066,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.627586206896552},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.751724137931035},17.875862068965517,16.758620689655174,15.682758620689652,14.606896551724137]
[null,57,18.289655172413791,18.289655172413791,18,18,17.668965517241382,17.668965517241382,17.379310344827587,17.379310344827587,16.344827586206897,16.344827586206897,15.351724137931035,15.351724137931035,14.317241379310346,14.317241379310346,null,1.0160919540229885,1,0.98160919540229896,0.96551724137931039,0.90804597701149425,0.85287356321839081,0.79540229885057478,1.0158371040723981,1.0137931034482759,1.0163934426229506,1.0142857142857142,1.0126582278481013,1.0107816711590296,1.0086705202312138,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.579310344827583,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.248275862068965},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.95862068965517},17.627586206896552,16.551724137931036,15.517241379310345,14.441379310344828]

{"sheet":"TCJF_60","index":19,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[15,0,18,0],[5,10,6,10],[5,11,6,11],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["TCJF60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1600,72,{"$f":"R8*$I$13","v":21.771126760563384},{"$f":"IF(AM8>C8,C8,AM8)","v":10.299295774647888},{"$f":"S8*$I$13","v":20.91549295774648},{"$f":"IF(AN8>E8,E8,AN8)","v":9.9823943661971839},{"$f":"T8*$I$13","v":20.059859154929576},{"$f":"IF(AO8>G8,G8,AO8)","v":9.6654929577464781},{"$f":"U8*$I$13","v":19.172535211267604},{"$f":"IF(AP8>I8,I8,AP8)","v":9.3485915492957741},{"$f":"V8*$I$13","v":18.063380281690144},{"$f":"IF(AQ8>K8,K8,AQ8)","v":8.9049295774647899},{"$f":"W8*$I$13","v":16.985915492957748},{"$f":"IF(AR8>M8,M8,AR8)","v":8.4929577464788739},{"$f":"X8*$I$13","v":15.908450704225352},{"$f":"IF(AS8>O8,O8,AS8)","v":8.080985915492958},null,1.2095070422535212,1.1619718309859155,1.1144366197183098,1.0651408450704225,1.0035211267605635,0.94366197183098599,0.88380281690140849,0.47307132459970885,0.47727272727272729,0.48183254344391785,0.48760330578512395,0.49298245614035091,0.5,0.50796812749003983,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.299295774647888},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":9.9823943661971839},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":9.6654929577464781},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.3485915492957741},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":8.9049295774647899},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":8.4929577464788739},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.080985915492958}]
[null,67,{"$f":"R9*$I$13","v":19.901408450704228},12.897887323943664,19.172535211267604,{"$f":"IF(AN9>E9,E9,AN9)","v":12.612676056338028},18.411971830985916,{"$f":"IF(AO9>G9,G9,AO9)","v":12.327464788732394},{"$f":"U9*$I$13","v":17.683098591549296},{"$f":"IF(AP9>I9,I9,AP9)","v":12.073943661971832},16.637323943661972,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.566901408450704},15.623239436619718,{"$f":"IF(AR9>M9,M9,AR9)","v":11.091549295774648},14.577464788732396,{"$f":"IF(AS9>O9,O9,AS9)","v":10.616197183098592},null,1.1056338028169015,1.0651408450704225,1.022887323943662,0.98239436619718312,0.92429577464788737,0.86795774647887325,0.8098591549295775,0.64808917197452232,0.65785123966942149,0.66953528399311524,0.68279569892473124,0.69523809523809521,0.70993914807302239,0.72826086956521741,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.897887323943664},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.612676056338028},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.327464788732394},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.073943661971832},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.566901408450704},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.091549295774648},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":10.616197183098592}]
[null,62,18.316901408450704,15.591549295774648,17.619718309859156,15.242957746478874,16.954225352112676,14.92605633802817,{"$f":"U10*$I$13","v":16.288732394366196},14.577464788732394,15.274647887323946,14.13380281690141,14.323943661971832,13.721830985915492,13.37323943661972,13.278169014084506,null,1.017605633802817,0.97887323943661975,0.94190140845070425,0.90492957746478875,0.84859154929577474,0.79577464788732399,0.74295774647887336,0.85121107266435991,0.8651079136690647,0.88037383177570094,0.89494163424124518,0.92531120331950201,0.95796460176991138,0.99289099526066338,1.06,1.06,1.06,1.06,1.06,1.06,1.06,15.591549295774648,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.242957746478874},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.92605633802817},14.577464788732394,14.13380281690141,13.721830985915492,13.278169014084506]
[null,57,17.27112676056338,17.112676056338028,16.700704225352116,16.573943661971832,16.098591549295776,16.035211267605636,{"$f":"U11*$I$13","v":15.528169014084508},15.496478873239438,14.704225352112676,14.704225352112676,13.880281690140844,13.880281690140844,13.088028169014084,13.088028169014084,null,0.95950704225352113,0.92781690140845086,0.89436619718309862,0.86267605633802824,0.81690140845070425,0.77112676056338025,0.727112676056338,0.99082568807339455,0.99240986717267543,0.99606299212598437,0.99795918367346936,1.0021551724137931,1.0068493150684932,1.0121065375302662,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.112676056338028,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.573943661971832},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.035211267605636},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.496478873239438},14.735915492957748,13.975352112676056,13.246478873239434]
[1800,72,22.088028169014088,10.806338028169016,21.200704225352119,10.489436619718314,20.345070422535215,10.172535211267608,{"$f":"U12*$I$13","v":19.45774647887324},9.8239436619718319,18.380281690140844,9.3802816901408441,17.334507042253524,8.96830985915493,16.320422535211268,8.524647887323944,null,1.2271126760563382,1.177816901408451,1.1302816901408452,1.0809859154929577,1.0211267605633803,0.96302816901408461,0.90669014084507049,0.48923959827833574,0.49476831091180867,0.5,0.50488599348534202,0.51034482758620692,0.51736745886654478,0.52233009708737865,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.806338028169016},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.489436619718314},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.172535211267608},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":9.8239436619718319},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.3802816901408441},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":8.96830985915493},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":8.524647887323944}]
[null,67,20.503521126760567,13.595070422535212,19.679577464788736,13.27816901408451,18.855633802816904,12.992957746478874,18,12.67605633802817,16.890845070422536,12.200704225352114,15.845070422535212,11.757042253521128,14.767605633802818,11.313380281690142,null,1.1390845070422537,1.0933098591549297,1.0475352112676057,1,0.93838028169014087,0.88028169014084512,0.82042253521126762,0.66306027820710967,0.67471819645732689,0.68907563025210083,0.70422535211267612,0.72232645403377116,0.74199999999999999,0.76609442060085842,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.595070422535212},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.27816901408451},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":12.992957746478874},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.67605633802817},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.200704225352114},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":11.757042253521128},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":11.313380281690142}]
[null,62,18.728873239436624,16.605633802816904,18,16.193661971830988,17.27112676056338,15.81338028169014,{"$f":"U14*$I$13","v":16.573943661971832},15.401408450704228,15.623239436619718,14.8943661971831,14.704225352112676,14.387323943661972,13.785211267605634,13.785211267605634,null,1.040492957746479,1,0.95950704225352113,0.92077464788732399,0.86795774647887325,0.81690140845070425,0.76584507042253525,0.88663282571912005,0.89964788732394374,0.91559633027522935,0.92925430210325055,0.95334685598377289,0.97844827586206895,1.0068965517241379,1.06,1.06,1.06,1.06,1.06,1.06,1.06,16.605633802816904,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.193661971830988},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.81338028169014},15.401408450704228,14.8943661971831,14.387323943661972,13.880281690140846]
[null,57,17.524647887323944,17.524647887323944,17.366197183098592,17.20774647887324,17.20774647887324,16.6056338028169,17.01760563380282,16.003521126760564,15.845070422535212,15.211267605633802,14.735915492957748,14.419014084507044,13.595070422535212,13.595070422535212,null,0.97359154929577463,0.96478873239436624,0.95598591549295775,0.94542253521126773,0.88028169014084512,0.81866197183098599,0.75528169014084512,1.0162748643761303,0.99087591240875916,0.96500920810313073,0.94040968342644315,0.96,0.978494623655914,1.0046620046620047,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.80985915492958,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.20774647887324},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":16.6056338028169},16.003521126760564,15.211267605633802,14.419014084507044,13.658450704225354]
[2000,72,22.404929577464792,11.345070422535212,21.51760563380282,10.996478873239438,20.630281690140844,10.647887323943664,19.742957746478872,10.330985915492956,18.697183098591552,9.8556338028169037,17.714788732394368,9.4119718309859177,16.700704225352116,8.9683098591549317,null,1.244718309859155,1.1954225352112677,1.1461267605633803,1.096830985915493,1.0387323943661972,0.98415492957746487,0.92781690140845086,0.50636492220650631,0.51104565537555224,0.51612903225806461,0.5232744783306581,0.52711864406779663,0.53130590339892669,0.53700189753320682,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.345070422535212},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":10.996478873239438},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.647887323943664},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.330985915492956},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":9.8556338028169037},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":9.4119718309859177},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":8.9683098591549317}]
[null,67,21.1056338028169,14.292253521126762,20.18661971830986,13.975352112676056,19.267605633802816,13.626760563380282,18.348591549295772,13.278169014084504,17.176056338028172,12.834507042253524,16.066901408450704,12.422535211267606,14.957746478873242,11.97887323943662,null,1.1725352112676055,1.1214788732394367,1.0704225352112675,1.0193661971830985,0.95422535211267612,0.89260563380281699,0.83098591549295786,0.67717717717717729,0.69230769230769229,0.70723684210526316,0.72366148531951635,0.74723247232472323,0.7731755424063117,0.80084745762711851,1.06,1.06,1.06,1.06,1.06,1.06,1.06,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.292253521126762},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":13.975352112676056},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.626760563380282},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.278169014084504},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":12.834507042253524},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.422535211267606},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":11.97887323943662}]
[null,62,19.140845070422536,17.651408450704228,18.380281690140844,17.176056338028168,17.619718309859156,16.700704225352112,16.859154929577468,16.22535211267606,15.971830985915494,15.623239436619718,15.084507042253524,15.052816901408454,14.22887323943662,14.22887323943662,null,1.063380281690141,1.0211267605633803,0.97887323943661975,0.93661971830985924,0.88732394366197187,0.83802816901408461,0.79049295774647887,0.92218543046357626,0.93448275862068975,0.94784172661870503,0.96240601503759393,0.97817460317460314,0.99789915966386555,1.0155902004454345,1.06,1.06,1.06,1.06,1.06,1.06,1.06,17.651408450704228,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.176056338028168},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":16.700704225352112},16.22535211267606,15.623239436619718,15.052816901408454,14.450704225352116]
[null,57,17.778169014084508,17.778169014084508,18.031690140845072,17.87323943661972,18.285211267605636,17.20774647887324,18.507042253521128,16.542253521126764,17.01760563380282,15.686619718309862,15.559859154929578,14.862676056338028,14.102112676056338,14.070422535211268,null,0.98767605633802824,1.0017605633802817,1.0158450704225352,1.028169014084507,0.94542253521126773,0.86443661971830987,0.78345070422535212,1.0427807486631016,0.99121265377855883,0.94107452339688036,0.89383561643835618,0.92178770949720668,0.95519348268839099,0.99775280898876406,1.06,1.06,1.06,1.06,1.06,1.06,1.06,18.538732394366196,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":17.87323943661972},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.20774647887324},16.542253521126764,15.686619718309862,14.862676056338028,14.070422535211268]

{"sheet":"Form","index":20,"n_rows":53,"n_cols":16,"rows_kept":53,"cut":false,"hidden":true,"merged":[[1,3,1,8],[2,3,2,8],[13,0,13,15],[26,14,26,15],[26,10,26,11],[18,6,18,11],[26,4,26,5],[26,12,26,13],[26,8,26,9],[25,2,25,15],[25,0,25,1],[26,2,26,3],[17,6,17,11],[26,6,26,7],[52,1,52,4],[28,2,29,2],[28,3,29,3],[28,9,29,9],[28,8,29,8],[27,1,29,1],[27,2,27,3],[27,6,27,7],[38,0,41,0],[27,12,27,13],[28,4,29,4],[28,5,29,5],[28,6,29,6],[28,7,29,7],[30,0,33,0],[27,8,27,9],[27,10,27,11],[28,12,29,12],[27,0,29,0],[28,11,29,11],[28,15,29,15],[27,4,27,5],[34,0,37,0],[28,13,29,13],[28,10,29,10],[27,14,27,15],[28,14,29,14]]}
[]
[null,null,"Select Luxaire Condenser:  "]
[null,null,"ADP Evaporator:  ",null,null,null,null,null,null,null,null,null,null,24]
[null,null,"Nominal Capacity:  ",null,"(Mbtuh)",null,null,null,null,null,null,"Condenser Entering Air Temperature: ",null,"(°F) Dry Bulb, 65°F to 125°F"]
[null,null,"AHRI Rated Capacity:  ",null,"(Mbtuh) @ 95 ˚F & 80/67 ˚F conditions",null,null,null,null,null,null,"Evaporator Air Flow (CFM): ",null,null,"to"]
[null,null,"Entering Evaporator Air (DB):  ",null,"(°F) Dry Bulb -- 80°F Standard",null,null,null,null,null,null,"Entering Evaporator Air (WB):  ",null,"(°F) Wet Bulb, 57°F to 72°F"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,48]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"CFM"]
[]
[]
[]
[]
[]
["Extended Ratings"]
[]
[]
[]
[null,null,null,null,null,"Luxaire Condenser :  "]
[null,null,null,null,null,"ADP Evaporator:  "]
[null,null,null,null,null,"Condenser Entering Air Temperature: ",null,"(°F) Dry Bulb, 65°F to 125°F"]
[null,null,null,null,null,"Evaporator Air Flow:",null,"CFM"]
[null,null,null,null,null,"Entering Evaporator Air (DB):  ",null,"(°F) Dry Bulb"]
[null,null,null,null,null,"Entering Evaporator Air (WB):  ",null,"(°F) Wet Bulb, 57°F to 72°F"]
[null,null,null,null,null,"AHRI Rated Capacity:  ",null,"(Mbtuh) @ 95 ˚F & 80/67 ˚F conditions"]
[]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",65,null,75,null,85,null,95,null,105,null,115,null,125]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,"Condenser Entering Air Temperature: ",null,"(°F) Dry Bulb, 65°F to 125°F",null,null,null,"CAPACITY IN MBTUH UNDER SPECIFIC CONDITIONS LISTED"]
[null,null,null,"Evaporator Air Flow:",null,"CFM",null,null,null,null,"TOTAL"]
[null,null,null,"Entering Evaporator Air (WB):  ",null,"(°F) Wet Bulb, 57°F to 72°F",null,null,null,null,"SENSIBLE"]
[]
["Notes:","† Entering Wet Bulb"]
[null,"Extended ratings are not certified.  They are calculated based upon typical condenser performance curves and are for engineering information only."]
[null,"When the required data fall between the published data, interpolation may be performed. Extrapolation is not an acceptable practice."]
[null,"Displayed sensible capacity has been adjusted based upon indoor DB.  Sensible capacity will increase with higher indoor DB and decrease with lower indoor DB."]
[null,"The magnitude of the adjustment depends partially on evaporator air flow, with greater adjustment at higher CFM."]
["Printed:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"LU-19-A"]

{"sheet":"Instructions","index":21,"n_rows":38,"n_cols":5,"rows_kept":38,"cut":false,"hidden":true,"merged":[]}
[]
[]
[]
[]
[]
[]
[null,"This spreadsheet generates capacity information for ADP rated matches at other than nominal conditions."]
[null,"The information is provided is not certified and is provided for engineering use only."]
[]
[null,"The latest version will always be available at:  www.adpnow.com/extratings/"]
[]
[null,"In order to generate an extended rating, you will need the following information:"]
[null,null,"Condenser model number"]
[null,null,"ADP coil model number"]
[null,null,"Nominal capacity"]
[null,null,"Rated capacity (from AHRI database)"]
[null,null,"Condenser entering air dry bulb temperature"]
[null,null,"Indoor entering air dry bulb temperature"]
[null,null,"Indoor entering air wet bulb temperature"]
[null,null,"Indoor airflow"]
[]
[null,"Select the condenser series and nominal tonnage form the drop down lists."]
[null,"Enter the remaining information in the correct cells. Note there are limits on the range of values allowed."]
[null,"Click on \"Calculate\" to calculate the extended ratings."]
[null,"The table will show capacities for various conditions.  The capacities at the specific design point are "]
[null,"at the bottom of the page."]
[null,"From this point you may:"]
[null,null,"Click \"Clear\" to clear the form and start over."]
[null,null,"Click \"Print\" to print a copy of the data."]
[null,null,"Click \"Copy\" to copy the data to a new spreadsheet and save it in the same directory."]
[]
[null,"Notes:","Displayed sensible capacity has been adjusted based upon indoor DB. Sensible capacity will"]
[null,null,"increase with higher indoor DB and decrease with lower indoor DB.  The magnitude of the "]
[null,null,"adjustment depends partially on evaporator air flow, with greater adjustment at higher CFM."]
[]
[null,"Versions:","LU-15-A","2015-03-10","Initial public release"]
[null,null,"LU-16-A","2016-03-22","Renewed date key through 2016"]
[null,null,"LU-19-A","2019-05-20","New Version"]

{"sheet":"Prompt","index":22,"n_rows":17,"n_cols":2,"rows_kept":17,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,"In order to use this spreadsheet, "]
[null,"Please enable Macros in your security settings."]
[]
[null,"Enabling Macros in Excel 2007"]
[null,"1. In Excel, click the Office button in the upper left corner of the screen."]
[null,"2. Click the \"Excel Options\" button in the lower right."]
[null,"3. Click the \"Trust Center\" button on the left. Then, at the bottom right, select \"Trust Center Settings\" as shown below."]
[null,"4. In the next window, select \"Macro Settings,\" then select the radio button for \"Disable all macros with notification.\""]
[null,"5. When openning this spreadsheet, you will see a warning like this in the menu bar:"]
[]
[]
[null,"6. Select \"Enable this content\" and click \"Okay\".  The spreadsheet will now be functional."]