## Front
SUBMITTAL DATA
MX SERIES AIR HANDLER
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Optional Accessories
Unit Size
|  | MXC8WPN4BA | MXC12ANN4CA | MXE1600N2EA | MXE800N2EA
Hot Water Coil |  | Hot water coil with pump | Hot water coil | No hot water coil | No hot water coil
Heat Size |  | 3 row hot water coil | 4 row hot water coil | No heat | No heat
Blower Data: | Motor Type | 3-speed PSC motor | 3-speed PSC motor | 5-speed ECM motor | 5-speed ECM motor
| Motor H.P. | 1/3 | 1/2 | 3/4 | 1/3
| F.L.A. | 5.3 | 7.1 | 6 | 2.8
Nominal CFM |  | 800 | 1200 | 1600 | 800
Max Unit Weight (lbs) |  | 66 | 66 | 74 | 69
Available Voltages |  | 120 V, 60 Hz, 1 Ph | 120 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph
Maximum Elec. Heat available (kW) |  | 10 kW | 15 kW | 20 kW | 10 kW
Transformer Size and Type |  | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2 | 40 VA, Class 2
Pump Conn. Size |  | 7/8" | 7/8" | 7/8" | 7/8"
Pump Amps |  | 0.52 | 0.52 | 0.52 | 0.52
Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
Easy Installation: "One-Man-Job"
Cabinet lined with high quality 5/8" foil faced insulation.
Available from factory as upflow, downflow, and horizontal.
Only four screws to remove blower panel, making it easier to service.
Embossed cabinet in heavy gauge galvanized steel to prevent corrosion.
Factory installed fan time delay postpones blower shutoff 30 seconds in heating mode and 45 seconds in cooling mode.
Dynamically balanced 3-speed PSC or 5-speed ECM motor with easy to adjust settings for fine tuning customer comfort.
Approved for installation in manufactured housing and mobile homes.
Electric Heat Kit
Aquastat Kit
10-year limited warranty available.
Product registration required.
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
MX SERIES AIR HANDLER
3-speed psc 120 Volt (hot water)
5-speed ecm 240 Volt (electric heat and No heat)

## Nomenclature (hidden)
MX | E |  | 08 |  | 00 |  | N | 2 |  | E |  | 2
Series | Blower Motor |  | Size/ Airflow |  | Hot Water Coil |  | Line Voltage Connection | Voltage |  | Heat Size |  | Revision | Revision
MX | C: | 3-speed PSC motor | 08: | 800 CFM | 00: | No hot water coil | N = Stripped wire | 2: | 208/240 V, 60 Hz, 1 ph | B: | 3 row hot water coil (size 08 and 20)
| E: | 5-speed high eff. ECM motor | 12: | 1200 CFM | WP: | Hot water coil with pump |  | 4: | 120 V, 60 Hz, 1 ph. | C: | 4 row hot water coil (size 08, 12 and 16)
|  |  | 16: | 1600 CFM | WN: | Hot water coil without pump |  |  |  | E: | No heat
|  |  | 20: | 2000 CFM | AP: | Hot water coil with 130̊ F aquastat & pump
[5 empty] | AN: | Hot water coil with 130̊ F aquastat & without pump

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model) | Pump Conn. Size | Pump Amps | Hot Water Coil | Heat Size
MXC8WPN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil with pump | 3 row hot water coil
MXC8WPN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil with pump | 4 row hot water coil
MXC8WNN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil without pump | 3 row hot water coil
MXC8WNN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil without pump | 4 row hot water coil
MXC8APN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 3 row hot water coil
MXC8APN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 4 row hot water coil
MXC8ANN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 3 row hot water coil
MXC8ANN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/3 | 5.3 | 800 | 66 | 120 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 4 row hot water coil
MXC12WPN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 12 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/2 | 7.1 | 1200 | 66 | 120 V, 60 Hz, 1 Ph | 15 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil with pump | 4 row hot water coil
MXC12WNN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 12 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/2 | 7.1 | 1200 | 66 | 120 V, 60 Hz, 1 Ph | 15 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil without pump | 4 row hot water coil
MXC12APN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 12 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/2 | 7.1 | 1200 | 66 | 120 V, 60 Hz, 1 Ph | 15 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 4 row hot water coil
MXC12ANN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 12 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 1/2 | 7.1 | 1200 | 66 | 120 V, 60 Hz, 1 Ph | 15 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 4 row hot water coil
MXC16WPN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 16 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 7.5 | 1600 | 71 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil with pump | 4 row hot water coil
MXC16WNN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 16 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 7.5 | 1600 | 71 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil without pump | 4 row hot water coil
MXC16APN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 16 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 7.5 | 1600 | 71 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 4 row hot water coil
MXC16ANN4CA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 16 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 7.5 | 1600 | 71 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 4 row hot water coil
MXC20WPN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 20 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 10.5 | 2000 | 83 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil with pump | 3 row hot water coil
MXC20WNN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 20 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 10.5 | 2000 | 83 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil without pump | 3 row hot water coil
MXC20APN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 20 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 10.5 | 2000 | 83 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 3 row hot water coil
MXC20ANN4BA | MX Series | 3-speed PSC motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 20 | Stripped wire | none | 120 V, 60 Hz, 1 ph. (PSC only) | A | N/A | N/A | 3/4 | 10.5 | 2000 | 83 | 120 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | Hot water coil | 3 row hot water coil
MXE800N2EA | MX Series | 5-speed ECM motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 8 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | N/A | N/A | 1/3 | 2.8 | 800 | 69 | 208/240 V, 60 Hz, 1 Ph | 10 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | No hot water coil | No heat
MXE1200N2EA | MX Series | 5-speed ECM motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 12 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | N/A | N/A | 1/2 | 4.1 | 1200 | 69 | 208/240 V, 60 Hz, 1 Ph | 15 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | No hot water coil | No heat
MXE1600N2EA | MX Series | 5-speed ECM motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 16 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | N/A | N/A | 3/4 | 6 | 1600 | 74 | 208/240 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | No hot water coil | No heat
MXE2000N2EA | MX Series | 5-speed ECM motor | Multi-pos. (vertical, left or right horiz.) | N/A | N/A | 20 | Stripped wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | N/A | N/A | 1 | 7.6 | 2000 | 86 | 208/240 V, 60 Hz, 1 Ph | 20 kW | 40 VA, Class 2 | N/A | N/A | 1 | 7/8" | 0.52 | No hot water coil | No heat

## Airflow (hidden)
[13 empty] | 3-speed psc 120 Volt (hot water) | [6 empty] | 5-speed ecm 240 Volt (electric heat and No heat)
[13 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.) | [6 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.)
ID | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | Voltage/Motor
8_120 V, 60 Hz, 1 ph. (PSC only)_1 | 8 | Low | 749 | 705 | 658 | 614 | 558 |  |  |  | 8 | Low | 749 | 705 | 658 | 614 | 558 | 8 | 1 | 502.2 | 265.5 | 155.3 | 155.8 | 155.7 | 208/240 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
8_120 V, 60 Hz, 1 ph. (PSC only)_2 | 8 | *Med | 865 | 815 | 760 | 708 | 646 |  |  |  |  | *Med | 865 | 815 | 760 | 708 | 646 | 8 | 2 | 667.4 | 667.8 | 636.2 | 596.9 | 562 | 120 V, 60 Hz, 1 ph. (PSC only) | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
8_120 V, 60 Hz, 1 ph. (PSC only)_3 | 8 | High | 904 | 836 | 801 | 740 | 681 |  |  |  |  | High | 904 | 836 | 801 | 740 | 681 | 8 | *3 | 1008.1 | 980 | 925.1 | 932.9 | 915.4 | 208/240 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
12_120 V, 60 Hz, 1 ph. (PSC only)_1 | 12 | Low | 1198 | 1144 | 1086 | 1018 | 962 |  |  |  | 12 | Low | 1198 | 1144 | 1086 | 1018 | 962 | 8 | +4 | 856.3 | 838.9 | 819.3 | 793.6 | 783.3 | 120 V, 60 Hz, 1 ph. (ECM only) | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
12_120 V, 60 Hz, 1 ph. (PSC only)_2 | 12 | *Med | 1257 | 1198 | 1130 | 1072 | 1010 |  |  |  |  | *Med | 1257 | 1198 | 1130 | 1072 | 1010 | 8 | 5 | 789.8 | 757.9 | 739.8 | 734.4 | 696.1
12_120 V, 60 Hz, 1 ph. (PSC only)_3 | 12 | High | 1273 | 1215 | 1158 | 1094 | 1018 |  |  |  |  | High | 1273 | 1215 | 1158 | 1094 | 1018 | 12 | 1 | 839.2 | 657.9 | 320.3 | 257.6 | 219.6
16_120 V, 60 Hz, 1 ph. (PSC only)_1 | 16 | Low | 1576 | 1514 | 1433 | 1338 | 1264 |  |  |  | 16 | Low | 1576 | 1514 | 1433 | 1338 | 1264 | 12 | 2 | 915.3 | 761.5 | 663.7 | 617.1 | 566.6
16_120 V, 60 Hz, 1 ph. (PSC only)_2 | 16 | Med | 1643 | 1576 | 1490 | 1407 | 1320 |  |  |  |  | Med | 1643 | 1576 | 1490 | 1407 | 1320 | 12 | *3 | 1314.8 | 1263.9 | 1226.7 | 1186.8 | 1151
16_120 V, 60 Hz, 1 ph. (PSC only)_3 | 16 | *High | 1707 | 1606 | 1545 | 1441 | 1364 |  |  |  |  | *High | 1707 | 1606 | 1545 | 1441 | 1364 | 12 | +4 | 1105 | 1060 | 1009 | 972.7 | 926.1
20_120 V, 60 Hz, 1 ph. (PSC only)_1 | 20 | Low | 1759 | 1691 | 1652 | 1580 | 1512 |  |  |  | 20 | Low | 1759 | 1691 | 1652 | 1580 | 1512 | 12 | 5 | 1047.6 | 990 | 951.2 | 910.2 | 852.1
20_120 V, 60 Hz, 1 ph. (PSC only)_2 | 20 | Med | 1838 | 1788 | 1729 | 1644 | 1555 |  |  |  |  | Med | 1838 | 1788 | 1729 | 1644 | 1555 | 16 | 1 | 957.1 | 772.7 | 655.9 | 599.3 | 530.7
20_120 V, 60 Hz, 1 ph. (PSC only)_3 | 20 | *High | 1928 | 1867 | 1810 | 1729 | 1637 |  |  |  |  | *High | 1928 | 1867 | 1810 | 1729 | 1637 | 16 | 2 | 1020.1 | 957.1 | 915.6 | 869.5 | 827.7
8_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 8 | 1 | 502.2 | 265.5 | 155.3 | 155.8 | 155.7 | [10 empty] | 16 | *3 | 1617.2 | 1579.8 | 1543.9 | 1511.6 | 1480.2
8_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 8 | 2 | 667.4 | 667.8 | 636.2 | 596.9 | 562 | [10 empty] | 16 | +4 | 1430.8 | 1390.5 | 1356.4 | 1324.9 | 1294.1
8_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 8 | *3 | 1008.1 | 980 | 925.1 | 932.9 | 915.4 | [10 empty] | 16 | 5 | 1384.8 | 1341.6 | 1301.4 | 1267.3 | 1232.8
8_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 8 | +4 | 856.3 | 838.9 | 819.3 | 793.6 | 783.3 | [10 empty] | 20 | 1 | 1112.7 | 899.8 | 756.6 | 677.5 | 595.4
8_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 8 | 5 | 789.8 | 757.9 | 739.8 | 734.4 | 696.1 | [10 empty] | 20 | 2 | 1359.6 | 1303.7 | 1249.4 | 1203.2 | 1144.8
12_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 12 | 1 | 839.2 | 657.9 | 320.3 | 257.6 | 219.6 | [10 empty] | 20 | *3 | 1924.3 | 1856.6 | 1799.2 | 1737.9 | 1692.2
12_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 12 | 2 | 915.3 | 761.5 | 663.7 | 617.1 | 566.6 | [10 empty] | 20 | +4 | 1556.9 | 1497.7 | 1427.1 | 1380.9 | 1320.8
12_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 12 | *3 | 1314.8 | 1263.9 | 1226.7 | 1186.8 | 1151 | [10 empty] | 20 | 5 | 1777.5 | 1688.6 | 1604.2 | 1543 | 1477.7
12_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 12 | +4 | 1105 | 1060 | 1009 | 972.7 | 926.1
12_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 12 | 5 | 1047.6 | 990 | 951.2 | 910.2 | 852.1 | [10 empty] | Speeds marked with * denote cooling airflow.
Speeds marked with + denote heating airflow.
16_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 16 | 1 | 957.1 | 772.7 | 655.9 | 599.3 | 530.7 | [10 empty] | All data is given while air handler is operating with a dry DX coil and air filter installed.
These are nominal values and blower performance can vary higher or lower from
16_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 16 | 2 | 1020.1 | 957.1 | 915.6 | 869.5 | 827.7 | [10 empty] | these values based on the evaporator coil that is used.
16_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 16 | *3 | 1617.2 | 1579.8 | 1543.9 | 1511.6 | 1480.2
16_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 16 | +4 | 1430.8 | 1390.5 | 1356.4 | 1324.9 | 1294.1
16_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 16 | 5 | 1384.8 | 1341.6 | 1301.4 | 1267.3 | 1232.8 |  |  |  | Speeds marked in bold with an asterisk* are the factory speed settings for both heating and cooling.
20_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 20 | 1 | 1112.7 | 899.8 | 756.6 | 677.5 | 595.4 |  |  |  | All data is given while air handler is operating with a dry DX coil and air filter installed.
20_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 20 | 2 | 1359.6 | 1303.7 | 1249.4 | 1203.2 | 1144.8 |  |  |  | These are nominal values and blower performance can vary higher or lower from these values based on the evaporator coil that is used.
20_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 20 | *3 | 1924.3 | 1856.6 | 1799.2 | 1737.9 | 1692.2 |  |  |  | Hot water heat airflow performance data includes associated air pressure drop across a 4 row hot water coil for Unit Size 08, 12, & 16;
20_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 20 | +4 | 1556.9 | 1497.7 | 1427.1 | 1380.9 | 1320.8 |  |  |  | air pressure drop across a 3 row hot water coil for Unit Size 20.
20_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 20 | 5 | 1777.5 | 1688.6 | 1604.2 | 1543 | 1477.7

## Electrial data (hidden)
No Electric Heat
| Unit Size | Electric Heating Capacity |  | Blower Amps (A) | Total Current, (A) | Minimum Circuit Ampacity (A) | Maximum Circuit Breaker size (A)
|  | kW [1] | BTUH
|  | 120 V | 120 V | 120 V | 120 V | 120 V | 120 V | [6 empty] | 3-speed PSC motor
3-speed PSC motor_8_none_1 | 8 | 0 | 0 | 5 | 5 | 6.25 | 15 | [6 empty] | 3-speed PSC motor
3-speed PSC motor_12_none_1 | 12 | 0 | 0 | 7.4 | 7.4 | 9.25 | 15 | [6 empty] | 3-speed PSC motor
3-speed PSC motor_16_none_1 | 16 | 0 | 0 | 8.4 | 8.4 | 10.5 | 15 | [6 empty] | 3-speed PSC motor
3-speed PSC motor_20_none_1 | 20 | 0 | 0 | 11.1 | 11.1 | 13.875 | 15 | [6 empty] | 3-speed PSC motor
Electric Data
| Unit Size | Circuit | Total Heat Capacity | Heating capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker size[2] (A)
|  |  |  | kW | BTUH
|  |  |  | 240 V[1] | 240 V[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
5-speed ECM motor_8_none_1 | 8 | CKT 1 | 0 | 0 | 0 | 2.4 | 2.4 | 2.4 | 2.4 | 3 | 3 | 15 | 15 | 3-speed PSC motor
5-speed ECM motor_8_none_1 | 8 | CKT 1 | 5 | 5 | 17060.71 | 2.4 | 2.4 | 20.4556 | 23.2333 | 25.5694 | 29.0417 | 30 | 30 | 5-speed ECM motor
5-speed ECM motor_8_none_1 | 8 | CKT 1 | 7.5 | 7.5 | 25591.065 | 2.4 | 2.4 | 29.4833 | 33.65 | 36.8542 | 42.0625 | 40 | 45
5-speed ECM motor_8_none_1 | 8 | CKT 1 | 10 | 10 | 34121.42 | 2.4 | 2.4 | 38.5111 | 44.0667 | 48.1389 | 55.0833 | 50 | 60
5-speed ECM motor_12_none_1 | 12 | CKT 1 | 0 | 0 | 0 | 4.1 | 4.1 | 4.1 | 4.1 | 5.125 | 5.125 | 15 | 15
5-speed ECM motor_12_none_1 | 12 | CKT 1 | 5 | 5 | 17060.71 | 4.1 | 4.1 | 22.1556 | 24.9333 | 27.6944 | 31.1667 | 30 | 35
5-speed ECM motor_12_none_1 | 12 | CKT 1 | 7.5 | 7.5 | 25591.065 | 4.1 | 4.1 | 31.1833 | 35.35 | 38.9792 | 44.1875 | 40 | 45
5-speed ECM motor_12_none_1 | 12 | CKT 1 | 10 | 10 | 34121.42 | 4.1 | 4.1 | 40.2111 | 45.7667 | 50.2639 | 57.2083 | 60 | 60
5-speed ECM motor_12_none_1 | 12 | CKT 1 | 15 | 10 | 34121.42 | 4.1 | 4.1 | 40.2111 | 45.7667 | 50.2639 | 57.2083 | 60 | 60
5-speed ECM motor_12_none_1 | 12 | CKT 2 | 15 | 5 | 17060.71 | 0 | 0 | 18.0556 | 20.8333 | 22.5694 | 26.0417 | 25 | 30
5-speed ECM motor_16_none_1 | 16 | CKT 1 | 0 | 0 | 0 | 6 | 6 | 6 | 6 | 7.5 | 7.5 | 15 | 15
5-speed ECM motor_16_none_1 | 16 | CKT 1 | 7.5 | 7.5 | 25591.065 | 6 | 6 | 33.0833 | 37.25 | 41.3542 | 46.5625 | 45 | 50
5-speed ECM motor_16_none_1 | 16 | CKT 1 | 10 | 10 | 34121.42 | 6 | 6 | 42.1111 | 47.6667 | 52.6389 | 59.5833 | 60 | 60
5-speed ECM motor_16_none_1 | 16 | CKT 1 | 15 | 10 | 34121.42 | 6 | 6 | 42.1111 | 47.6667 | 52.6389 | 59.5833 | 60 | 60
5-speed ECM motor_16_none_1 | 16 | CKT 2 | 15 | 5 | 17060.71 | 0 | 0 | 18.0556 | 20.8333 | 22.5694 | 26.0417 | 25 | 30
5-speed ECM motor_16_none_1 | 16 | CKT 1 | 20 | 10 | 34121.42 | 6 | 6 | 42.1111 | 47.6667 | 52.6389 | 59.5833 | 60 | 60
5-speed ECM motor_16_none_1 | 16 | CKT 2 | 20 | 10 | 34121.42 | 0 | 0 | 36.1111 | 41.6667 | 45.1389 | 52.0833 | 50 | 60
5-speed ECM motor_20_none_1 | 20 | CKT 1 | 0 | 0 | 0 | 6.1 | 6.1 | 6.1 | 6.1 | 7.625 | 7.625 | 15 | 15
5-speed ECM motor_20_none_1 | 20 | CKT 1 | 7.5 | 7.5 | 25591.065 | 6.1 | 6.1 | 33.1833 | 37.35 | 41.4792 | 46.6875 | 45 | 50
5-speed ECM motor_20_none_1 | 20 | CKT 1 | 10 | 10 | 34121.42 | 6.1 | 6.1 | 42.2111 | 47.7667 | 52.7639 | 59.7083 | 60 | 60
5-speed ECM motor_20_none_1 | 20 | CKT 1 | 15 | 10 | 34121.42 | 6.1 | 6.1 | 42.2111 | 47.7667 | 52.7639 | 59.7083 | 60 | 60
5-speed ECM motor_20_none_1 | 20 | CKT 2 | 15 | 5 | 17060.71 | 0 | 0 | 18.0556 | 20.8333 | 22.5694 | 26.0417 | 25 | 30
5-speed ECM motor_20_none_1 | 20 | CKT 1 | 20 | 10 | 34121.42 | 6.1 | 6.1 | 42.2111 | 47.7667 | 52.7639 | 59.7083 | 60 | 60
5-speed ECM motor_20_none_1 | 20 | CKT 2 | 20 | 10 | 34121.42 | 0 | 0 | 36.1111 | 41.6667 | 45.1389 | 52.0833 | 50 | 60
kW packages in bold italics indicate that these heat packages require and include circuit breakers; circuit breakers are optional for all other models.
[1] For 208 Volts use 0.751 correction factor for kW & BTUH.
[2] Circuit breaker supplied with the electric heat kit may need to be changed.

## Dim (hidden)
Dimensions |  |  |  | Supply Duct Opening |  | Return Duct Opening
Unit size | A (in) | B (in) | C (in) | Depth (in) | Width (in) | Depth (in) | Width (in)
8 | 27 | 20.5 | 17.5 | 16 | 15.5 | 19.25 | 16
12 | 27 | 20.5 | 17.5 | 16 | 15.5 | 19.25 | 16
16 | 28 | 20.5 | 21 | 16 | 19 | 19.25 | 19.5
20 | 28 | 20.5 | 24.5 | 16 | 22.5 | 19.25 | 23