{"text_format":"1","workbook":"xlsx","n_sheets":61,"sheets":["notes","Options","Calcs","(C,H,T)4A3_18","(C,H,T)4A3_24","(C,H,T)4A3_30","(C,H,T)4A3_36","(C,H,T)4A3_42","(C,H,T)4A3_48","(C,H,T)4A3_60","(C,H,T)4A4_18","(C,H,T)4A4_24","(C,H,T)4A4_30","(C,H,T)4A4_36","(C,H,T)4A4_42","(C,H,T)4A4_48","(C,H,T)4A4_49","(C,H,T)4A4_60","(C,H,T)XA6_18","(C,H,T)XA6_24","(C,H,T)XA6_30","(C,H,T)XA6_36","(C,H,T)XA6_42","(C,H,T)XA6_48","(C,H,T)XA6_49","(C,H,T)XA6_60","(C,H,T)XA6_61","N4A3_18","N4A3_24","N4A3_30","N4A3_36","N4A3_42","N4A3_48","N4A3_60","N4A4_18","N4A4_24","N4A4_30","N4A4_36","N4A4_42","N4A4_48","N4A4_49","N4A4_60","NXA6_18","NXA6_24","NXA6_30","NXA6_36","NXA6_42","NXA6_48","NXA6_49","NXA6_60","NXA6_61","R4A3_18","R4A3_24","R4A3_30","R4A3_36","R4A3_42","R4A3_48","R4A3_60","Form","Instructions","Prompt"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":0,"defined_names":124,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"notes","index":0,"n_rows":65,"n_cols":16,"rows_kept":65,"cut":false,"hidden":true,"merged":[]}
[]
[null,null,null,null,null,null,null,{"$f":"SUM(H3:H8)","v":0}]
[null,null,600,24,600,1000,{"$f":"IF(Form!$D$4=D3,1,0)","v":0},{"$f":"IF(G3=1,IF(OR(E3>Form!M$5,F3<Form!M$5),1,0),0)","v":0}]
[null,null,800,30,800,1200,{"$f":"IF(Form!$D$4=D4,1,0)","v":0},{"$f":"IF(G4=1,IF(OR(E4>Form!M$5,F4<Form!M$5),1,0),0)","v":0}]
[null,null,1000,36,1000,1400,{"$f":"IF(Form!$D$4=D5,1,0)","v":0},{"$f":"IF(G5=1,IF(OR(E5>Form!M$5,F5<Form!M$5),1,0),0)","v":0}]
[null,null,1200,42,1200,1600,{"$f":"IF(Form!$D$4=D6,1,0)","v":0},{"$f":"IF(G6=1,IF(OR(E6>Form!M$5,F6<Form!M$5),1,0),0)","v":0}]
[null,null,1400,48,1400,1800,{"$f":"IF(Form!$D$4=D7,1,0)","v":0},{"$f":"IF(G7=1,IF(OR(E7>Form!M$5,F7<Form!M$5),1,0),0)","v":0}]
[null,null,1600,60,1600,2000,{"$f":"IF(Form!$D$4=D8,1,0)","v":0},{"$f":"IF(G8=1,IF(OR(E8>Form!M$5,F8<Form!M$5),1,0),0)","v":0}]
[null,null,1800]
[null,null,2000]
[]
[]
[null,null,null,"Total"]
[null,{"$f":"Form!M5+Form!M6","v":0},null,null,{"$f":"E31","v":0},{"$f":"F31","v":0},0,0,0,0,0,{"$f":"SUM(E14:K14)","v":0},null,null,null,58]
[null,null,null,null,{"$f":"Form!C27","v":75},{"$f":"Form!E27","v":80},{"$f":"Form!G27","v":85},{"$f":"Form!I27","v":95},{"$f":"Form!K27","v":105},{"$f":"Form!M27","v":110},{"$f":"Form!O27","v":115}]
[{"$f":"C16+D16","v":0},{"$f":"P16","v":0},{"$f":"Form!A31","v":0},{"$f":"Form!B31","v":0},{"$f":"Form!C31","v":0},{"$f":"Form!E31","v":0},{"$f":"Form!G31","v":0},{"$f":"Form!I31","v":0},{"$f":"Form!K31","v":0},{"$f":"Form!M31","v":0},{"$f":"Form!O31","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C16+D16=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A16<L16,1,0)","v":0},{"$f":"IF(A16>L16,2,0)","v":0},{"$f":"IF(AND(N16=1,N17=0),1,0)+IF(AND(O15=0,O16=2),2,0)","v":0}]
[{"$f":"C17+D17","v":0},{"$f":"P17","v":0},{"$f":"C16","v":0},{"$f":"Form!B32","v":0},{"$f":"Form!C32","v":0},{"$f":"Form!E32","v":0},{"$f":"Form!G32","v":0},{"$f":"Form!I32","v":0},{"$f":"Form!K32","v":0},{"$f":"Form!M32","v":0},{"$f":"Form!O32","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C17+D17=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A17<L17,1,0)","v":0},{"$f":"IF(A17>L17,2,0)","v":0},{"$f":"IF(AND(N17=1,N18=0),1,0)+IF(AND(O16=0,O17=2),2,0)","v":0}]
[0,0,{"$f":"C17","v":0},{"$f":"Form!B33","v":0},{"$f":"Form!C33","v":0},{"$f":"Form!E33","v":0},{"$f":"Form!G33","v":0},{"$f":"Form!I33","v":0},{"$f":"Form!K33","v":0},{"$f":"Form!M33","v":0},{"$f":"Form!O33","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C18+D18=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A18>L18,2,0)","v":0},{"$f":"IF(AND(N18=1,N19=0),1,0)+IF(AND(O17=0,O18=2),2,0)","v":0}]
[0,0,{"$f":"C18","v":0},{"$f":"Form!B34","v":0},{"$f":"Form!C34","v":0},{"$f":"Form!E34","v":0},{"$f":"Form!G34","v":0},{"$f":"Form!I34","v":0},{"$f":"Form!K34","v":0},{"$f":"Form!M34","v":0},{"$f":"Form!O34","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C19+D19=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A19>L19,2,0)","v":0},{"$f":"IF(AND(N19=1,N20=0),1,0)+IF(AND(O18=0,O19=2),2,0)","v":0}]
[0,0,{"$f":"Form!A35","v":0},{"$f":"Form!B35","v":0},{"$f":"Form!C35","v":0},{"$f":"Form!E35","v":0},{"$f":"Form!G35","v":0},{"$f":"Form!I35","v":0},{"$f":"Form!K35","v":0},{"$f":"Form!M35","v":0},{"$f":"Form!O35","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C20+D20=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A20>L20,2,0)","v":0},{"$f":"IF(AND(N20=1,N21=0),1,0)+IF(AND(O19=0,O20=2),2,0)","v":0}]
[0,0,{"$f":"C20","v":0},{"$f":"Form!B36","v":0},{"$f":"Form!C36","v":0},{"$f":"Form!E36","v":0},{"$f":"Form!G36","v":0},{"$f":"Form!I36","v":0},{"$f":"Form!K36","v":0},{"$f":"Form!M36","v":0},{"$f":"Form!O36","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C21+D21=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A21>L21,2,0)","v":0},{"$f":"IF(AND(N21=1,N22=0),1,0)+IF(AND(O20=0,O21=2),2,0)","v":0}]
[0,0,{"$f":"C21","v":0},{"$f":"Form!B37","v":0},{"$f":"Form!C37","v":0},{"$f":"Form!E37","v":0},{"$f":"Form!G37","v":0},{"$f":"Form!I37","v":0},{"$f":"Form!K37","v":0},{"$f":"Form!M37","v":0},{"$f":"Form!O37","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C22+D22=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C22","v":0},{"$f":"Form!B38","v":0},{"$f":"Form!C38","v":0},{"$f":"Form!E38","v":0},{"$f":"Form!G38","v":0},{"$f":"Form!I38","v":0},{"$f":"Form!K38","v":0},{"$f":"Form!M38","v":0},{"$f":"Form!O38","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C23+D23=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"Form!A39","v":0},{"$f":"Form!B39","v":0},{"$f":"Form!C39","v":0},{"$f":"Form!E39","v":0},{"$f":"Form!G39","v":0},{"$f":"Form!I39","v":0},{"$f":"Form!K39","v":0},{"$f":"Form!M39","v":0},{"$f":"Form!O39","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C24+D24=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C24","v":0},{"$f":"Form!B40","v":0},{"$f":"Form!C40","v":0},{"$f":"Form!E40","v":0},{"$f":"Form!G40","v":0},{"$f":"Form!I40","v":0},{"$f":"Form!K40","v":0},{"$f":"Form!M40","v":0},{"$f":"Form!O40","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C25+D25=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C25","v":0},{"$f":"Form!B41","v":0},{"$f":"Form!C41","v":0},{"$f":"Form!E41","v":0},{"$f":"Form!G41","v":0},{"$f":"Form!I41","v":0},{"$f":"Form!K41","v":0},{"$f":"Form!M41","v":0},{"$f":"Form!O41","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C26+D26=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,{"$f":"C26","v":0},{"$f":"Form!B42","v":0},{"$f":"Form!C42","v":0},{"$f":"Form!E42","v":0},{"$f":"Form!G42","v":0},{"$f":"Form!I42","v":0},{"$f":"Form!K42","v":0},{"$f":"Form!M42","v":0},{"$f":"Form!O42","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C27+D27=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,{"$f":"SUM(B16:B27)","v":0}]
[null,null,null,null,null,{"$f":"IF(AND(F15>Form!$M$4,E15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(G15>Form!$M$4,F15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(H15>Form!$M$4,G15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(I15>Form!$M$4,H15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(J15>Form!$M$4,I15<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(K15>Form!$M$4,J15<Form!$M$4),2,0)","v":0}]
[null,null,{"$f":"HLOOKUP(1,E14:K15,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"IF(F29=2,1,0)","v":0},{"$f":"IF(G29=2,1,0)","v":0},0,0,0,0,0]
[null,null,{"$f":"HLOOKUP(2,E14:K15,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"SUM(E29:E30)","v":0},0,0,0,0,0,0]
[null,{"$f":"(VLOOKUP(1,B14:K27,3,FALSE))","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B32),0,B32)","v":0},null,{"$f":"(C34-C35)/(C32-C33)*(Form!$M$6-C33)+C35","v":{"$error":"#N/A"}},{"$f":"(C36-C37)/(C32-C33)*(Form!M6-C33)+C37","v":{"$error":"#N/A"}}]
[null,{"$f":"VLOOKUP(2,B14:K27,3,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B33),0,B33)","v":0},null,{"$f":"IF(AND(B28=0,L14=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A14:K27,MATCH(1,notes!A14:K14,FALSE),FALSE),0)","v":0},{"$f":"IF(AND(B28=0,L14=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A14:K27,MATCH(2,notes!A14:K14,FALSE),FALSE),0)","v":0},null,null,"exactly"]
[null,{"$f":"VLOOKUP(1,B14:K27,MATCH(1,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B34,B36)","v":{"$error":"#N/A"}},null,{"$f":"IF(ISERROR(E32),E33,E32)","v":0},{"$f":"IF(ISERROR(F32),F33,F32)","v":0},null,null,"x","y","err1","err2","err3","ans"]
[null,{"$f":"VLOOKUP(2,B14:K27,MATCH(1,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B35,B37)","v":{"$error":"#N/A"}},null,{"$f":"MIN(E34:F34)","v":0},{"$f":"MAX(E34:F34)","v":0},null,null,"y","y",{"$f":"IF(ISERROR(VLOOKUP(Form!$M$5+Form!$M$6,notes!A15:K27,MATCH(Form!$M$4,notes!A15:K15,FALSE),FALSE)),0,VLOOKUP(Form!$M$5+Form!$M$6,notes!A15:K27,MATCH(Form!$M$4,notes!A15:K15,FALSE),FALSE))","v":0},null,null,{"$f":"SUM(K35:M35)","v":0}]
[null,{"$f":"VLOOKUP(1,B14:K27,MATCH(2,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B36,B34)","v":{"$error":"#N/A"}},null,{"$f":"(E35-F35)/(C31-C30)*(Form!$M$4-C30)+F35","v":{"$error":"#N/A"}},null,null,null,"y","n",null,null,null,{"$f":"SUM(K36:M36)","v":0}]
[null,{"$f":"VLOOKUP(2,B14:K27,MATCH(2,B14:K14,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B35,B37)","v":{"$error":"#N/A"}},null,null,null,null,null,"n","n",{"$f":"IF(OR(E36>100000,E36<=0),0,E36)","v":{"$error":"#N/A"}},{"$f":"IF(K37<>0,0,MIN(E32:F32))","v":{"$error":"#N/A"}},{"$f":"IF(AND(L37=0,K37=0),C34,0)","v":{"$error":"#N/A"}},{"$f":"SUM(K37:M37)","v":{"$error":"#N/A"}}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(ISERROR(N37),N35,N37)","v":0}]
[]
[]
["sens",null,null,null,{"$f":"E58","v":0},{"$f":"F58","v":0},0,0,0,0,0,{"$f":"SUM(E41:K41)","v":0}]
[null,null,null,null,{"$f":"E15","v":75},{"$f":"F15","v":80},85,95,105,110,115]
[{"$f":"C43+D43","v":0},{"$f":"P43","v":0},{"$f":"C16","v":0},{"$f":"D16","v":0},{"$f":"Form!D31","v":0},{"$f":"Form!F31","v":0},{"$f":"Form!H31","v":0},{"$f":"Form!J31","v":0},{"$f":"Form!L31","v":0},{"$f":"Form!N31","v":0},{"$f":"Form!P31","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C43+D43=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A43<L43,1,0)","v":0},{"$f":"IF(A43>L43,2,0)","v":0},{"$f":"IF(AND(N43=1,N44=0),1,0)+IF(AND(O42=0,O43=2),2,0)","v":0}]
[{"$f":"C44+D44","v":0},{"$f":"P44","v":0},{"$f":"C17","v":0},{"$f":"D17","v":0},{"$f":"Form!D32","v":0},{"$f":"Form!F32","v":0},{"$f":"Form!H32","v":0},{"$f":"Form!J32","v":0},{"$f":"Form!L32","v":0},{"$f":"Form!N32","v":0},{"$f":"Form!P32","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C44+D44=Form!M$5+Form!M$6,1,0)","v":1},{"$f":"IF(A44<L44,1,0)","v":0},{"$f":"IF(A44>L44,2,0)","v":0},{"$f":"IF(AND(N44=1,N45=0),1,0)+IF(AND(O43=0,O44=2),2,0)","v":0}]
[{"$f":"C45+D45","v":0},0,0,0,{"$f":"Form!D33","v":0},{"$f":"Form!F33","v":0},{"$f":"Form!H33","v":0},{"$f":"Form!J33","v":0},{"$f":"Form!L33","v":0},{"$f":"Form!N33","v":0},{"$f":"Form!P33","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C45+D45=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A45>L45,2,0)","v":0},{"$f":"IF(AND(N45=1,N46=0),1,0)+IF(AND(O44=0,O45=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D34","v":0},{"$f":"Form!F34","v":0},{"$f":"Form!H34","v":0},{"$f":"Form!J34","v":0},{"$f":"Form!L34","v":0},{"$f":"Form!N34","v":0},{"$f":"Form!P34","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C46+D46=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A46>L46,2,0)","v":0},{"$f":"IF(AND(N46=1,N47=0),1,0)+IF(AND(O45=0,O46=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D35","v":0},{"$f":"Form!F35","v":0},{"$f":"Form!H35","v":0},{"$f":"Form!J35","v":0},{"$f":"Form!L35","v":0},{"$f":"Form!N35","v":0},{"$f":"Form!P35","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C47+D47=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A47>L47,2,0)","v":0},{"$f":"IF(AND(N47=1,N48=0),1,0)+IF(AND(O46=0,O47=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D36","v":0},{"$f":"Form!F36","v":0},{"$f":"Form!H36","v":0},{"$f":"Form!J36","v":0},{"$f":"Form!L36","v":0},{"$f":"Form!N36","v":0},{"$f":"Form!P36","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C48+D48=Form!M$5+Form!M$6,1,0)","v":1},0,{"$f":"IF(A48>L48,2,0)","v":0},{"$f":"IF(AND(N48=1,N49=0),1,0)+IF(AND(O47=0,O48=2),2,0)","v":0}]
[0,0,0,0,{"$f":"Form!D37","v":0},{"$f":"Form!F37","v":0},{"$f":"Form!H37","v":0},{"$f":"Form!J37","v":0},{"$f":"Form!L37","v":0},{"$f":"Form!N37","v":0},{"$f":"Form!P37","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C49+D49=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D38","v":0},{"$f":"Form!F38","v":0},{"$f":"Form!H38","v":0},{"$f":"Form!J38","v":0},{"$f":"Form!L38","v":0},{"$f":"Form!N38","v":0},{"$f":"Form!P38","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C50+D50=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D39","v":0},{"$f":"Form!F39","v":0},{"$f":"Form!H39","v":0},{"$f":"Form!J39","v":0},{"$f":"Form!L39","v":0},{"$f":"Form!N39","v":0},{"$f":"Form!P39","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C51+D51=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D40","v":0},{"$f":"Form!F40","v":0},{"$f":"Form!H40","v":0},{"$f":"Form!J40","v":0},{"$f":"Form!L40","v":0},{"$f":"Form!N40","v":0},{"$f":"Form!P40","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C52+D52=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D41","v":0},{"$f":"Form!F41","v":0},{"$f":"Form!H41","v":0},{"$f":"Form!J41","v":0},{"$f":"Form!L41","v":0},{"$f":"Form!N41","v":0},{"$f":"Form!P41","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C53+D53=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,0,0,0,{"$f":"Form!D42","v":0},{"$f":"Form!F42","v":0},{"$f":"Form!H42","v":0},{"$f":"Form!J42","v":0},{"$f":"Form!L42","v":0},{"$f":"Form!N42","v":0},{"$f":"Form!P42","v":0},{"$f":"Form!$M$5+Form!M$6","v":0},{"$f":"IF(C54+D54=Form!M$5+Form!M$6,1,0)","v":1},0,0,0]
[0,{"$f":"SUM(B43:B54)","v":0}]
[null,null,null,null,null,{"$f":"IF(AND(F42>Form!$M$4,E42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(G42>Form!$M$4,F42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(H42>Form!$M$4,G42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(I42>Form!$M$4,H42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(J42>Form!$M$4,I42<Form!$M$4),2,0)","v":0},{"$f":"IF(AND(K42>Form!$M$4,J42<Form!$M$4),2,0)","v":0}]
[null,null,{"$f":"HLOOKUP(1,E41:K42,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"IF(F56=2,1,0)","v":0},{"$f":"IF(G56=2,1,0)","v":0},0,0,0,0,0]
[null,null,{"$f":"HLOOKUP(2,E41:K42,2,FALSE)","v":{"$error":"#N/A"}},null,{"$f":"SUM(E56:E57)","v":0},0,0,0,0,0,0]
[null,{"$f":"(VLOOKUP(1,B41:K54,3,FALSE))","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B59),0,B59)","v":0},null,{"$f":"(C61-C62)/(C59-C60)*(Form!$M$6-C60)+C62","v":{"$error":"#N/A"}},{"$f":"(C63-C64)/(C59-C60)*(Form!M6-C60)+C64","v":{"$error":"#N/A"}}]
[null,{"$f":"VLOOKUP(2,B41:K54,3,FALSE)","v":{"$error":"#N/A"}},{"$f":"IF(ISERROR(B60),0,B60)","v":0},null,{"$f":"IF(AND(B55=0,L41=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A41:K54,MATCH(1,notes!A41:K41,FALSE),FALSE),0)","v":0},{"$f":"IF(AND(B55=0,L41=3),VLOOKUP(Form!$M$5+Form!$M$6,notes!A41:K54,MATCH(2,notes!A41:K41,FALSE),FALSE),0)","v":0},null,null,"exactly"]
[null,{"$f":"VLOOKUP(1,B41:K54,MATCH(1,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B61,B63)","v":{"$error":"#N/A"}},null,{"$f":"IF(ISERROR(E59),E60,E59)","v":0},{"$f":"IF(ISERROR(F59),F60,F59)","v":0},null,null,"x","y","err1","err2","err3","ans"]
[null,{"$f":"VLOOKUP(2,B41:K54,MATCH(1,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B62,B64)","v":{"$error":"#N/A"}},null,{"$f":"MIN(E61:F61)","v":0},{"$f":"MAX(E61:F61)","v":0},null,null,"y","y",{"$f":"IF(ISERROR(VLOOKUP(Form!$M$5+Form!$M$6,notes!A42:K54,MATCH(Form!$M$4,notes!A42:K42,FALSE),FALSE)),0,VLOOKUP(Form!$M$5+Form!$M$6,notes!A42:K54,MATCH(Form!$M$4,notes!A42:K42,FALSE),FALSE))","v":0},null,null,{"$f":"SUM(K62:M62)","v":0}]
[null,{"$f":"VLOOKUP(1,B41:K54,MATCH(2,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MAX(B63,B61)","v":{"$error":"#N/A"}},null,{"$f":"(E62-F62)/(C58-C57)*(Form!$M$4-C57)+F62","v":{"$error":"#N/A"}},null,null,null,"y","n",null,null,null,{"$f":"SUM(K63:M63)","v":0}]
[null,{"$f":"VLOOKUP(2,B41:K54,MATCH(2,B41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},{"$f":"MIN(B62,B64)","v":{"$error":"#N/A"}},null,null,null,null,null,"n","n",{"$f":"IF(OR(E63>100000,E63<=0),0,E63)","v":{"$error":"#N/A"}},{"$f":"IF(K64<>0,0,MIN(E59:F59))","v":{"$error":"#N/A"}},{"$f":"IF(AND(L64=0,K64=0),C61,0)","v":{"$error":"#N/A"}},{"$f":"SUM(K64:M64)","v":{"$error":"#N/A"}}]
[null,{"$f":"VLOOKUP(Form!M32+Form!M33,A41:K54,MATCH(2,A41:K41,FALSE),FALSE)","v":{"$error":"#N/A"}},null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(ISERROR(N64),N62,N64)","v":0}]

{"sheet":"Options","index":1,"n_rows":7,"n_cols":1,"rows_kept":7,"cut":false,"hidden":true,"merged":[]}
["(C,H,T)4A3"]
["(C,H,T)4A4"]
["(C,H,T)XA6"]
["N4A3"]
["N4A4"]
["NXA6"]
["R4A3"]

{"sheet":"Calcs","index":2,"n_rows":21,"n_cols":7,"rows_kept":21,"cut":false,"hidden":true,"merged":[[0,4,0,9],[1,4,1,9]]}
[null,null,null,"Condenser :  "]
[null,null,null,"ADP Evaporator:  "]
[null,null,null,"Condenser Entering Air Temperature: ",100,"(°F) Dry Bulb, 85°F to 115°F"]
[null,null,null,"Evaporator Air Flow:",1265,"CFM"]
[null,null,null,"Entering Evaporator Air (DB):  ",77.5,"(°F) Dry Bulb"]
[null,null,null,"Entering Evaporator Air (WB):  ",60.6,"(°F) Wet Bulb, 63°F to 71°F"]
[]
[]
["Total"]
[28.549999999999997,"1200 60.6"]
[]
[null,"Diff 200",{"$f":"A10-A14","v":0.30799999999999983},"Diff 1 cfm",{"$f":"C12/200","v":1.5399999999999991E-3},"  1265 total",{"$f":"A10-(65*E12)","v":28.449899999999996}]
[]
[28.241999999999997,"1400 60.6"]
[]
["Sens"]
[25.319999999999997,"1200 60.6"]
[]
[null,"Diff 200",{"$f":"A17-A21","v":0.55439999999999756},"Diff 1 cfm",{"$f":"C19/200","v":2.771999999999988E-3},"  1265 Sens",{"$f":"A17-(65*E19)","v":25.139819999999997}]
[]
[24.765599999999999,"1400 60.6"]

{"sheet":"(C,H,T)4A3_18","index":3,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.233720930232558},{"$f":"IF(AM8>C8,C8,AM8)","v":10.616860465116279},{"$f":"S8*$I$13","v":20.768023255813954},{"$f":"IF(AN8>E8,E8,AN8)","v":10.384011627906977},{"$f":"T8*$I$13","v":20.302325581395348},{"$f":"IF(AO8>G8,G8,AO8)","v":10.151162790697674},{"$f":"U8*$I$13","v":19.308139534883718},{"$f":"IF(AP8>I8,I8,AP8)","v":9.8471511627906967},{"$f":"V8*$I$13","v":18.334883720930232},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.534139534883721},{"$f":"W8*$I$13","v":17.795930232558138},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3428633720930225},{"$f":"X8*$I$13","v":17.256976744186048},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1461976744186053},null,1.1796511627906976,1.1537790697674419,1.1279069767441861,1.0726744186046511,1.0186046511627906,0.98866279069767438,0.95872093023255811,0.5,0.5,0.5,0.51,0.52,0.52500000000000002,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.616860465116279},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.384011627906977},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.151162790697674},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.8471511627906967},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.534139534883721},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3428633720930225},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1461976744186053}]
[null,67,19.548837209302327,13.09772093023256,19.109302325581393,{"$f":"IF(AN9>E9,E9,AN9)","v":12.898779069767441},18.669767441860468,{"$f":"IF(AO9>G9,G9,AO9)","v":12.69544186046512},{"$f":"U9*$I$13","v":17.738372093023255},{"$f":"IF(AP9>I9,I9,AP9)","v":12.239476744186044},16.79651162790698,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.925523255813955},16.283720930232562,{"$f":"IF(AR9>M9,M9,AR9)","v":11.724279069767444},15.77093023255814,{"$f":"IF(AS9>O9,O9,AS9)","v":11.512779069767442},null,1.086046511627907,1.061627906976744,1.0372093023255815,0.98546511627906974,0.93313953488372103,0.90465116279069779,0.87616279069767444,0.67,0.67500000000000004,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.09772093023256},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.898779069767441},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.69544186046512},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.239476744186044},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.925523255813955},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.724279069767444},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.512779069767442}]
[null,62,17.989534883720932,15.471000000000002,17.586627906976744,15.300366279069767,17.18372093023256,15.121674418604654,{"$f":"U10*$I$13","v":16.325581395348838},14.693023255813955,15.456976744186047,14.220418604651163,15.017441860465118,14.416744186046513,14.577906976744185,14.577906976744185,null,0.99941860465116295,0.97703488372093028,0.95465116279069784,0.90697674418604657,0.85872093023255813,0.83430232558139539,0.80988372093023253,0.86,0.87,0.88,0.9,0.92,0.96,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.471000000000002,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.300366279069767},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.121674418604654},14.693023255813955,14.220418604651163,14.416744186046513,14.577906976744185]
[null,57,17.466279069767445,17.466279069767445,17.136627906976745,17.136627906976745,16.806976744186045,16.806976744186045,{"$f":"U11*$I$13","v":16.105813953488372},16.105813953488372,15.373255813953488,15.373255813953488,14.975581395348836,14.975581395348836,14.577906976744185,14.577906976744185,null,0.97034883720930243,0.95203488372093026,0.93372093023255809,0.8947674418604652,0.85406976744186047,0.8319767441860465,0.80988372093023253,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.466279069767445,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.136627906976745},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.806976744186045},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.105813953488372},15.373255813953488,14.975581395348836,14.577906976744185]
[600,72,21.61046511627907,11.021337209302326,21.092441860465119,10.862607558139537,20.574418604651164,10.698697674418606,{"$f":"U12*$I$13","v":19.559302325581399},10.366430232558143,18.554651162790702,10.019511627906979,18.000000000000004,9.8100000000000023,17.445348837209306,9.5949418604651182,null,1.2005813953488371,1.1718023255813954,1.1430232558139535,1.0866279069767444,1.0308139534883722,1.0000000000000002,0.9691860465116281,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.021337209302326},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.862607558139537},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.698697674418606},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.366430232558143},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.019511627906979},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8100000000000023},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.5949418604651182}]
[null,67,19.86279069767442,13.903953488372093,19.412790697674421,13.686017441860466,18.962790697674418,13.463581395348836,18,13.14,17.037209302325582,12.777906976744188,16.50872093023256,12.546627906976745,15.980232558139535,12.304779069767443,null,1.1034883720930233,1.0784883720930234,1.0534883720930233,1,0.94651162790697685,0.91715116279069775,0.88779069767441865,0.7,0.70499999999999996,0.71,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.903953488372093},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.686017441860466},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.463581395348836},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.777906976744188},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.546627906976745},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.304779069767443}]
[null,62,18.376744186046512,16.539069767441863,17.968604651162792,16.35143023255814,17.560465116279072,16.155627906976747,{"$f":"U14*$I$13","v":16.70232558139535},16.70232558139535,15.948837209302326,15.948837209302326,15.525,15.525,15.101162790697675,15.101162790697675,null,1.0209302325581395,0.9982558139534885,0.97558139534883737,0.9279069767441861,0.88604651162790704,0.86250000000000004,0.83895348837209305,0.9,0.91,0.92,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.539069767441863,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.35143023255814},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.155627906976747},16.70232558139535,15.948837209302326,15.525,15.101162790697675]
[null,57,18.156976744186046,18.156976744186046,17.811627906976749,17.811627906976749,17.466279069767445,17.466279069767445,16.723255813953489,16.723255813953489,15.948837209302326,15.948837209302326,15.530232558139534,15.530232558139534,15.111627906976743,15.111627906976743,null,1.0087209302325582,0.98953488372093046,0.97034883720930243,0.92906976744186054,0.88604651162790704,0.86279069767441863,0.83953488372093021,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.156976744186046,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.811627906976749},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.466279069767445},16.723255813953489,15.948837209302326,15.530232558139534,15.111627906976743]
[675,72,21.851162790697675,11.581116279069768,21.306976744186048,11.399232558139536,20.762790697674419,11.211906976744187,19.716279069767442,10.843953488372094,18.70116279069768,10.472651162790701,18.136046511627903,10.246866279069764,17.57093023255814,10.015430232558138,null,1.213953488372093,1.1837209302325582,1.1534883720930234,1.0953488372093023,1.0389534883720932,1.0075581395348836,0.97616279069767442,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.581116279069768},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.399232558139536},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.211906976744187},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.843953488372094},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.472651162790701},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.246866279069764},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.015430232558138}]
[null,67,20.082558139534886,14.660267441860466,19.622093023255815,14.422238372093023,19.161627906976747,14.179604651162792,18.17790697674419,13.815209302325584,17.2046511627907,13.591674418604654,16.665697674418606,13.332558139534886,16.126744186046512,13.062662790697676,null,1.1156976744186047,1.0901162790697674,1.0645348837209303,1.0098837209302327,0.95581395348837217,0.9258720930232559,0.89593023255813953,0.73,0.73499999999999999,0.74,0.76,0.79,0.8,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.660267441860466},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.422238372093023},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.179604651162792},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.815209302325584},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.591674418604654},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.332558139534886},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.062662790697676}]
[null,62,18.743023255813952,18.555593023255813,18.366279069767444,18.274447674418607,17.989534883720932,17.989534883720932,17.2046511627907,17.2046511627907,16.409302325581397,16.409302325581397,15.969767441860466,15.969767441860466,15.530232558139534,15.530232558139534,null,1.0412790697674419,1.0203488372093024,0.99941860465116295,0.95581395348837217,0.91162790697674423,0.88720930232558137,0.86279069767441863,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.555593023255813,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.274447674418607},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.989534883720932},17.2046511627907,16.409302325581397,15.969767441860466,15.530232558139534]
[null,57,18.722093023255816,18.722093023255816,18.355813953488372,18.355813953488372,17.989534883720932,17.989534883720932,17.2046511627907,17.2046511627907,16.409302325581397,16.409302325581397,15.969767441860466,15.969767441860466,15.530232558139534,15.530232558139534,null,1.0401162790697676,1.0197674418604652,0.99941860465116295,0.95581395348837217,0.91162790697674423,0.88720930232558137,0.86279069767441863,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.722093023255816,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.355813953488372},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.989534883720932},17.2046511627907,16.409302325581397,15.969767441860466,15.530232558139534]

{"sheet":"(C,H,T)4A3_24","index":4,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.177391304347825},{"$f":"IF(AM8>C8,C8,AM8)","v":10.800469565217391},{"$f":"S8*$I$13","v":20.692173913043476},{"$f":"IF(AN8>E8,E8,AN8)","v":10.553008695652172},{"$f":"T8*$I$13","v":20.20695652173913},{"$f":"IF(AO8>G8,G8,AO8)","v":10.305547826086956},{"$f":"U8*$I$13","v":19.283478260869568},{"$f":"IF(AP8>I8,I8,AP8)","v":10.027408695652175},{"$f":"V8*$I$13","v":18.344347826086956},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7225043478260869},{"$f":"W8*$I$13","v":17.82391304347826},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5357934782608691},{"$f":"X8*$I$13","v":17.303478260869564},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3438782608695661},null,1.1765217391304348,1.1495652173913042,1.1226086956521739,1.0713043478260871,1.0191304347826087,0.99021739130434772,0.96130434782608698,0.51,0.51,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.800469565217391},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.553008695652172},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.305547826086956},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.027408695652175},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7225043478260869},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5357934782608691},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3438782608695661}]
[null,67,19.463478260869568,13.235165217391307,19.052608695652172,{"$f":"IF(AN9>E9,E9,AN9)","v":13.051036956521738},18.641739130434782,{"$f":"IF(AO9>G9,G9,AO9)","v":12.862799999999998},{"$f":"U9*$I$13","v":17.765217391304347},{"$f":"IF(AP9>I9,I9,AP9)","v":12.613304347826086},16.865217391304348,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.311608695652174},16.376086956521739,{"$f":"IF(AR9>M9,M9,AR9)","v":12.118304347826086},15.88695652173913,{"$f":"IF(AS9>O9,O9,AS9)","v":11.915217391304347},null,1.0813043478260871,1.0584782608695651,1.0356521739130435,0.9869565217391304,0.93695652173913047,0.9097826086956522,0.88260869565217392,0.68,0.68500000000000005,0.69,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.235165217391307},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.051036956521738},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.862799999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.613304347826086},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.311608695652174},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.118304347826086},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.915217391304347}]
[null,62,17.984347826086957,15.826226086956522,17.600869565217394,15.664773913043481,17.217391304347828,15.495652173913046,{"$f":"U10*$I$13","v":16.411304347826086},15.0984,15.589565217391305,14.654191304347826,15.182608695652172,14.727130434782607,14.775652173913043,14.775652173913043,null,0.99913043478260877,0.97782608695652184,0.95652173913043481,0.91173913043478261,0.86608695652173917,0.84347826086956512,0.82086956521739129,0.88,0.89,0.9,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.826226086956522,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.664773913043481},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.495652173913046},15.0984,14.654191304347826,14.727130434782607,14.775652173913043]
[null,57,17.538260869565217,17.538260869565217,17.225217391304348,17.225217391304348,16.912173913043478,16.912173913043478,{"$f":"U11*$I$13","v":16.239130434782609},16.239130434782609,15.534782608695652,15.534782608695652,15.155217391304349,15.155217391304349,14.775652173913043,14.775652173913043,null,0.97434782608695658,0.95695652173913037,0.93956521739130427,0.90217391304347827,0.86304347826086958,0.84195652173913049,0.82086956521739129,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.538260869565217,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.225217391304348},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.912173913043478},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.239130434782609},15.534782608695652,15.155217391304349,14.775652173913043]
[800,72,21.521739130434781,11.191304347826087,20.989565217391302,11.019521739130434,20.457391304347826,10.842417391304348,{"$f":"U12*$I$13","v":19.510434782608698},10.535634782608698,18.54,10.197000000000001,18.007826086956523,9.9943434782608715,17.475652173913041,9.7863652173913032,null,1.1956521739130435,1.1660869565217391,1.1365217391304347,1.0839130434782609,1.03,1.0004347826086957,0.97086956521739121,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.191304347826087},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.019521739130434},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.842417391304348},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.535634782608698},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.197000000000001},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9943434782608715},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7863652173913032}]
[null,67,19.753043478260871,14.024660869565217,19.326521739130438,13.915095652173916,18.900000000000002,13.797000000000001,18,13.5,17.084347826086955,12.984104347826086,16.579565217391306,12.849163043478262,16.074782608695649,12.699078260869564,null,1.0973913043478261,1.0736956521739132,1.05,1,0.94913043478260861,0.92108695652173911,0.89304347826086949,0.71,0.72,0.73,0.75,0.76,0.77500000000000002,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.024660869565217},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.915095652173916},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.797000000000001},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.984104347826086},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.849163043478262},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.699078260869564}]
[null,62,18.344347826086956,16.876799999999999,17.960869565217394,16.703608695652175,17.577391304347827,16.522747826086956,{"$f":"U14*$I$13","v":16.818260869565215},16.818260869565215,16.082608695652176,16.082608695652176,15.679565217391305,15.679565217391305,15.276521739130436,15.276521739130436,null,1.0191304347826087,0.99782608695652186,0.97652173913043483,0.93434782608695643,0.89347826086956528,0.87108695652173918,0.84869565217391307,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.876799999999999,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.703608695652175},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.522747826086956},16.818260869565215,16.082608695652176,15.679565217391305,15.276521739130436]
[null,57,18.195652173913043,18.195652173913043,17.866956521739127,17.866956521739127,17.538260869565217,17.538260869565217,16.818260869565215,16.818260869565215,16.082608695652176,16.082608695652176,15.679565217391305,15.679565217391305,15.276521739130436,15.276521739130436,null,1.0108695652173914,0.9926086956521738,0.97434782608695658,0.93434782608695643,0.89347826086956528,0.87108695652173918,0.84869565217391307,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.195652173913043,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.866956521739127},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.538260869565217},16.818260869565215,16.082608695652176,15.679565217391305,15.276521739130436]
[900,72,21.740869565217395,11.740069565217395,21.193043478260865,11.550208695652172,20.64521739130435,11.354869565217394,19.659130434782607,11.009113043478262,18.673043478260869,10.643634782608695,18.12521739130435,10.512626086956523,17.577391304347827,10.370660869565217,null,1.2078260869565218,1.1773913043478259,1.1469565217391304,1.0921739130434782,1.037391304347826,1.0069565217391305,0.97652173913043483,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.740069565217395},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.550208695652172},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.354869565217394},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.009113043478262},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.643634782608695},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.512626086956523},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.370660869565217}]
[null,67,19.964347826086957,14.973260869565218,19.526086956521741,14.742195652173915,19.087826086956522,14.506747826086956,18.164347826086956,14.168191304347827,17.233043478260868,13.786434782608694,16.720434782608699,13.627154347826089,16.207826086956523,13.452495652173914,null,1.1091304347826088,1.0847826086956522,1.0604347826086957,1.0091304347826087,0.95739130434782604,0.92891304347826098,0.90043478260869569,0.75,0.755,0.76,0.78,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.973260869565218},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.742195652173915},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.506747826086956},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.168191304347827},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.786434782608694},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.627154347826089},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.452495652173914}]
[null,62,18.72,18.72,18.375652173913046,18.375652173913046,18.031304347826083,18.031304347826083,17.28,17.28,16.513043478260869,16.513043478260869,16.09434782608696,16.09434782608696,15.675652173913043,15.675652173913043,null,1.04,1.0208695652173914,1.0017391304347825,0.96,0.91739130434782612,0.89413043478260879,0.87086956521739134,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.72,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.375652173913046},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.031304347826083},17.28,16.513043478260869,16.09434782608696,15.675652173913043]
[null,57,18.727826086956522,18.727826086956522,18.379565217391303,18.379565217391303,18.031304347826083,18.031304347826083,17.28,17.28,16.513043478260869,16.513043478260869,16.09434782608696,16.09434782608696,15.675652173913043,15.675652173913043,null,1.0404347826086957,1.0210869565217391,1.0017391304347825,0.96,0.91739130434782612,0.89413043478260879,0.87086956521739134,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.727826086956522,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.379565217391303},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.031304347826083},17.28,16.513043478260869,16.09434782608696,15.675652173913043]

{"sheet":"(C,H,T)4A3_30","index":5,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":36.493382352941175},{"$f":"IF(AM8>C8,C8,AM8)","v":18.611625},{"$f":"S8*$I$13","v":35.729779411764703},{"$f":"IF(AN8>E8,E8,AN8)","v":18.400836397058821},{"$f":"T8*$I$13","v":34.966176470588238},{"$f":"IF(AO8>G8,G8,AO8)","v":18.182411764705883},{"$f":"U8*$I$13","v":33.336397058823529},{"$f":"IF(AP8>I8,I8,AP8)","v":17.66829044117647},{"$f":"V8*$I$13","v":31.638235294117653},{"$f":"IF(AQ8>K8,K8,AQ8)","v":16.768264705882356},{"$f":"W8*$I$13","v":30.697977941176472},{"$f":"IF(AR8>M8,M8,AR8)","v":16.576908088235296},{"$f":"X8*$I$13","v":29.757720588235294},{"$f":"IF(AS8>O8,O8,AS8)","v":16.366746323529412},null,1.1772058823529412,1.1525735294117647,1.1279411764705882,1.0753676470588236,1.0205882352941178,0.99025735294117656,0.95992647058823533,0.51,0.51500000000000001,0.52,0.53,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":18.611625},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":18.400836397058821},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":18.182411764705883},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":17.66829044117647},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":16.768264705882356},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":16.576908088235296},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":16.366746323529412}]
[null,67,33.66691176470588,23.230169117647055,32.948897058823533,{"$f":"IF(AN9>E9,E9,AN9)","v":22.899483455882354},32.23088235294118,{"$f":"IF(AO9>G9,G9,AO9)","v":22.561617647058824},{"$f":"U9*$I$13","v":30.680882352941179},{"$f":"IF(AP9>I9,I9,AP9)","v":22.090235294117647},29.0625,{"$f":"IF(AQ9>K9,K9,AQ9)","v":21.506250000000001},28.173529411764704,{"$f":"IF(AR9>M9,M9,AR9)","v":21.130147058823528},27.284558823529416,{"$f":"IF(AS9>O9,O9,AS9)","v":20.736264705882355},null,1.0860294117647058,1.0628676470588236,1.0397058823529413,0.98970588235294121,0.9375,0.9088235294117647,0.8801470588235295,0.69,0.69499999999999995,0.7,0.72,0.74,0.75,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":23.230169117647055},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":22.899483455882354},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":22.561617647058824},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":22.090235294117647},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":21.506250000000001},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":21.130147058823528},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":20.736264705882355}]
[null,62,31.170955882352946,27.742150735294121,30.50992647058824,27.458933823529417,29.848897058823532,27.162496323529414,{"$f":"U10*$I$13","v":28.447058823529414},28.16258823529412,27.13639705882353,27.13639705882353,26.429779411764706,26.429779411764706,25.723161764705885,25.723161764705885,null,1.005514705882353,0.9841911764705884,0.96286764705882355,0.91764705882352948,0.87536764705882353,0.85257352941176467,0.82977941176470593,0.89,0.9,0.91,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,27.742150735294121,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":27.458933823529417},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":27.162496323529414},28.16258823529412,27.13639705882353,26.429779411764706,25.723161764705885]
[null,57,30.749264705882354,30.749264705882354,30.185110294117649,30.185110294117649,29.620955882352938,29.620955882352938,{"$f":"U11*$I$13","v":28.412867647058821},28.412867647058821,27.13639705882353,27.13639705882353,26.435477941176472,26.435477941176472,25.734558823529412,25.734558823529412,null,0.99191176470588238,0.97371323529411768,0.95551470588235288,0.91654411764705879,0.87536764705882353,0.85275735294117649,0.83014705882352935,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,30.749264705882354,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":30.185110294117649},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":29.620955882352938},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":28.412867647058821},27.13639705882353,26.435477941176472,25.734558823529412]
[1000,72,36.903676470588245,19.558948529411772,36.100183823529413,19.313598345588236,35.296691176470588,19.060213235294118,{"$f":"U12*$I$13","v":33.632720588235294},18.497996323529414,31.888970588235299,17.857823529411768,30.925919117647059,17.473144301470587,29.962867647058825,17.07883455882353,null,1.1904411764705884,1.1645220588235294,1.1386029411764707,1.0849264705882353,1.0286764705882354,0.99761029411764701,0.96654411764705883,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":19.558948529411772},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":19.313598345588236},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":19.060213235294118},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":18.497996323529414},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":17.857823529411768},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":17.473144301470587},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":17.07883455882353}]
[null,67,34.065808823529409,24.868040441176468,33.325000000000003,24.493875000000003,32.584191176470583,24.112301470588232,31,23.56,29.347426470588239,22.890992647058827,28.441360294117647,22.610881433823529,27.535294117647062,22.303588235294121,null,1.0988970588235294,1.0750000000000002,1.0511029411764705,1,0.94669117647058831,0.91746323529411766,0.88823529411764712,0.73,0.73499999999999999,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":24.868040441176468},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":24.493875000000003},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":24.112301470588232},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":23.56},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":22.890992647058827},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":22.610881433823529},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":22.303588235294121}]
[null,62,31.809191176470588,31.491099264705881,31.205147058823535,31.049121323529416,30.601102941176471,30.601102941176471,{"$f":"U14*$I$13","v":29.32463235294118},29.32463235294118,27.979779411764707,27.979779411764707,27.24466911764706,27.24466911764706,26.509558823529414,26.509558823529414,null,1.0261029411764706,1.0066176470588237,0.98713235294117652,0.94595588235294126,0.90257352941176472,0.8788602941176471,0.85514705882352948,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,31.491099264705881,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":31.049121323529416},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":30.601102941176471},29.32463235294118,27.979779411764707,27.24466911764706,26.509558823529414]
[null,57,31.786397058823532,31.786397058823532,31.193750000000001,31.193750000000001,30.601102941176471,30.601102941176471,29.32463235294118,29.32463235294118,27.991176470588236,27.991176470588236,27.250367647058823,27.250367647058823,26.509558823529414,26.509558823529414,null,1.0253676470588236,1.0062500000000001,0.98713235294117652,0.94595588235294126,0.90294117647058825,0.87904411764705881,0.85514705882352948,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,31.786397058823532,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":31.193750000000001},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":30.601102941176471},29.32463235294118,27.991176470588236,27.250367647058823,26.509558823529414]
[1125,72,37.154411764705891,20.434926470588241,36.333823529411767,20.165272058823533,35.513235294117642,19.887411764705881,33.815073529411762,19.274591911764702,32.037132352941178,18.581536764705881,31.051286764705878,18.320259191176469,30.065441176470589,18.039264705882353,null,1.1985294117647061,1.1720588235294118,1.1455882352941176,1.0908088235294118,1.0334558823529412,1.0016544117647057,0.96985294117647058,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":20.434926470588241},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":20.165272058823533},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":19.887411764705881},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":19.274591911764702},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":18.581536764705881},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":18.320259191176469},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":18.039264705882353}]
[null,67,34.339338235294115,26.097897058823527,33.581433823529409,25.857704044117646,32.823529411764703,25.60235294117647,31.216544117647061,24.97323529411765,29.541176470588237,24.519176470588235,28.618014705882356,24.039132352941177,27.694852941176471,23.540624999999999,null,1.1077205882352941,1.0832720588235294,1.0588235294117647,1.0069852941176471,0.95294117647058829,0.9231617647058824,0.89338235294117652,0.76,0.77,0.78,0.8,0.83,0.84,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":26.097897058823527},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":25.857704044117646},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":25.60235294117647},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":24.97323529411765},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":24.519176470588235},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":24.039132352941177},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":23.540624999999999}]
[null,62,32.595588235294116,32.595588235294116,31.980147058823533,31.980147058823533,31.36470588235294,31.36470588235294,30.031250000000004,30.031250000000004,28.640808823529412,28.640808823529412,27.871507352941176,27.871507352941176,27.102205882352944,27.102205882352944,null,1.0514705882352942,1.0316176470588236,1.0117647058823529,0.96875000000000011,0.92389705882352935,0.89908088235294115,0.87426470588235305,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,32.595588235294116,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":31.980147058823533},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":31.36470588235294},30.031250000000004,28.640808823529412,27.871507352941176,27.102205882352944]
[null,57,32.595588235294116,32.595588235294116,31.980147058823533,31.980147058823533,31.36470588235294,31.36470588235294,30.031250000000004,30.031250000000004,28.640808823529412,28.640808823529412,27.871507352941176,27.871507352941176,27.102205882352944,27.102205882352944,null,1.0514705882352942,1.0316176470588236,1.0117647058823529,0.96875000000000011,0.92389705882352935,0.89908088235294115,0.87426470588235305,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,32.595588235294116,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":31.980147058823533},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":31.36470588235294},30.031250000000004,28.640808823529412,27.871507352941176,27.102205882352944]

{"sheet":"(C,H,T)4A3_36","index":6,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.390340909090906},{"$f":"IF(AM8>C8,C8,AM8)","v":10.909073863636362},{"$f":"S8*$I$13","v":20.917329545454546},{"$f":"IF(AN8>E8,E8,AN8)","v":10.772424715909091},{"$f":"T8*$I$13","v":20.444318181818176},{"$f":"IF(AO8>G8,G8,AO8)","v":10.631045454545452},{"$f":"U8*$I$13","v":19.43181818181818},{"$f":"IF(AP8>I8,I8,AP8)","v":10.298863636363636},{"$f":"V8*$I$13","v":18.357954545454543},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.9132954545454535},{"$f":"W8*$I$13","v":17.772443181818179},{"$f":"IF(AR8>M8,M8,AR8)","v":9.6859815340909083},{"$f":"X8*$I$13","v":17.186931818181815},{"$f":"IF(AS8>O8,O8,AS8)","v":9.4528124999999985},null,1.1883522727272726,1.1620738636363637,1.1357954545454543,1.0795454545454544,1.0198863636363635,0.98735795454545439,0.95482954545454535,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.909073863636362},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.772424715909091},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.631045454545452},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.298863636363636},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.9132954545454535},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.6859815340909083},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.4528124999999985}]
[null,67,19.549431818181816,13.489107954545451,19.11221590909091,{"$f":"IF(AN9>E9,E9,AN9)","v":13.282990056818182},18.675000000000001,{"$f":"IF(AO9>G9,G9,AO9)","v":13.0725},{"$f":"U9*$I$13","v":17.744318181818183},{"$f":"IF(AP9>I9,I9,AP9)","v":12.775909090909092},16.752272727272725,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.229159090909089},16.215340909090909,{"$f":"IF(AR9>M9,M9,AR9)","v":12.080428977272726},15.67840909090909,{"$f":"IF(AS9>O9,O9,AS9)","v":11.915590909090909},null,1.0860795454545453,1.0617897727272727,1.0375000000000001,0.98579545454545459,0.93068181818181805,0.90085227272727264,0.87102272727272723,0.69,0.69499999999999995,0.7,0.72,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.489107954545451},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.282990056818182},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.0725},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.775909090909092},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.229159090909089},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.080428977272726},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.915590909090909}]
[null,62,17.902840909090909,15.93352840909091,17.509090909090904,15.758181818181814,17.115340909090907,15.574960227272726,{"$f":"U10*$I$13","v":16.276704545454542},15.137335227272725,15.402272727272726,14.786181818181817,14.949715909090907,14.650721590909088,14.497159090909092,14.497159090909092,null,0.99460227272727264,0.97272727272727255,0.95085227272727257,0.90426136363636356,0.8556818181818181,0.83053977272727264,0.80539772727272729,0.89,0.9,0.91,0.93,0.96,0.98,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.93352840909091,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.758181818181814},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.574960227272726},15.137335227272725,14.786181818181817,14.650721590909088,14.497159090909092]
[null,57,17.371022727272727,17.371022727272727,17.05142045454545,17.05142045454545,16.731818181818181,16.731818181818181,{"$f":"U11*$I$13","v":16.046590909090906},16.046590909090906,15.310227272727273,15.310227272727273,14.908806818181818,14.908806818181818,14.507386363636362,14.507386363636362,null,0.9650568181818181,0.94730113636363622,0.92954545454545445,0.89147727272727262,0.85056818181818183,0.82826704545454544,0.80596590909090904,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.371022727272727,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.05142045454545},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.731818181818181},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.046590909090906},15.310227272727273,14.908806818181818,14.507386363636362]
[1200,72,21.743181818181817,11.523886363636363,21.249715909090909,11.368598011363638,20.756249999999998,11.208375,{"$f":"U12*$I$13","v":19.702840909090906},10.639534090909089,18.588068181818183,10.409318181818184,17.982102272727271,10.159887784090907,17.376136363636363,9.904397727272725,null,1.2079545454545455,1.1805397727272728,1.153125,1.0946022727272726,1.0326704545454546,0.99900568181818172,0.96534090909090897,0.53,0.53500000000000003,0.54,0.54,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.523886363636363},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.368598011363638},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.208375},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.639534090909089},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.409318181818184},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.159887784090907},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.904397727272725}]
[null,67,19.886931818181818,14.318590909090908,19.429261363636364,14.086214488636363,18.97159090909091,13.849261363636364,18,13.5,16.977272727272727,13.0725,16.422443181818181,12.891617897727272,15.867613636363636,12.69409090909091,null,1.1048295454545454,1.079403409090909,1.0539772727272727,1,0.94318181818181823,0.91235795454545454,0.88153409090909085,0.72,0.72499999999999998,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.318590909090908},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.086214488636363},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.849261363636364},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.0725},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.891617897727272},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.69409090909091}]
[null,62,18.296590909090906,17.015829545454544,17.895170454545458,16.82146022727273,17.493749999999999,16.619062499999998,{"$f":"U14*$I$13","v":16.660227272727269},16.493624999999998,15.862499999999997,15.862499999999997,15.432954545454544,15.432954545454544,15.003409090909091,15.003409090909091,null,1.0164772727272726,0.99417613636363644,0.97187499999999993,0.92556818181818168,0.88124999999999987,0.85738636363636356,0.83352272727272725,0.93,0.94,0.95,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.015829545454544,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.82146022727273},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.619062499999998},16.493624999999998,15.862499999999997,15.432954545454544,15.003409090909091]
[null,57,18.061363636363637,18.061363636363637,17.721306818181819,17.721306818181819,17.381249999999998,17.381249999999998,16.64488636363636,16.64488636363636,15.862499999999997,15.862499999999997,15.432954545454544,15.432954545454544,15.003409090909091,15.003409090909091,null,1.0034090909090909,0.98451704545454544,0.96562499999999996,0.92471590909090895,0.88124999999999987,0.85738636363636356,0.83352272727272725,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.061363636363637,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.721306818181819},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.381249999999998},16.64488636363636,15.862499999999997,15.432954545454544,15.003409090909091]
[1350,72,22.003977272727273,11.882147727272727,21.492613636363632,11.713474431818181,20.981249999999999,11.539687500000001,19.897159090909089,11.142409090909091,18.751704545454544,10.688471590909089,18.12784090909091,10.514147727272727,17.503977272727269,10.327346590909087,null,1.2224431818181818,1.1940340909090907,1.1656249999999999,1.1053977272727271,1.0417613636363636,1.0071022727272727,0.97244318181818168,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.882147727272727},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.713474431818181},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.539687500000001},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.142409090909091},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.688471590909089},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.514147727272727},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.327346590909087}]
[null,67,20.132386363636364,15.099289772727273,19.661931818181817,14.844758522727272,19.191477272727273,14.585522727272727,18.194318181818183,14.191568181818184,17.146022727272726,13.888278409090908,16.578409090909091,13.677187499999999,16.010795454545452,13.449068181818179,null,1.118465909090909,1.0923295454545454,1.0661931818181818,1.0107954545454545,0.95255681818181814,0.92102272727272727,0.88948863636363629,0.75,0.755,0.76,0.78,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.099289772727273},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.844758522727272},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.585522727272727},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.191568181818184},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.888278409090908},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.677187499999999},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.449068181818179}]
[null,62,18.659659090909091,18.099869318181817,18.278693181818184,18.00451278409091,17.897727272727273,17.897727272727273,17.130681818181817,17.130681818181817,16.307386363636361,16.307386363636361,15.854829545454546,15.854829545454546,15.402272727272726,15.402272727272726,null,1.0366477272727272,1.0154829545454547,0.99431818181818177,0.95170454545454541,0.90596590909090902,0.88082386363636367,0.8556818181818181,0.97,0.98499999999999999,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.099869318181817,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.00451278409091},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.897727272727273},17.130681818181817,16.307386363636361,15.854829545454546,15.402272727272726]
[null,57,18.628977272727273,18.628977272727273,18.26846590909091,18.26846590909091,17.907954545454544,17.907954545454544,17.135795454545452,17.135795454545452,16.307386363636361,16.307386363636361,15.854829545454546,15.854829545454546,15.402272727272726,15.402272727272726,null,1.0349431818181818,1.0149147727272727,0.99488636363636362,0.95198863636363618,0.90596590909090902,0.88082386363636367,0.8556818181818181,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.628977272727273,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.26846590909091},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.907954545454544},17.135795454545452,16.307386363636361,15.854829545454546,15.402272727272726]

{"sheet":"(C,H,T)4A3_42","index":7,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.28829268292683},{"$f":"IF(AM8>C8,C8,AM8)","v":11.282795121951221},{"$f":"S8*$I$13","v":20.827317073170729},{"$f":"IF(AN8>E8,E8,AN8)","v":11.038478048780487},{"$f":"T8*$I$13","v":20.366341463414635},{"$f":"IF(AO8>G8,G8,AO8)","v":10.794160975609756},{"$f":"U8*$I$13","v":19.396097560975612},{"$f":"IF(AP8>I8,I8,AP8)","v":10.473892682926831},{"$f":"V8*$I$13","v":18.364390243902438},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.100414634146341},{"$f":"W8*$I$13","v":17.804634146341463},{"$f":"IF(AR8>M8,M8,AR8)","v":9.881571951219513},{"$f":"X8*$I$13","v":17.244878048780489},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6571317073170739},null,1.1826829268292682,1.1570731707317072,1.1314634146341465,1.0775609756097562,1.0202439024390244,0.98914634146341462,0.95804878048780495,0.53,0.53,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.282795121951221},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.038478048780487},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.794160975609756},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.473892682926831},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.100414634146341},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.881571951219513},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6571317073170739}]
[null,67,19.523414634146341,13.861624390243902,19.095365853658539,{"$f":"IF(AN9>E9,E9,AN9)","v":13.653186585365855},18.667317073170732,{"$f":"IF(AO9>G9,G9,AO9)","v":13.440468292682926},{"$f":"U9*$I$13","v":17.762926829268292},{"$f":"IF(AP9>I9,I9,AP9)","v":12.966936585365852},16.805853658536588,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.60439024390244},16.290000000000003,{"$f":"IF(AR9>M9,M9,AR9)","v":12.380400000000002},15.774146341463414,{"$f":"IF(AS9>O9,O9,AS9)","v":12.146092682926829},null,1.0846341463414635,1.0608536585365855,1.0370731707317074,0.98682926829268292,0.93365853658536591,0.90500000000000014,0.87634146341463415,0.71,0.71499999999999997,0.72,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.861624390243902},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.653186585365855},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.440468292682926},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.966936585365852},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.60439024390244},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.380400000000002},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.146092682926829}]
[null,62,17.925365853658537,16.31208292682927,17.539024390243902,16.135902439024392,17.152682926829268,15.951995121951221,{"$f":"U10*$I$13","v":16.340487804878048},15.523463414634145,15.493170731707316,15.183307317073169,15.060731707317073,14.910124390243903,14.62829268292683,14.62829268292683,null,0.99585365853658536,0.97439024390243911,0.95292682926829264,0.90780487804878041,0.86073170731707316,0.8367073170731707,0.81268292682926835,0.91,0.92,0.93,0.95,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.31208292682927,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.135902439024392},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.951995121951221},15.523463414634145,15.183307317073169,14.910124390243903,14.62829268292683]
[null,57,17.442439024390243,17.442439024390243,17.126341463414633,17.126341463414633,16.810243902439023,16.810243902439023,{"$f":"U11*$I$13","v":16.138536585365852},16.138536585365852,15.418536585365853,15.418536585365853,15.027804878048782,15.027804878048782,14.637073170731709,14.637073170731709,null,0.96902439024390241,0.9514634146341463,0.93390243902439019,0.89658536585365844,0.85658536585365852,0.83487804878048788,0.81317073170731713,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.442439024390243,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.126341463414633},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.810243902439023},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.138536585365852},15.418536585365853,15.027804878048782,14.637073170731709]
[1400,72,21.604390243902436,11.666370731707316,21.123658536585367,11.512393902439026,20.642926829268294,11.353609756097562,{"$f":"U12*$I$13","v":19.637560975609752},10.997034146341463,18.570731707317073,10.58531707317073,17.99341463414634,10.346213414634144,17.416097560975611,10.101336585365853,null,1.2002439024390243,1.1735365853658537,1.1468292682926831,1.0909756097560974,1.0317073170731708,0.99963414634146341,0.96756097560975618,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.666370731707316},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.512393902439026},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.353609756097562},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.997034146341463},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.58531707317073},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.346213414634144},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.101336585365853}]
[null,67,19.826341463414632,14.671492682926827,19.382926829268293,14.440280487804879,18.939512195121953,14.204634146341466,18,13.86,17.012195121951219,13.439634146341463,16.483170731707318,13.268952439024391,15.954146341463417,13.082400000000002,null,1.1014634146341462,1.076829268292683,1.0521951219512196,1,0.94512195121951215,0.91573170731707321,0.88634146341463427,0.74,0.745,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.671492682926827},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.440280487804879},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.204634146341466},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.439634146341463},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.268952439024391},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.082400000000002}]
[null,62,18.302926829268294,17.387780487804879,17.912195121951218,17.195707317073168,17.521463414634145,16.995819512195119,{"$f":"U14*$I$13","v":16.69170731707317},16.69170731707317,15.954146341463417,15.954146341463417,15.539268292682928,15.539268292682928,15.12439024390244,15.12439024390244,null,1.0168292682926829,0.99512195121951208,0.97341463414634133,0.92731707317073175,0.88634146341463427,0.86329268292682937,0.84024390243902447,0.95,0.96,0.97,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.387780487804879,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.195707317073168},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.995819512195119},16.69170731707317,15.954146341463417,15.539268292682928,15.12439024390244]
[null,57,18.109756097560975,18.109756097560975,17.77390243902439,17.77390243902439,17.438048780487804,17.438048780487804,16.718048780487806,16.718048780487806,15.954146341463417,15.954146341463417,15.539268292682928,15.539268292682928,15.12439024390244,15.12439024390244,null,1.0060975609756098,0.98743902439024389,0.96878048780487802,0.92878048780487799,0.88634146341463427,0.86329268292682937,0.84024390243902447,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.109756097560975,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.77390243902439},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.438048780487804},16.718048780487806,15.954146341463417,15.539268292682928,15.12439024390244]
[1575,72,21.841463414634145,12.231219512195123,21.347560975609756,12.061371951219511,20.853658536585364,11.886585365853657,19.817560975609759,11.494185365853658,18.72,11.044799999999999,18.127317073170733,10.785753658536585,17.534634146341464,10.520780487804878,null,1.2134146341463414,1.1859756097560976,1.1585365853658536,1.1009756097560977,1.04,1.0070731707317073,0.97414634146341461,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.57999999999999996,0.59,0.59499999999999997,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.231219512195123},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.061371951219511},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.886585365853657},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.494185365853658},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.044799999999999},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.785753658536585},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.520780487804878}]
[null,67,20.059024390243898,15.445448780487801,19.602439024390243,15.191890243902439,19.145853658536588,14.933765853658539,18.184390243902438,14.547512195121952,17.174634146341461,14.254946341463413,16.632439024390244,14.054410975609755,16.090243902439024,13.83760975609756,null,1.1143902439024389,1.0890243902439023,1.0636585365853659,1.0102439024390244,0.95414634146341459,0.92402439024390237,0.89390243902439026,0.77,0.77500000000000002,0.78,0.8,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.445448780487801},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.191890243902439},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.933765853658539},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.547512195121952},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.254946341463413},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":14.054410975609755},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.83760975609756}]
[null,62,18.667317073170732,18.480643902439024,18.305121951219512,18.213596341463415,17.942926829268291,17.942926829268291,17.183414634146342,17.183414634146342,16.38,16.38,15.943170731707315,15.943170731707315,15.506341463414634,15.506341463414634,null,1.0370731707317074,1.016951219512195,0.99682926829268281,0.95463414634146337,0.91,0.88573170731707307,0.86146341463414633,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.480643902439024,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.213596341463415},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.942926829268291},17.183414634146342,16.38,15.943170731707315,15.506341463414634]
[null,57,18.654146341463417,18.654146341463417,18.298536585365852,18.298536585365852,17.942926829268291,17.942926829268291,17.18780487804878,17.18780487804878,16.384390243902441,16.384390243902441,15.945365853658537,15.945365853658537,15.506341463414634,15.506341463414634,null,1.0363414634146342,1.0165853658536586,0.99682926829268281,0.95487804878048776,0.91024390243902442,0.88585365853658538,0.86146341463414633,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.654146341463417,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.298536585365852},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.942926829268291},17.18780487804878,16.384390243902441,15.945365853658537,15.506341463414634]

{"sheet":"(C,H,T)4A3_48","index":8,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.318260869565215},{"$f":"IF(AM8>C8,C8,AM8)","v":10.232765217391302},{"$f":"S8*$I$13","v":20.868260869565219},{"$f":"IF(AN8>E8,E8,AN8)","v":10.121106521739131},{"$f":"T8*$I$13","v":20.41826086956522},{"$f":"IF(AO8>G8,G8,AO8)","v":10.004947826086958},{"$f":"U8*$I$13","v":19.459565217391305},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7297826086956523},{"$f":"V8*$I$13","v":18.442173913043479},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.4055086956521752},{"$f":"W8*$I$13","v":17.896304347826089},{"$f":"IF(AR8>M8,M8,AR8)","v":9.216596739130436},{"$f":"X8*$I$13","v":17.350434782608698},{"$f":"IF(AS8>O8,O8,AS8)","v":9.0222260869565236},null,1.1843478260869564,1.1593478260869565,1.1343478260869566,1.0810869565217391,1.0245652173913045,0.99423913043478263,0.9639130434782609,0.48,0.48499999999999999,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.232765217391302},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.121106521739131},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.004947826086958},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7297826086956523},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.4055086956521752},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.216596739130436},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.0222260869565236}]
[null,67,19.486956521739131,12.666521739130436,19.062391304347827,{"$f":"IF(AN9>E9,E9,AN9)","v":12.581178260869565},18.637826086956526,{"$f":"IF(AO9>G9,G9,AO9)","v":12.487343478260874},{"$f":"U9*$I$13","v":17.741739130434784},{"$f":"IF(AP9>I9,I9,AP9)","v":12.064382608695654},16.798695652173912,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.759086956521738},16.291956521739131,{"$f":"IF(AR9>M9,M9,AR9)","v":11.567289130434782},15.78521739130435,{"$f":"IF(AS9>O9,O9,AS9)","v":11.365356521739132},null,1.0826086956521739,1.0590217391304348,1.0354347826086958,0.98565217391304361,0.93326086956521737,0.905108695652174,0.87695652173913052,0.65,0.66,0.67,0.68,0.7,0.71,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.666521739130436},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.581178260869565},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.487343478260874},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.064382608695654},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.759086956521738},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.567289130434782},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.365356521739132}]
[null,62,17.835652173913044,15.160304347826086,17.450217391304349,15.007186956521741,17.064782608695651,14.846360869565217,{"$f":"U10*$I$13","v":16.258695652173913},14.470239130434782,15.436956521739132,15.28258695652174,15.049565217391304,14.974317391304348,14.662173913043477,14.662173913043477,null,0.99086956521739122,0.96945652173913044,0.94804347826086954,0.90326086956521734,0.85760869565217401,0.83608695652173914,0.81456521739130427,0.85,0.86,0.87,0.89,0.99,0.995,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.160304347826086,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.007186956521741},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.846360869565217},14.470239130434782,15.28258695652174,14.974317391304348,14.662173913043477]
[null,57,17.432608695652171,17.432608695652171,17.117608695652173,17.117608695652173,16.802608695652175,16.802608695652175,{"$f":"U11*$I$13","v":16.133478260869566},16.133478260869566,15.425217391304349,15.425217391304349,15.043695652173914,15.043695652173914,14.662173913043477,14.662173913043477,null,0.96847826086956512,0.95097826086956516,0.9334782608695652,0.89630434782608692,0.85695652173913051,0.83576086956521745,0.81456521739130427,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.432608695652171,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.117608695652173},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.802608695652175},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.133478260869566},15.425217391304349,15.043695652173914,14.662173913043477]
[1600,72,21.654782608695655,10.827391304347827,21.187173913043477,10.699522826086955,20.719565217391306,10.566978260869567,{"$f":"U12*$I$13","v":19.729565217391308},10.259373913043481,18.676956521739132,9.8987869565217412,18.111521739130435,9.6896641304347835,17.546086956521741,9.4748869565217415,null,1.2030434782608697,1.1770652173913043,1.1510869565217392,1.0960869565217393,1.037608695652174,1.006195652173913,0.97478260869565225,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.827391304347827},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.699522826086955},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.566978260869567},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.259373913043481},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8987869565217412},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.6896641304347835},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.4748869565217415}]
[null,67,19.807826086956521,13.469321739130436,19.369565217391301,13.364999999999997,18.931304347826089,13.251913043478261,18,12.78,17.025652173913045,12.428726086956523,16.503260869565217,12.294929347826086,15.980869565217391,12.145460869565218,null,1.1004347826086955,1.076086956521739,1.0517391304347827,1,0.94586956521739129,0.91684782608695647,0.88782608695652177,0.68,0.69,0.7,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.469321739130436},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.364999999999997},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.251913043478261},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.78},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.428726086956523},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.294929347826086},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.145460869565218}]
[null,62,18.22695652173913,16.221991304347824,17.841521739130435,16.77103043478261,17.456086956521737,17.281526086956521,{"$f":"U14*$I$13","v":16.724347826086955},16.724347826086955,15.97304347826087,15.97304347826087,15.568043478260869,15.568043478260869,15.163043478260869,15.163043478260869,null,1.0126086956521738,0.99119565217391303,0.96978260869565214,0.92913043478260871,0.88739130434782609,0.86489130434782602,0.84239130434782605,0.89,0.94,0.99,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.221991304347824,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.77103043478261},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.281526086956521},16.724347826086955,15.97304347826087,15.568043478260869,15.163043478260869]
[null,57,18.105652173913047,18.105652173913047,17.771086956521742,17.771086956521742,17.436521739130434,17.436521739130434,16.728260869565219,16.728260869565219,15.97304347826087,15.97304347826087,15.568043478260869,15.568043478260869,15.163043478260869,15.163043478260869,null,1.0058695652173915,0.98728260869565232,0.96869565217391307,0.92934782608695654,0.88739130434782609,0.86489130434782602,0.84239130434782605,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.105652173913047,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.771086956521742},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.436521739130434},16.728260869565219,15.97304347826087,15.568043478260869,15.163043478260869]
[1800,72,21.897391304347828,11.38664347826087,21.41804347826087,11.137382608695653,20.938695652173912,10.888121739130435,19.917391304347824,10.556217391304347,18.841304347826089,10.362717391304349,18.260217391304348,10.134420652173914,17.679130434782607,9.9003130434782616,null,1.2165217391304348,1.1898913043478261,1.1632608695652173,1.1065217391304347,1.0467391304347826,1.0144565217391304,0.98217391304347823,0.52,0.52,0.52,0.53,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.38664347826087},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.137382608695653},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.888121739130435},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.556217391304347},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.362717391304349},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.134420652173914},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.9003130434782616}]
[null,67,20.03869565217391,14.227473913043475,19.588695652173914,14.103860869565217,19.138695652173912,13.971247826086955,18.187826086956523,13.640869565217393,17.189999999999998,13.236299999999998,16.65586956521739,13.074857608695652,16.121739130434783,12.897391304347828,null,1.1132608695652173,1.0882608695652174,1.0632608695652173,1.0104347826086957,0.95499999999999996,0.92532608695652174,0.89565217391304353,0.71,0.72,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.227473913043475},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.103860869565217},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.971247826086955},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.640869565217393},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.236299999999998},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.074857608695652},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.897391304347828}]
[null,62,18.649565217391302,18.649565217391302,18.299347826086958,18.299347826086958,17.94913043478261,17.94913043478261,17.205652173913045,17.205652173913045,16.411304347826086,16.411304347826086,15.986739130434785,15.986739130434785,15.56217391304348,15.56217391304348,null,1.036086956521739,1.0166304347826087,0.99717391304347824,0.9558695652173913,0.91173913043478261,0.88815217391304357,0.86456521739130443,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.649565217391302,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.299347826086958},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.94913043478261},17.205652173913045,16.411304347826086,15.986739130434785,15.56217391304348]
[null,57,18.653478260869566,18.653478260869566,18.303260869565221,18.303260869565221,17.95304347826087,17.95304347826087,17.205652173913045,17.205652173913045,16.415217391304349,16.415217391304349,15.988695652173911,15.988695652173911,15.56217391304348,15.56217391304348,null,1.0363043478260869,1.0168478260869567,0.99739130434782619,0.9558695652173913,0.91195652173913044,0.88826086956521733,0.86456521739130443,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.653478260869566,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.303260869565221},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.95304347826087},17.205652173913045,16.415217391304349,15.988695652173911,15.56217391304348]

{"sheet":"(C,H,T)4A3_60","index":9,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11]]}
[]
["(C,H,T)4A3_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.224210526315787},{"$f":"IF(AM8>C8,C8,AM8)","v":10.824347368421051},{"$f":"S8*$I$13","v":20.769473684210528},{"$f":"IF(AN8>E8,E8,AN8)","v":10.59243157894737},{"$f":"T8*$I$13","v":20.314736842105262},{"$f":"IF(AO8>G8,G8,AO8)","v":10.360515789473684},{"$f":"U8*$I$13","v":19.342105263157894},{"$f":"IF(AP8>I8,I8,AP8)","v":10.057894736842105},{"$f":"V8*$I$13","v":18.312631578947371},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7056947368421067},{"$f":"W8*$I$13","v":17.763157894736842},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5032894736842106},{"$f":"X8*$I$13","v":17.213684210526317},{"$f":"IF(AS8>O8,O8,AS8)","v":9.295389473684212},null,1.1791228070175437,1.153859649122807,1.1285964912280702,1.0745614035087718,1.0173684210526317,0.98684210526315785,0.95631578947368423,0.51,0.51,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.824347368421051},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.59243157894737},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.360515789473684},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.057894736842105},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7056947368421067},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5032894736842106},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.295389473684212}]
[null,67,19.509473684210526,13.26644210526316,19.087894736842106,{"$f":"IF(AN9>E9,E9,AN9)","v":13.075207894736844},18.666315789473686,{"$f":"IF(AO9>G9,G9,AO9)","v":12.879757894736843},{"$f":"U9*$I$13","v":17.766315789473683},{"$f":"IF(AP9>I9,I9,AP9)","v":12.614084210526315},16.822105263157898,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.280136842105264},16.321578947368423,{"$f":"IF(AR9>M9,M9,AR9)","v":12.077968421052633},15.821052631578949,{"$f":"IF(AS9>O9,O9,AS9)","v":11.865789473684211},null,1.083859649122807,1.0604385964912282,1.0370175438596492,0.98701754385964913,0.93456140350877204,0.90675438596491231,0.8789473684210527,0.68,0.68500000000000005,0.69,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.26644210526316},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.075207894736844},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.879757894736843},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.614084210526315},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.280136842105264},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.077968421052633},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.865789473684211}]
[null,62,17.952631578947368,15.798315789473685,17.572105263157894,15.639173684210526,17.19157894736842,15.472421052631578,{"$f":"U10*$I$13","v":16.386315789473684},15.075410526315791,15.562105263157896,14.628378947368422,15.161052631578949,14.70622105263158,14.760000000000002,14.760000000000002,null,0.99736842105263157,0.97622807017543856,0.95508771929824554,0.91035087719298247,0.86456140350877198,0.84228070175438607,0.82000000000000006,0.88,0.89,0.9,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.798315789473685,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.639173684210526},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.472421052631578},15.075410526315791,14.628378947368422,14.70622105263158,14.760000000000002]
[null,57,17.529473684210526,17.529473684210526,17.216842105263158,17.216842105263158,16.90421052631579,16.90421052631579,{"$f":"U11*$I$13","v":16.234736842105264},16.234736842105264,15.527368421052632,15.527368421052632,15.143684210526315,15.143684210526315,14.760000000000002,14.760000000000002,null,0.97385964912280698,0.95649122807017539,0.93912280701754391,0.90192982456140347,0.86263157894736842,0.84131578947368413,0.82000000000000006,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.529473684210526,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.216842105263158},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.90421052631579},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.234736842105264},15.527368421052632,15.143684210526315,14.760000000000002]
[2000,72,21.543157894736844,11.20244210526316,21.066315789473688,11.059815789473687,20.589473684210525,10.912421052631579,{"$f":"U12*$I$13","v":19.582105263157896},10.574336842105264,18.51157894736842,10.181368421052632,17.943157894736842,9.9584526315789486,17.374736842105264,9.7298526315789484,null,1.1968421052631579,1.1703508771929827,1.143859649122807,1.0878947368421052,1.0284210526315789,0.99684210526315786,0.96526315789473693,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.20244210526316},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.059815789473687},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.912421052631579},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.574336842105264},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.181368421052632},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9584526315789486},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7298526315789484}]
[null,67,19.812631578947368,14.06696842105263,19.373684210526317,13.949052631578947,18.934736842105263,13.822357894736841,18,13.5,17.021052631578947,13.10621052631579,16.503157894736841,12.872463157894737,15.985263157894735,12.628357894736842,null,1.100701754385965,1.0763157894736843,1.0519298245614035,1,0.94561403508771924,0.9168421052631579,0.88807017543859645,0.71,0.72,0.73,0.75,0.77,0.78,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.06696842105263},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.949052631578947},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.822357894736841},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.10621052631579},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.872463157894737},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.628357894736842}]
[null,62,18.322105263157898,16.856336842105268,17.936842105263157,16.681263157894733,17.551578947368419,16.498484210526314,{"$f":"U14*$I$13","v":16.796842105263156},16.796842105263156,16.038947368421052,16.038947368421052,15.628421052631577,15.628421052631577,15.217894736842103,15.217894736842103,null,1.0178947368421054,0.99649122807017543,0.97508771929824556,0.93315789473684208,0.89105263157894732,0.8682456140350876,0.84543859649122799,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.856336842105268,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.681263157894733},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.498484210526314},16.796842105263156,16.038947368421052,15.628421052631577,15.217894736842103]
[null,57,18.18,18.18,17.846842105263157,17.846842105263157,17.513684210526314,17.513684210526314,16.8,16.8,16.042105263157893,16.042105263157893,15.629999999999999,15.629999999999999,15.217894736842103,15.217894736842103,null,1.01,0.99149122807017542,0.97298245614035084,0.93333333333333335,0.89122807017543859,0.86833333333333329,0.84543859649122799,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.18,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.846842105263157},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.513684210526314},16.8,16.042105263157893,15.629999999999999,15.217894736842103]
[2250,72,21.767368421052637,11.754378947368425,21.274736842105266,11.594731578947371,20.782105263157895,11.430157894736844,19.746315789473687,11.057936842105265,18.644210526315792,10.6272,18.059999999999999,10.474799999999998,17.475789473684213,10.310715789473685,null,1.2092982456140353,1.1819298245614036,1.1545614035087719,1.0970175438596492,1.0357894736842106,1.0033333333333332,0.97087719298245623,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.754378947368425},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.594731578947371},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.430157894736844},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.057936842105265},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.6272},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.474799999999998},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.310715789473685}]
[null,67,20.030526315789473,14.822589473684209,19.577368421052633,14.683026315789474,19.124210526315789,14.5344,18.167368421052632,14.170547368421055,17.16,13.899600000000001,16.63105263157895,13.637463157894739,16.102105263157895,13.364747368421053,null,1.1128070175438596,1.0876315789473685,1.0624561403508772,1.0092982456140351,0.95333333333333337,0.92394736842105274,0.894561403508772,0.74,0.75,0.76,0.78,0.81,0.82000000000000006,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.822589473684209},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.683026315789474},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.5344},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.170547368421055},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.899600000000001},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.637463157894739},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.364747368421053}]
[null,62,18.710526315789473,18.710526315789473,18.356842105263155,18.356842105263155,18.003157894736841,18.003157894736841,17.248421052631578,17.248421052631578,16.455789473684209,16.455789473684209,16.021578947368422,16.021578947368422,15.587368421052631,15.587368421052631,null,1.0394736842105263,1.0198245614035086,1.0001754385964912,0.95824561403508768,0.91421052631578947,0.89008771929824559,0.86596491228070172,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.710526315789473,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.356842105263155},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.003157894736841},17.248421052631578,16.455789473684209,16.021578947368422,15.587368421052631]
[null,57,18.710526315789473,18.710526315789473,18.356842105263155,18.356842105263155,18.003157894736841,18.003157894736841,17.248421052631578,17.248421052631578,16.45894736842105,16.45894736842105,16.02315789473684,16.02315789473684,15.587368421052631,15.587368421052631,null,1.0394736842105263,1.0198245614035086,1.0001754385964912,0.95824561403508768,0.91438596491228064,0.89017543859649118,0.86596491228070172,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.710526315789473,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.356842105263155},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.003157894736841},17.248421052631578,16.45894736842105,16.02315789473684,15.587368421052631]

{"sheet":"(C,H,T)4A4_18","index":10,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.57},{"$f":"IF(AM8>C8,C8,AM8)","v":11.2164},{"$f":"S8*$I$13","v":21.045000000000002},{"$f":"IF(AN8>E8,E8,AN8)","v":11.048625000000001},{"$f":"T8*$I$13","v":20.52},{"$f":"IF(AO8>G8,G8,AO8)","v":10.8756},{"$f":"U8*$I$13","v":19.45},{"$f":"IF(AP8>I8,I8,AP8)","v":10.3085},{"$f":"V8*$I$13","v":18.329999999999998},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.8981999999999992},{"$f":"W8*$I$13","v":17.754999999999999},{"$f":"IF(AR8>M8,M8,AR8)","v":9.76525},{"$f":"X8*$I$13","v":17.18},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6208000000000009},null,1.1983333333333333,1.1691666666666667,1.1399999999999999,1.0805555555555555,1.0183333333333333,0.98638888888888887,0.95444444444444443,0.52,0.52500000000000002,0.53,0.53,0.54,0.55000000000000004,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.2164},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.048625000000001},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.8756},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.3085},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.8981999999999992},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.76525},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6208000000000009}]
[null,67,19.600000000000001,13.72,19.125,{"$f":"IF(AN9>E9,E9,AN9)","v":13.483124999999999},18.649999999999999,{"$f":"IF(AO9>G9,G9,AO9)","v":13.241499999999998},{"$f":"U9*$I$13","v":17.670000000000002},{"$f":"IF(AP9>I9,I9,AP9)","v":12.899100000000001},16.649999999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.320999999999998},16.125,{"$f":"IF(AR9>M9,M9,AR9)","v":12.174375},15.600000000000001,{"$f":"IF(AS9>O9,O9,AS9)","v":12.012000000000002},null,1.088888888888889,1.0625,1.036111111111111,0.9816666666666668,0.92499999999999993,0.89583333333333337,0.8666666666666667,0.7,0.70499999999999996,0.71,0.73,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.72},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.483124999999999},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.241499999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.899100000000001},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.320999999999998},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.174375},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.012000000000002}]
[null,62,17.82,16.038,17.39,15.824900000000001,16.96,15.603200000000001,{"$f":"U10*$I$13","v":16.079999999999998},15.275999999999998,15.18,14.724599999999999,14.734999999999999,14.513974999999999,14.29,14.29,null,0.99,0.96611111111111114,0.94222222222222229,0.8933333333333332,0.84333333333333327,0.81861111111111107,0.79388888888888887,0.9,0.91,0.92,0.95,0.97,0.98499999999999999,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.038,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.824900000000001},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.603200000000001},15.275999999999998,14.724599999999999,14.513974999999999,14.29]
[null,57,17.16,17.16,16.824999999999999,16.824999999999999,16.489999999999998,16.489999999999998,{"$f":"U11*$I$13","v":15.79},15.79,15.06,15.06,14.675000000000001,14.675000000000001,14.29,14.29,null,0.95333333333333337,0.93472222222222223,0.91611111111111099,0.87722222222222213,0.83666666666666667,0.81527777777777777,0.79388888888888887,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.16,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.824999999999999},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.489999999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.79},15.06,14.675000000000001,14.29]
[600,72,22.010000000000005,11.665300000000004,21.465000000000003,11.483775000000003,20.92,11.296800000000001,{"$f":"U12*$I$13","v":19.79},10.884500000000001,18.62,10.427200000000001,18.020000000000003,10.271400000000003,17.420000000000002,10.1036,null,1.222777777777778,1.1925000000000001,1.1622222222222223,1.0994444444444444,1.0344444444444445,1.0011111111111113,0.96777777777777785,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.57000000000000006,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.665300000000004},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.483775000000003},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.296800000000001},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.884500000000001},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.427200000000001},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.271400000000003},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.1036}]
[null,67,20.03,14.6219,19.53,14.35455,19.03,14.0822,18,13.68,16.940000000000001,13.213200000000002,16.39,13.030050000000001,15.84,12.830400000000001,null,1.1127777777777779,1.085,1.0572222222222223,1,0.94111111111111123,0.91055555555555556,0.88,0.73,0.73499999999999999,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.6219},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.35455},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.0822},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.68},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.213200000000002},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.030050000000001},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.830400000000001}]
[null,62,18.27,17.3565,17.824999999999999,17.111999999999998,17.38,16.858599999999999,{"$f":"U14*$I$13","v":16.5},16.335000000000001,15.7,15.7,15.279999999999998,15.279999999999998,14.86,14.86,null,1.0149999999999999,0.9902777777777777,0.9655555555555555,0.91666666666666663,0.87222222222222223,0.8488888888888888,0.82555555555555549,0.95,0.96,0.97,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.3565,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.111999999999998},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.858599999999999},16.335000000000001,15.7,15.279999999999998,14.86]
[null,57,17.96,17.96,17.594999999999999,17.594999999999999,17.23,17.23,16.48,16.48,15.7,15.7,15.285,15.285,14.869999999999997,14.869999999999997,null,0.99777777777777787,0.97749999999999992,0.9572222222222222,0.91555555555555557,0.87222222222222223,0.84916666666666663,0.82611111111111102,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.96,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.594999999999999},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.23},16.48,15.7,15.285,14.869999999999997]
[675,72,22.34,12.287000000000001,21.769999999999996,12.082349999999998,21.2,11.872,20.03,11.4171,18.829999999999998,11.109699999999998,18.204999999999998,10.831974999999998,17.579999999999998,10.547999999999998,null,1.2411111111111111,1.2094444444444443,1.1777777777777778,1.1127777777777779,1.046111111111111,1.0113888888888889,0.97666666666666657,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.59,0.59499999999999997,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.287000000000001},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.082349999999998},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.872},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.4171},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.109699999999998},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.831974999999998},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.547999999999998}]
[null,67,20.350000000000001,15.466000000000001,19.829999999999998,15.2691,19.309999999999995,15.061799999999996,18.25,14.600000000000001,17.149999999999999,14.062999999999999,16.585000000000001,13.848475000000001,16.02,13.616999999999999,null,1.1305555555555555,1.1016666666666666,1.0727777777777776,1.0138888888888888,0.95277777777777772,0.92138888888888892,0.89,0.76,0.77,0.78,0.8,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.466000000000001},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.2691},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.061799999999996},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.600000000000001},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.062999999999999},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.848475000000001},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.616999999999999}]
[null,62,18.68,18.493199999999998,18.27,18.178650000000001,17.86,17.86,17.059999999999999,17.059999999999999,16.22,16.22,15.774999999999999,15.774999999999999,15.33,15.33,null,1.0377777777777777,1.0149999999999999,0.99222222222222223,0.94777777777777772,0.90111111111111108,0.87638888888888877,0.85166666666666668,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.493199999999998,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.178650000000001},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.86},17.059999999999999,16.22,15.774999999999999,15.33]
[null,57,18.63,18.63,18.244999999999997,18.244999999999997,17.86,17.86,17.059999999999999,17.059999999999999,16.22,16.22,15.774999999999999,15.774999999999999,15.33,15.33,null,1.0349999999999999,1.013611111111111,0.99222222222222223,0.94777777777777772,0.90111111111111108,0.87638888888888877,0.85166666666666668,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.63,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.244999999999997},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.86},17.059999999999999,16.22,15.774999999999999,15.33]

{"sheet":"(C,H,T)4A4_24","index":11,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.468103448275862},{"$f":"IF(AM8>C8,C8,AM8)","v":10.734051724137931},{"$f":"S8*$I$13","v":20.99094827586207},{"$f":"IF(AN8>E8,E8,AN8)","v":10.495474137931035},{"$f":"T8*$I$13","v":20.513793103448275},{"$f":"IF(AO8>G8,G8,AO8)","v":10.256896551724138},{"$f":"U8*$I$13","v":19.520689655172415},{"$f":"IF(AP8>I8,I8,AP8)","v":9.9555517241379317},{"$f":"V8*$I$13","v":18.465517241379313},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.602068965517244},{"$f":"W8*$I$13","v":17.899137931034485},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3970474137931053},{"$f":"X8*$I$13","v":17.332758620689656},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1863620689655185},null,1.1926724137931035,1.1661637931034483,1.1396551724137931,1.0844827586206898,1.0258620689655173,0.99439655172413799,0.96293103448275863,0.5,0.5,0.5,0.51,0.52,0.52500000000000002,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.734051724137931},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.495474137931035},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.256896551724138},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.9555517241379317},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.602068965517244},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3970474137931053},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1863620689655185}]
[null,67,19.489655172413798,13.058068965517245,19.047413793103452,{"$f":"IF(AN9>E9,E9,AN9)","v":12.857004310344831},18.605172413793106,{"$f":"IF(AO9>G9,G9,AO9)","v":12.651517241379313},{"$f":"U9*$I$13","v":17.689655172413794},{"$f":"IF(AP9>I9,I9,AP9)","v":12.205862068965518},16.71206896551724,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.865568965517239},16.188362068965517,{"$f":"IF(AR9>M9,M9,AR9)","v":11.655620689655173},15.664655172413793,{"$f":"IF(AS9>O9,O9,AS9)","v":11.435198275862069},null,1.0827586206896553,1.0581896551724139,1.0336206896551725,0.98275862068965525,0.92844827586206891,0.89935344827586217,0.8702586206896552,0.67,0.67500000000000004,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.058068965517245},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.857004310344831},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.651517241379313},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.205862068965518},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.865568965517239},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.655620689655173},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.435198275862069}]
[null,62,17.751724137931035,15.26648275862069,17.35603448275862,15.099749999999998,16.960344827586205,14.925103448275861,{"$f":"U10*$I$13","v":16.130172413793105},14.678456896551726,15.276724137931037,14.207353448275866,14.85387931034483,14.333993534482762,14.431034482758623,14.431034482758623,null,0.98620689655172411,0.96422413793103445,0.9422413793103448,0.89612068965517244,0.84870689655172427,0.82521551724137943,0.80172413793103459,0.86,0.87,0.88,0.91,0.93,0.96500000000000008,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.26648275862069,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.099749999999998},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.925103448275861},14.678456896551726,14.207353448275866,14.333993534482762,14.431034482758623]
[null,57,17.231896551724141,17.231896551724141,16.913793103448278,16.913793103448278,16.595689655172414,16.595689655172414,{"$f":"U11*$I$13","v":15.92844827586207},15.92844827586207,15.206896551724141,15.206896551724141,14.818965517241381,14.818965517241381,14.431034482758623,14.431034482758623,null,0.95732758620689662,0.93965517241379315,0.92198275862068968,0.88491379310344831,0.84482758620689669,0.82327586206896564,0.80172413793103459,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.231896551724141,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.913793103448278},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.595689655172414},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.92844827586207},15.206896551724141,14.818965517241381,14.431034482758623]
[800,72,21.887068965517241,11.162405172413793,21.39051724137931,11.016116379310345,20.893965517241377,10.864862068965516,{"$f":"U12*$I$13","v":19.846551724137932},10.518672413793105,18.752586206896556,10.126396551724142,18.16293103448276,9.8987974137931047,17.573275862068964,9.6653017241379313,null,1.215948275862069,1.1883620689655172,1.1607758620689654,1.1025862068965517,1.0418103448275864,1.0090517241379311,0.9762931034482758,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.162405172413793},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.016116379310345},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.864862068965516},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.518672413793105},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.126396551724142},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8987974137931047},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6653017241379313}]
[null,67,19.877586206896556,13.914310344827589,19.415948275862068,13.688243534482757,18.954310344827586,13.457560344827586,18,13.14,16.991379310344826,12.743534482758619,16.448275862068968,12.58293103448276,15.905172413793105,12.406034482758622,null,1.1043103448275864,1.0786637931034482,1.0530172413793104,1,0.94396551724137923,0.91379310344827591,0.88362068965517249,0.7,0.70499999999999996,0.71,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.914310344827589},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.688243534482757},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.457560344827586},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.743534482758619},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.58293103448276},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.406034482758622}]
[null,62,18.186206896551727,16.549448275862073,17.782758620689659,16.360137931034487,17.379310344827584,16.162758620689655,{"$f":"U14*$I$13","v":16.572413793103447},16.572413793103447,15.819827586206898,15.819827586206898,15.404741379310346,15.404741379310346,14.989655172413794,14.989655172413794,null,1.010344827586207,0.98793103448275876,0.96551724137931028,0.92068965517241375,0.87887931034482769,0.85581896551724146,0.83275862068965523,0.91,0.92,0.93,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.549448275862073,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.360137931034487},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.162758620689655},16.572413793103447,15.819827586206898,15.404741379310346,14.989655172413794]
[null,57,17.976724137931036,17.976724137931036,17.639224137931034,17.639224137931034,17.301724137931036,17.301724137931036,16.580172413793104,16.580172413793104,15.819827586206898,15.819827586206898,15.404741379310346,15.404741379310346,14.989655172413794,14.989655172413794,null,0.99870689655172429,0.97995689655172413,0.9612068965517242,0.92112068965517246,0.87887931034482769,0.85581896551724146,0.83275862068965523,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.976724137931036,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.639224137931034},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.301724137931036},16.580172413793104,15.819827586206898,15.404741379310346,14.989655172413794]
[900,72,22.197413793103447,11.764629310344828,21.681465517241381,11.59958405172414,21.165517241379312,11.42937931034483,20.087068965517243,11.047887931034484,18.954310344827586,10.614413793103449,18.349137931034484,10.367262931034482,17.743965517241381,10.114060344827587,null,1.2331896551724137,1.2045258620689656,1.1758620689655173,1.1159482758620691,1.0530172413793104,1.0193965517241379,0.98577586206896561,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.764629310344828},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.59958405172414},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.42937931034483},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.047887931034484},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.614413793103449},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.367262931034482},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.114060344827587}]
[null,67,20.164655172413795,14.720198275862071,19.695258620689653,14.476015086206894,19.225862068965519,14.227137931034484,18.232758620689655,13.856896551724137,17.193103448275863,13.582551724137932,16.638362068965517,13.393881465517239,16.083620689655174,13.188568965517241,null,1.1202586206896552,1.0941810344827585,1.0681034482758622,1.0129310344827587,0.95517241379310347,0.92435344827586208,0.89353448275862069,0.73,0.73499999999999999,0.74,0.76,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.720198275862071},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.476015086206894},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.227137931034484},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.856896551724137},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.582551724137932},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.393881465517239},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.188568965517241}]
[null,62,18.605172413793106,18.605172413793106,18.244396551724137,18.244396551724137,17.883620689655174,17.883620689655174,17.123275862068965,17.123275862068965,16.316379310344828,16.316379310344828,15.878017241379311,15.878017241379311,15.439655172413792,15.439655172413792,null,1.0336206896551725,1.0135775862068965,0.99353448275862077,0.95129310344827589,0.90646551724137936,0.8821120689655173,0.85775862068965514,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.605172413793106,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.244396551724137},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.883620689655174},17.123275862068965,16.316379310344828,15.878017241379311,15.439655172413792]
[null,57,18.605172413793106,18.605172413793106,18.244396551724137,18.244396551724137,17.883620689655174,17.883620689655174,17.123275862068965,17.123275862068965,16.316379310344828,16.316379310344828,15.878017241379311,15.878017241379311,15.439655172413792,15.439655172413792,null,1.0336206896551725,1.0135775862068965,0.99353448275862077,0.95129310344827589,0.90646551724137936,0.8821120689655173,0.85775862068965514,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.605172413793106,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.244396551724137},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.883620689655174},17.123275862068965,16.316379310344828,15.878017241379311,15.439655172413792]

{"sheet":"(C,H,T)4A4_30","index":12,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":21.302068965517243},{"$f":"IF(AM8>C8,C8,AM8)","v":10.651034482758622},{"$f":"S8*$I$13","v":20.839655172413796},{"$f":"IF(AN8>E8,E8,AN8)","v":10.524025862068967},{"$f":"T8*$I$13","v":20.377241379310345},{"$f":"IF(AO8>G8,G8,AO8)","v":10.392393103448276},{"$f":"U8*$I$13","v":19.390344827586205},{"$f":"IF(AP8>I8,I8,AP8)","v":10.082979310344827},{"$f":"V8*$I$13","v":18.366206896551724},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7340896551724132},{"$f":"W8*$I$13","v":17.810689655172414},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5287189655172426},{"$f":"X8*$I$13","v":17.255172413793105},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3177931034482775},null,1.183448275862069,1.1577586206896553,1.1320689655172413,1.0772413793103448,1.0203448275862068,0.98948275862068968,0.95862068965517244,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.651034482758622},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.524025862068967},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.392393103448276},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.082979310344827},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7340896551724132},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5287189655172426},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3177931034482775}]
[null,67,19.520689655172411,13.078862068965517,19.089310344827584,{"$f":"IF(AN9>E9,E9,AN9)","v":12.980731034482757},18.657931034482758,{"$f":"IF(AO9>G9,G9,AO9)","v":12.873972413793101},{"$f":"U9*$I$13","v":17.745517241379311},{"$f":"IF(AP9>I9,I9,AP9)","v":12.421862068965517},16.783448275862071,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.08408275862069},16.268275862068965,{"$f":"IF(AR9>M9,M9,AR9)","v":11.875841379310344},15.753103448275862,{"$f":"IF(AS9>O9,O9,AS9)","v":11.657296551724137},null,1.0844827586206895,1.0605172413793102,1.036551724137931,0.9858620689655172,0.9324137931034483,0.9037931034482759,0.8751724137931034,0.67,0.67999999999999994,0.69,0.7,0.72,0.73,0.74,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.078862068965517},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.980731034482757},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.873972413793101},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.421862068965517},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.08408275862069},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.875841379310344},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.657296551724137}]
[null,62,17.888275862068966,15.562799999999999,17.497241379310342,15.397572413793101,17.106206896551722,15.224524137931033,{"$f":"U10*$I$13","v":16.286896551724137},14.821075862068966,15.430344827586207,14.504524137931034,14.99896551724138,14.548996551724139,14.56758620689655,14.56758620689655,null,0.99379310344827587,0.97206896551724131,0.95034482758620686,0.90482758620689652,0.85724137931034483,0.83327586206896553,0.80931034482758613,0.87,0.88,0.89,0.91,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.562799999999999,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.397572413793101},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.224524137931033},14.821075862068966,14.504524137931034,14.548996551724139,14.56758620689655]
[null,57,17.379310344827587,17.379310344827587,17.062758620689657,17.062758620689657,16.746206896551726,16.746206896551726,{"$f":"U11*$I$13","v":16.069655172413793},16.069655172413793,15.355862068965516,15.355862068965516,14.964827586206896,14.964827586206896,14.573793103448276,14.573793103448276,null,0.96551724137931039,0.94793103448275873,0.93034482758620696,0.89275862068965517,0.85310344827586204,0.83137931034482759,0.80965517241379314,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.379310344827587,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.062758620689657},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.746206896551726},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.069655172413793},15.355862068965516,14.964827586206896,14.573793103448276]
[1000,72,21.649655172413794,11.257820689655173,21.165517241379312,11.006068965517242,20.681379310344827,10.75431724137931,{"$f":"U12*$I$13","v":19.651034482758622},10.41504827586207,18.595862068965516,10.04176551724138,18.021724137931038,9.9119482758620716,17.447586206896553,9.7706482758620705,null,1.2027586206896552,1.1758620689655173,1.1489655172413793,1.0917241379310345,1.0331034482758621,1.0012068965517242,0.96931034482758616,0.52,0.52,0.52,0.53,0.54,0.55000000000000004,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.257820689655173},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.006068965517242},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.75431724137931},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.41504827586207},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.04176551724138},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9119482758620716},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7706482758620705}]
[null,67,19.849655172413794,13.894758620689656,19.399655172413794,13.773755172413793,18.949655172413795,13.643751724137932,18,13.14,17.006896551724139,12.755172413793105,16.476206896551727,12.604298275862071,15.945517241379312,12.437503448275864,null,1.1027586206896551,1.0777586206896552,1.0527586206896553,1,0.94482758620689655,0.91534482758620694,0.88586206896551734,0.7,0.71,0.72,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.894758620689656},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.773755172413793},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.643751724137932},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.755172413793105},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.604298275862071},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.437503448275864}]
[null,62,18.273103448275862,16.628524137931034,17.875862068965517,16.445793103448278,17.478620689655173,16.255117241379313,{"$f":"U14*$I$13","v":16.640689655172412},16.640689655172412,15.902068965517241,15.902068965517241,15.486206896551726,15.486206896551726,15.070344827586206,15.070344827586206,null,1.0151724137931035,0.99310344827586206,0.9710344827586207,0.92448275862068963,0.88344827586206898,0.86034482758620701,0.83724137931034481,0.91,0.92,0.93,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.628524137931034,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.445793103448278},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.255117241379313},16.640689655172412,15.902068965517241,15.486206896551726,15.070344827586206]
[null,57,18.062068965517245,18.062068965517245,17.723793103448276,17.723793103448276,17.385517241379311,17.385517241379311,16.665517241379312,16.665517241379312,15.902068965517241,15.902068965517241,15.486206896551726,15.486206896551726,15.070344827586206,15.070344827586206,null,1.0034482758620691,0.98465517241379308,0.9658620689655173,0.92586206896551726,0.88344827586206898,0.86034482758620701,0.83724137931034481,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.062068965517245,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.723793103448276},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.385517241379311},16.665517241379312,15.902068965517241,15.486206896551726,15.070344827586206]
[1125,72,21.891724137931039,11.602613793103451,21.395172413793102,11.44641724137931,20.898620689655175,11.285255172413795,19.837241379310342,10.910482758620688,18.757241379310344,10.504055172413793,18.167586206896551,10.355524137931036,17.577931034482759,10.1952,null,1.2162068965517243,1.1886206896551723,1.1610344827586208,1.1020689655172413,1.0420689655172413,1.0093103448275862,0.97655172413793101,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.57000000000000006,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.602613793103451},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.44641724137931},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.285255172413795},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.910482758620688},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.504055172413793},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.355524137931036},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.1952}]
[null,67,20.085517241379311,14.662427586206896,19.623103448275863,14.521096551724138,19.160689655172416,14.370517241379311,18.18,13.9986,17.168275862068967,13.562937931034485,16.625172413793102,13.383263793103445,16.082068965517241,13.187296551724137,null,1.1158620689655172,1.0901724137931035,1.0644827586206898,1.01,0.95379310344827584,0.92362068965517241,0.89344827586206899,0.73,0.74,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.662427586206896},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.521096551724138},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.370517241379311},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.9986},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.562937931034485},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.383263793103445},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.187296551724137}]
[null,62,18.633103448275865,17.70144827586207,18.266896551724138,17.810224137931034,17.900689655172414,17.900689655172414,17.14344827586207,17.14344827586207,16.336551724137934,16.336551724137934,15.902068965517241,15.902068965517241,15.467586206896552,15.467586206896552,null,1.0351724137931035,1.0148275862068965,0.99448275862068969,0.95241379310344831,0.90758620689655178,0.88344827586206898,0.85931034482758628,0.95,0.97499999999999998,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.70144827586207,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.810224137931034},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.900689655172414},17.14344827586207,16.336551724137934,15.902068965517241,15.467586206896552]
[null,57,18.614482758620689,18.614482758620689,18.257586206896548,18.257586206896548,17.900689655172414,17.900689655172414,17.14344827586207,17.14344827586207,16.336551724137934,16.336551724137934,15.902068965517241,15.902068965517241,15.467586206896552,15.467586206896552,null,1.0341379310344827,1.0143103448275861,0.99448275862068969,0.95241379310344831,0.90758620689655178,0.88344827586206898,0.85931034482758628,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.614482758620689,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.257586206896548},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.900689655172414},17.14344827586207,16.336551724137934,15.902068965517241,15.467586206896552]

{"sheet":"(C,H,T)4A4_36","index":13,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.534636871508383},{"$f":"IF(AM8>C8,C8,AM8)","v":11.198011173184359},{"$f":"S8*$I$13","v":21.05446927374302},{"$f":"IF(AN8>E8,E8,AN8)","v":11.053596368715086},{"$f":"T8*$I$13","v":20.574301675977654},{"$f":"IF(AO8>G8,G8,AO8)","v":10.904379888268158},{"$f":"U8*$I$13","v":19.568715083798885},{"$f":"IF(AP8>I8,I8,AP8)","v":10.567106145251399},{"$f":"V8*$I$13","v":18.492737430167601},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.171005586592182},{"$f":"W8*$I$13","v":17.912011173184357},{"$f":"IF(AR8>M8,M8,AR8)","v":9.9411662011173192},{"$f":"X8*$I$13","v":17.331284916201117},{"$f":"IF(AS8>O8,O8,AS8)","v":9.7055195530726266},null,1.1963687150837989,1.1696927374301678,1.1430167597765364,1.0871508379888271,1.0273743016759778,0.99511173184357549,0.96284916201117321,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.198011173184359},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.053596368715086},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.904379888268158},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.567106145251399},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.171005586592182},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.9411662011173192},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.7055195530726266}]
[null,67,19.523463687150837,13.666424581005586,19.07849162011173,{"$f":"IF(AN9>E9,E9,AN9)","v":13.545729050279329},18.633519553072627,{"$f":"IF(AO9>G9,G9,AO9)","v":13.416134078212291},{"$f":"U9*$I$13","v":17.698324022346373},{"$f":"IF(AP9>I9,I9,AP9)","v":12.919776536312852},16.702793296089386,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.52709497206704},16.164804469273744,{"$f":"IF(AR9>M9,M9,AR9)","v":12.285251396648045},15.626815642458102,{"$f":"IF(AS9>O9,O9,AS9)","v":12.032648044692738},null,1.0846368715083798,1.0599162011173184,1.035195530726257,0.98324022346368734,0.9279329608938548,0.89804469273743015,0.86815642458100561,0.7,0.71,0.72,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.666424581005586},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.545729050279329},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.416134078212291},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.919776536312852},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.52709497206704},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.285251396648045},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.032648044692738}]
[null,62,17.768715083798885,16.169530726256987,17.36648044692738,15.97716201117319,16.964245810055868,15.776748603351958,{"$f":"U10*$I$13","v":16.124581005586595},15.318351955307264,15.244692737430169,14.939798882681565,14.807262569832403,14.659189944134079,14.369832402234636,14.369832402234636,null,0.98715083798882697,0.9648044692737433,0.94245810055865931,0.89581005586592188,0.84692737430167608,0.82262569832402244,0.79832402234636868,0.91,0.92,0.93,0.95,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.169530726256987,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.97716201117319},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.776748603351958},15.318351955307264,14.939798882681565,14.659189944134079,14.369832402234636]
[null,57,17.225698324022346,17.225698324022346,16.903910614525142,16.903910614525142,16.582122905027934,16.582122905027934,{"$f":"U11*$I$13","v":15.903351955307263},15.903351955307263,15.169273743016761,15.169273743016761,14.769553072625699,14.769553072625699,14.369832402234636,14.369832402234636,null,0.9569832402234637,0.93910614525139668,0.92122905027932955,0.88351955307262575,0.84273743016759783,0.82053072625698331,0.79832402234636868,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.225698324022346,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.903910614525142},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.582122905027934},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.903351955307263},15.169273743016761,14.769553072625699,14.369832402234636]
[1200,72,21.951955307262569,11.854055865921788,21.451675977653629,11.691163407821229,20.951396648044692,11.523268156424582,{"$f":"U12*$I$13","v":19.900558659217879},10.945307262569834,18.784357541899443,10.707083798882682,18.181005586592178,10.454078212290502,17.577653631284917,10.195039106145252,null,1.2195530726256982,1.1917597765363128,1.1639664804469274,1.1055865921787711,1.0435754189944135,1.0100558659217878,0.97653631284916209,0.54,0.54500000000000004,0.55000000000000004,0.55000000000000004,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.854055865921788},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.691163407821229},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.523268156424582},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.945307262569834},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.707083798882682},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.454078212290502},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.195039106145252}]
[null,67,19.900558659217879,14.527407821229051,19.437988826815641,14.384111731843573,18.97541899441341,14.231564245810057,18,13.86,16.96927374301676,13.405726256983241,16.416201117318437,13.21504189944134,15.863128491620113,13.007765363128492,null,1.1055865921787711,1.0798882681564246,1.0541899441340783,1,0.94273743016759781,0.91201117318435754,0.88128491620111737,0.73,0.74,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.527407821229051},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.384111731843573},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.231564245810057},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.405726256983241},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.21504189944134},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.007765363128492}]
[null,62,18.191061452513971,17.281508379888272,17.78379888268157,17.072446927374305,17.376536312849165,16.855240223463689,{"$f":"U14*$I$13","v":16.5268156424581},16.5268156424581,15.762569832402237,15.762569832402237,15.340223463687153,15.340223463687153,14.91787709497207,14.91787709497207,null,1.010614525139665,0.98798882681564271,0.9653631284916202,0.91815642458100555,0.87569832402234649,0.85223463687150847,0.82877094972067056,0.95,0.96,0.97,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.281508379888272,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.072446927374305},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.855240223463689},16.5268156424581,15.762569832402237,15.340223463687153,14.91787709497207]
[null,57,17.959776536312848,17.959776536312848,17.617877094972069,17.617877094972069,17.275977653631287,17.275977653631287,16.546927374301678,16.546927374301678,15.76759776536313,15.76759776536313,15.342737430167599,15.342737430167599,14.91787709497207,14.91787709497207,null,0.99776536312849162,0.97877094972067047,0.9597765363128492,0.91927374301675979,0.87597765363128499,0.85237430167597772,0.82877094972067056,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.959776536312848,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.617877094972069},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.275977653631287},16.546927374301678,15.76759776536313,15.342737430167599,14.91787709497207]
[1350,72,22.258659217877099,12.242262569832405,21.743296089385478,12.067529329608941,21.22793296089386,11.887642458100563,20.141899441340783,11.480882681564246,18.990502793296091,11.014491620111732,18.372067039106149,10.839519553072627,17.753631284916203,10.652178770949721,null,1.23659217877095,1.2079608938547488,1.1793296089385477,1.1189944134078214,1.055027932960894,1.0206703910614527,0.98631284916201134,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.242262569832405},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.067529329608941},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.887642458100563},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.480882681564246},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.014491620111732},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.839519553072627},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.652178770949721}]
[null,67,20.182122905027931,15.338413407821228,19.704469273743015,15.172441340782122,19.226815642458103,14.996916201117321,18.226256983240226,14.581005586592182,17.170391061452513,14.07972067039106,16.602234636871508,13.945877094972065,16.034078212290503,13.789307262569832,null,1.1212290502793296,1.0946927374301676,1.0681564245810058,1.0125698324022347,0.9539106145251397,0.9223463687150838,0.89078212290502801,0.76,0.77,0.78,0.8,0.82,0.84,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.338413407821228},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.172441340782122},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.996916201117321},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.581005586592182},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.07972067039106},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.945877094972065},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.789307262569832}]
[null,62,18.588268156424579,18.402385474860335,18.216201117318441,18.125120111731849,17.844134078212292,17.844134078212292,17.079888268156424,17.079888268156424,16.255307262569833,16.255307262569833,15.810335195530728,15.810335195530728,15.365363128491619,15.365363128491619,null,1.03268156424581,1.0120111731843577,0.99134078212290522,0.94888268156424582,0.90307262569832403,0.87835195530726262,0.85363128491620111,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.402385474860335,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.125120111731849},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.844134078212292},17.079888268156424,16.255307262569833,15.810335195530728,15.365363128491619]
[null,57,18.573184357541901,18.573184357541901,18.211173184357541,18.211173184357541,17.849162011173185,17.849162011173185,17.079888268156424,17.079888268156424,16.260335195530729,16.260335195530729,15.812849162011176,15.812849162011176,15.365363128491619,15.365363128491619,null,1.0318435754189945,1.011731843575419,0.99162011173184361,0.94888268156424582,0.90335195530726276,0.87849162011173199,0.85363128491620111,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.573184357541901,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.211173184357541},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.849162011173185},17.079888268156424,16.260335195530729,15.812849162011176,15.365363128491619]

{"sheet":"(C,H,T)4A4_42","index":14,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.306666666666665},{"$f":"IF(AM8>C8,C8,AM8)","v":11.079466666666667},{"$f":"S8*$I$13","v":20.851111111111113},{"$f":"IF(AN8>E8,E8,AN8)","v":10.946833333333334},{"$f":"T8*$I$13","v":20.395555555555553},{"$f":"IF(AO8>G8,G8,AO8)","v":10.809644444444444},{"$f":"U8*$I$13","v":19.41333333333333},{"$f":"IF(AP8>I8,I8,AP8)","v":10.483199999999998},{"$f":"V8*$I$13","v":18.355555555555554},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.095555555555556},{"$f":"W8*$I$13","v":17.784444444444446},{"$f":"IF(AR8>M8,M8,AR8)","v":9.8703666666666692},{"$f":"X8*$I$13","v":17.213333333333331},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6394666666666655},null,1.1837037037037037,1.1583950617283951,1.1330864197530863,1.0785185185185184,1.019753086419753,0.98802469135802473,0.9562962962962962,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.079466666666667},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.946833333333334},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.809644444444444},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.483199999999998},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.095555555555556},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.8703666666666692},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6394666666666655}]
[null,67,19.484444444444446,13.639111111111111,19.064444444444447,{"$f":"IF(AN9>E9,E9,AN9)","v":13.535755555555557},18.644444444444446,{"$f":"IF(AO9>G9,G9,AO9)","v":13.424000000000001},{"$f":"U9*$I$13","v":17.737777777777776},{"$f":"IF(AP9>I9,I9,AP9)","v":12.948577777777777},16.755555555555556,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.566666666666666},16.22666666666667,{"$f":"IF(AR9>M9,M9,AR9)","v":12.413400000000003},15.697777777777777,{"$f":"IF(AS9>O9,O9,AS9)","v":12.244266666666666},null,1.0824691358024692,1.059135802469136,1.0358024691358025,0.98543209876543203,0.93086419753086425,0.90148148148148166,0.87209876543209874,0.7,0.71,0.72,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.639111111111111},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.535755555555557},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.424000000000001},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.948577777777777},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.566666666666666},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.413400000000003},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.244266666666666}]
[null,62,17.826666666666668,16.22226666666667,17.446666666666665,16.050933333333333,17.066666666666666,15.872,{"$f":"U10*$I$13","v":16.248888888888889},15.598933333333333,15.382222222222223,15.074577777777778,14.959999999999999,14.8104,14.537777777777778,14.537777777777778,null,0.99037037037037035,0.96925925925925915,0.94814814814814807,0.9027160493827161,0.85456790123456794,0.83111111111111102,0.80765432098765433,0.91,0.92,0.93,0.96,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.22226666666667,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.050933333333333},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.872},15.598933333333333,15.074577777777778,14.8104,14.537777777777778]
[null,57,17.342222222222222,17.342222222222222,17.035555555555554,17.035555555555554,16.728888888888889,16.728888888888889,{"$f":"U11*$I$13","v":16.062222222222225},16.062222222222225,15.333333333333334,15.333333333333334,14.935555555555558,14.935555555555558,14.537777777777778,14.537777777777778,null,0.96345679012345686,0.94641975308641968,0.92938271604938272,0.89234567901234574,0.85185185185185186,0.82975308641975321,0.80765432098765433,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.342222222222222,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.035555555555554},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.728888888888889},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.062222222222225},15.333333333333334,14.935555555555558,14.537777777777778]
[1400,72,21.657777777777774,11.695199999999998,21.184444444444445,11.545522222222223,20.711111111111109,11.39111111111111,{"$f":"U12*$I$13","v":19.688888888888886},11.025777777777778,18.591111111111111,10.596933333333332,18.002222222222223,10.351277777777778,17.413333333333334,10.099733333333333,null,1.2032098765432098,1.1769135802469135,1.1506172839506172,1.093827160493827,1.0328395061728395,1.0001234567901234,0.96740740740740738,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.695199999999998},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.545522222222223},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.39111111111111},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":11.025777777777778},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.596933333333332},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.351277777777778},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.099733333333333}]
[null,67,19.826666666666668,14.671733333333334,19.38666666666667,14.443066666666668,18.946666666666669,14.21,18,13.86,16.986666666666668,13.419466666666668,16.442222222222224,13.235988888888889,15.89777777777778,13.036177777777779,null,1.1014814814814815,1.0770370370370372,1.0525925925925927,1,0.94370370370370371,0.91345679012345693,0.88320987654320993,0.74,0.745,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.671733333333334},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.443066666666668},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.21},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.419466666666668},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.235988888888889},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.036177777777779}]
[null,62,18.226666666666667,17.497599999999998,17.84,17.3048,17.453333333333337,17.104266666666671,{"$f":"U14*$I$13","v":16.675555555555558},16.675555555555558,15.89777777777778,15.89777777777778,15.475555555555555,15.475555555555555,15.053333333333331,15.053333333333331,null,1.0125925925925925,0.99111111111111116,0.96962962962962973,0.92641975308641988,0.88320987654320993,0.85975308641975312,0.8362962962962962,0.96,0.97,0.98,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.497599999999998,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.3048},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.104266666666671},16.675555555555558,15.89777777777778,15.475555555555555,15.053333333333331]
[null,57,18.048888888888889,18.048888888888889,17.720000000000002,17.720000000000002,17.391111111111112,17.391111111111112,16.675555555555558,16.675555555555558,15.902222222222223,15.902222222222223,15.47777777777778,15.47777777777778,15.053333333333331,15.053333333333331,null,1.0027160493827161,0.98444444444444457,0.96617283950617294,0.92641975308641988,0.88345679012345679,0.85987654320987661,0.8362962962962962,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.048888888888889,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.720000000000002},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.391111111111112},16.675555555555558,15.902222222222223,15.47777777777778,15.053333333333331]
[1575,72,21.915555555555557,12.272711111111112,21.426666666666666,12.106066666666665,20.937777777777779,11.934533333333333,19.88,11.530399999999998,18.755555555555556,11.065777777777777,18.148888888888891,10.889333333333335,17.542222222222222,10.700755555555554,null,1.2175308641975309,1.1903703703703703,1.16320987654321,1.1044444444444443,1.0419753086419754,1.0082716049382716,0.97456790123456782,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.57999999999999996,0.59,0.6,0.61,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.272711111111112},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.106066666666665},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.934533333333333},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.530399999999998},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.065777777777777},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.889333333333335},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.700755555555554}]
[null,67,20.066666666666663,15.451333333333331,19.615555555555556,15.300133333333335,19.164444444444442,15.139911111111109,18.191111111111113,14.734800000000002,17.151111111111113,14.235422222222223,16.595555555555556,14.023244444444444,16.040000000000003,13.794400000000001,null,1.1148148148148147,1.0897530864197531,1.0646913580246913,1.0106172839506173,0.95283950617283963,0.92197530864197541,0.89111111111111119,0.77,0.78,0.79,0.81,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.451333333333331},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.300133333333335},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.139911111111109},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.734800000000002},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.235422222222223},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":14.023244444444444},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.794400000000001}]
[null,62,18.604444444444443,18.604444444444443,18.262222222222224,18.262222222222224,17.919999999999998,17.919999999999998,17.164444444444445,17.164444444444445,16.346666666666668,16.346666666666668,15.900000000000004,15.900000000000004,15.453333333333335,15.453333333333335,null,1.0335802469135802,1.0145679012345681,0.99555555555555553,0.95358024691358023,0.90814814814814815,0.88333333333333353,0.85851851851851857,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.604444444444443,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.262222222222224},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.919999999999998},17.164444444444445,16.346666666666668,15.900000000000004,15.453333333333335]
[null,57,18.617777777777775,18.617777777777775,18.271111111111111,18.271111111111111,17.924444444444443,17.924444444444443,17.16888888888889,17.16888888888889,16.346666666666668,16.346666666666668,15.902222222222223,15.902222222222223,15.457777777777778,15.457777777777778,null,1.0343209876543209,1.0150617283950618,0.99580246913580239,0.95382716049382721,0.90814814814814815,0.88345679012345679,0.85876543209876544,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.617777777777775,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.271111111111111},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.924444444444443},17.16888888888889,16.346666666666668,15.902222222222223,15.457777777777778]

{"sheet":"(C,H,T)4A4_48","index":15,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.355051546391753},{"$f":"IF(AM8>C8,C8,AM8)","v":10.891076288659795},{"$f":"S8*$I$13","v":20.865154639175259},{"$f":"IF(AN8>E8,E8,AN8)","v":10.641228865979382},{"$f":"T8*$I$13","v":20.375257731958762},{"$f":"IF(AO8>G8,G8,AO8)","v":10.391381443298968},{"$f":"U8*$I$13","v":19.38061855670103},{"$f":"IF(AP8>I8,I8,AP8)","v":10.077921649484535},{"$f":"V8*$I$13","v":18.345154639175259},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7229319587628886},{"$f":"W8*$I$13","v":17.792164948453607},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5188082474226796},{"$f":"X8*$I$13","v":17.239175257731958},{"$f":"IF(AS8>O8,O8,AS8)","v":9.309154639175258},null,1.1863917525773195,1.1591752577319587,1.1319587628865979,1.0767010309278351,1.0191752577319588,0.98845360824742268,0.95773195876288664,0.51,0.51,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.891076288659795},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.641228865979382},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.391381443298968},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.077921649484535},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7229319587628886},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5188082474226796},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.309154639175258}]
[null,67,19.521649484536081,13.274721649484535,19.07443298969072,{"$f":"IF(AN9>E9,E9,AN9)","v":13.065986597938144},18.627216494845364,{"$f":"IF(AO9>G9,G9,AO9)","v":12.8527793814433},{"$f":"U9*$I$13","v":17.714226804123712},{"$f":"IF(AP9>I9,I9,AP9)","v":12.399958762886598},16.76041237113402,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.067496907216494},16.250103092783505,{"$f":"IF(AR9>M9,M9,AR9)","v":11.862575257731958},15.739793814432989,{"$f":"IF(AS9>O9,O9,AS9)","v":11.647447422680411},null,1.0845360824742267,1.0596907216494844,1.0348453608247423,0.98412371134020615,0.93113402061855666,0.90278350515463912,0.87443298969072158,0.68,0.68500000000000005,0.69,0.7,0.72,0.73,0.74,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.274721649484535},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.065986597938144},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.8527793814433},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.399958762886598},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.067496907216494},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.862575257731958},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.647447422680411}]
[null,62,17.866391752577318,15.543760824742266,17.461855670103091,15.36643298969072,17.057319587628868,15.181014432989693,{"$f":"U10*$I$13","v":16.237113402061855},14.938144329896907,15.383505154639177,14.460494845360826,14.938144329896907,14.49,14.492783505154637,14.492783505154637,null,0.99257731958762885,0.97010309278350515,0.94762886597938145,0.90206185567010311,0.85463917525773203,0.82989690721649489,0.80515463917525765,0.87,0.88,0.89,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.543760824742266,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.36643298969072},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.181014432989693},14.938144329896907,14.460494845360826,14.49,14.492783505154637]
[null,57,17.268865979381445,17.268865979381445,16.947835051546392,16.947835051546392,16.626804123711338,16.626804123711338,{"$f":"U11*$I$13","v":15.96618556701031},15.96618556701031,15.261030927835051,15.261030927835051,14.88061855670103,14.88061855670103,14.500206185567011,14.500206185567011,null,0.95938144329896913,0.94154639175257726,0.9237113402061855,0.88701030927835056,0.84783505154639172,0.82670103092783498,0.80556701030927835,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.268865979381445,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.947835051546392},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.626804123711338},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.96618556701031},15.261030927835051,14.88061855670103,14.500206185567011]
[1600,72,21.752164948453608,11.311125773195876,21.238144329896908,11.150025773195877,20.724123711340209,10.983785567010312,{"$f":"U12*$I$13","v":19.681237113402062},10.627868041237114,18.604948453608248,10.232721649484537,18.033402061855675,10.008538144329901,17.461855670103091,9.778639175257732,null,1.2084536082474227,1.1798969072164949,1.1513402061855671,1.0934020618556701,1.0336082474226804,1.001855670103093,0.97010309278350515,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.311125773195876},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.150025773195877},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.983785567010312},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.627868041237114},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.232721649484537},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.008538144329901},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.778639175257732}]
[null,67,19.89278350515464,14.123876288659794,19.423298969072164,13.887658762886597,18.953814432989688,13.646746391752576,18,13.32,17.009072164948453,12.926894845360824,16.4820618556701,12.691187628865977,15.955051546391752,12.444940206185567,null,1.1051546391752578,1.0790721649484536,1.0529896907216494,1,0.94494845360824742,0.91567010309278341,0.88639175257731961,0.71,0.71499999999999997,0.72,0.74,0.76,0.77,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.123876288659794},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.887658762886597},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.646746391752576},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.926894845360824},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.691187628865977},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.444940206185567}]
[null,62,18.270927835051545,16.80925360824742,17.855257731958762,16.605389690721648,17.439587628865979,16.39321237113402,{"$f":"U14*$I$13","v":16.611958762886598},16.445839175257731,15.84,15.84,15.433608247422681,15.433608247422681,15.02721649484536,15.02721649484536,null,1.0150515463917524,0.9919587628865979,0.96886597938144337,0.92288659793814432,0.88,0.85742268041237113,0.83484536082474226,0.92,0.92999999999999994,0.94,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.80925360824742,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.605389690721648},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.39321237113402},16.445839175257731,15.84,15.433608247422681,15.02721649484536]
[null,57,18,18,17.654845360824744,17.654845360824744,17.309690721649485,17.309690721649485,16.59340206185567,16.59340206185567,15.84,15.84,15.433608247422681,15.433608247422681,15.02721649484536,15.02721649484536,null,1,0.98082474226804128,0.96164948453608246,0.92185567010309277,0.88,0.85742268041237113,0.83484536082474226,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.654845360824744},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.309690721649485},16.59340206185567,15.84,15.433608247422681,15.02721649484536]
[1800,72,22.041649484536084,11.902490721649485,21.510927835051547,11.723455670103094,20.98020618556701,11.539113402061856,19.900206185567008,11.144115463917526,18.790515463917526,10.710593814432988,18.202268041237115,10.466304123711341,17.614020618556701,10.216131958762887,null,1.2245360824742269,1.1950515463917526,1.1655670103092783,1.1055670103092783,1.0439175257731959,1.0112371134020619,0.97855670103092784,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.902490721649485},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.723455670103094},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.539113402061856},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.144115463917526},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.710593814432988},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.466304123711341},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.216131958762887}]
[null,67,20.167422680412372,14.923892783505154,19.679381443298972,14.661139175257734,19.191340206185568,14.393505154639175,18.211546391752577,14.022890721649485,17.190927835051546,13.752742268041239,16.650927835051544,13.570506185567007,16.110927835051545,13.372070103092781,null,1.1204123711340206,1.0932989690721651,1.0661855670103093,1.0117525773195877,0.9550515463917526,0.92505154639175247,0.89505154639175255,0.74,0.745,0.75,0.77,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.923892783505154},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.661139175257734},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.393505154639175},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.022890721649485},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.752742268041239},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.570506185567007},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.372070103092781}]
[null,62,18.638350515463916,18.451967010309275,18.252371134020621,18.161109278350516,17.866391752577318,17.866391752577318,17.109278350515464,17.109278350515464,16.311340206185569,16.311340206185569,15.882680412371135,15.882680412371135,15.454020618556701,15.454020618556701,null,1.0354639175257732,1.0140206185567011,0.99257731958762885,0.95051546391752584,0.90618556701030939,0.88237113402061862,0.85855670103092785,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.451967010309275,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.161109278350516},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.866391752577318},17.109278350515464,16.311340206185569,15.882680412371135,15.454020618556701]
[null,57,18.60123711340206,18.60123711340206,18.233814432989689,18.233814432989689,17.866391752577318,17.866391752577318,17.109278350515464,17.109278350515464,16.311340206185569,16.311340206185569,15.882680412371135,15.882680412371135,15.454020618556701,15.454020618556701,null,1.0334020618556701,1.0129896907216493,0.99257731958762885,0.95051546391752584,0.90618556701030939,0.88237113402061862,0.85855670103092785,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.60123711340206,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.233814432989689},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.866391752577318},17.109278350515464,16.311340206185569,15.882680412371135,15.454020618556701]

{"sheet":"(C,H,T)4A4_49","index":16,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_49"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.799565217391308},{"$f":"IF(AM8>C8,C8,AM8)","v":10.899782608695654},{"$f":"S8*$I$13","v":21.251739130434785},{"$f":"IF(AN8>E8,E8,AN8)","v":10.732128260869567},{"$f":"T8*$I$13","v":20.703913043478263},{"$f":"IF(AO8>G8,G8,AO8)","v":10.558995652173914},{"$f":"U8*$I$13","v":19.569130434782611},{"$f":"IF(AP8>I8,I8,AP8)","v":10.175947826086958},{"$f":"V8*$I$13","v":18.39130434782609},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7473913043478273},{"$f":"W8*$I$13","v":17.774999999999999},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5096249999999998},{"$f":"X8*$I$13","v":17.158695652173911},{"$f":"IF(AS8>O8,O8,AS8)","v":9.2656956521739122},null,1.2110869565217393,1.1806521739130436,1.1502173913043479,1.0871739130434783,1.0217391304347827,0.98749999999999993,0.95326086956521738,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.899782608695654},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.732128260869567},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.558995652173914},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.175947826086958},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7473913043478273},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5096249999999998},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.2656956521739122}]
[null,67,19.753043478260871,13.432069565217393,19.260000000000002,{"$f":"IF(AN9>E9,E9,AN9)","v":13.289400000000001},18.766956521739129,{"$f":"IF(AO9>G9,G9,AO9)","v":13.13686956521739},{"$f":"U9*$I$13","v":17.753478260869564},{"$f":"IF(AP9>I9,I9,AP9)","v":12.60496956521739},16.696956521739132,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.188778260869567},16.14521739130435,{"$f":"IF(AR9>M9,M9,AR9)","v":12.02818695652174},15.593478260869567,{"$f":"IF(AS9>O9,O9,AS9)","v":11.851043478260872},null,1.0973913043478261,1.07,1.0426086956521738,0.98630434782608689,0.92760869565217396,0.89695652173913054,0.86630434782608701,0.68,0.69,0.7,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.432069565217393},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.289400000000001},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.13686956521739},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.60496956521739},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.188778260869567},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.02818695652174},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.851043478260872}]
[null,62,17.972608695652173,15.815895652173912,17.546086956521741,15.703747826086959,17.119565217391305,15.578804347826088,{"$f":"U10*$I$13","v":16.258695652173913},16.096108695652173,15.460434782608694,15.460434782608694,15.045652173913046,15.045652173913046,14.63086956521739,14.63086956521739,null,0.99847826086956526,0.97478260869565225,0.95108695652173914,0.90326086956521734,0.85891304347826081,0.83586956521739142,0.8128260869565217,0.88,0.89500000000000002,0.91,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.815895652173912,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.703747826086959},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.578804347826088},16.096108695652173,15.460434782608694,15.045652173913046,14.63086956521739]
[null,57,17.628260869565217,17.628260869565217,17.281956521739129,17.281956521739129,16.935652173913041,16.935652173913041,{"$f":"U11*$I$13","v":16.211739130434783},16.211739130434783,15.436956521739132,15.436956521739132,15.024130434782611,15.024130434782611,14.611304347826087,14.611304347826087,null,0.97934782608695647,0.96010869565217394,0.94086956521739129,0.90065217391304342,0.85760869565217401,0.83467391304347838,0.81173913043478263,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.628260869565217,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.281956521739129},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.935652173913041},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.211739130434783},15.436956521739132,15.024130434782611,14.611304347826087]
[1600,72,22.171304347826084,11.529078260869564,21.592173913043478,11.335891304347827,21.013043478260869,11.136913043478261,{"$f":"U12*$I$13","v":19.827391304347827},10.706791304347828,18.602608695652172,10.231434782608696,17.96086956521739,10.058086956521739,17.319130434782608,9.8719043478260851,null,1.2317391304347824,1.1995652173913043,1.1673913043478261,1.1015217391304348,1.0334782608695652,0.99782608695652175,0.96217391304347821,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.529078260869564},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.335891304347827},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.136913043478261},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.706791304347828},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.231434782608696},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.058086956521739},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8719043478260851}]
[null,67,20.093478260869567,14.266369565217392,19.576956521739131,14.095408695652173,19.060434782608699,13.91411739130435,18,13.5,16.904347826086958,13.185391304347828,16.331086956521737,12.983214130434781,15.757826086956522,12.763839130434784,null,1.116304347826087,1.087608695652174,1.058913043478261,1,0.93913043478260871,0.90728260869565214,0.87543478260869567,0.71,0.72,0.73,0.75,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.266369565217392},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.095408695652173},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.91411739130435},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.185391304347828},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.983214130434781},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.763839130434784}]
[null,62,18.414782608695656,18.2306347826087,18.023478260869567,17.93336086956522,17.632173913043481,17.632173913043481,{"$f":"U14*$I$13","v":16.841739130434782},16.841739130434782,16.008260869565216,16.008260869565216,15.560217391304349,15.560217391304349,15.112173913043478,15.112173913043478,null,1.0230434782608697,1.001304347826087,0.97956521739130442,0.93565217391304345,0.88934782608695639,0.86445652173913046,0.8395652173913043,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.2306347826087,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.93336086956522},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.632173913043481},16.841739130434782,16.008260869565216,15.560217391304349,15.112173913043478]
[null,57,18.36,18.36,17.982391304347825,17.982391304347825,17.60478260869565,17.60478260869565,16.818260869565215,16.818260869565215,15.984782608695653,15.984782608695653,15.538695652173914,15.538695652173914,15.092608695652174,15.092608695652174,null,1.02,0.99902173913043479,0.97804347826086957,0.93434782608695643,0.8880434782608696,0.86326086956521741,0.83847826086956523,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.36,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.982391304347825},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.60478260869565},16.818260869565215,15.984782608695653,15.538695652173914,15.092608695652174]
[1800,72,22.433478260869563,12.114078260869565,21.834782608695651,11.899956521739131,21.236086956521739,11.679847826086958,20.007391304347827,11.204139130434784,18.735652173913046,10.679321739130435,18.078260869565216,10.485391304347825,17.420869565217394,10.278313043478262,null,1.2463043478260869,1.2130434782608694,1.1797826086956522,1.1115217391304348,1.0408695652173914,1.0043478260869565,0.96782608695652184,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.114078260869565},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.899956521739131},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.679847826086958},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.204139130434784},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.679321739130435},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.485391304347825},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.278313043478262}]
[null,67,20.34391304347826,15.257934782608695,19.807826086956524,15.053947826086958,19.271739130434781,14.839239130434782,18.18,14.3622,17.049130434782608,13.980286956521738,16.462173913043479,13.745915217391305,15.875217391304348,13.493934782608695,null,1.1302173913043478,1.1004347826086958,1.0706521739130435,1.01,0.94717391304347831,0.91456521739130436,0.88195652173913042,0.75,0.76,0.77,0.79,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.257934782608695},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.053947826086958},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.839239130434782},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.3622},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.980286956521738},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.745915217391305},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.493934782608695}]
[null,62,18.982173913043475,18.982173913043475,18.577173913043477,18.577173913043477,18.17217391304348,18.17217391304348,17.330869565217391,17.330869565217391,16.442608695652176,16.442608695652176,15.969130434782608,15.969130434782608,15.495652173913044,15.495652173913044,null,1.0545652173913043,1.0320652173913043,1.0095652173913043,0.96282608695652172,0.9134782608695653,0.88717391304347826,0.86086956521739133,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.982173913043475,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.577173913043477},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.17217391304348},17.330869565217391,16.442608695652176,15.969130434782608,15.495652173913044]
[null,57,18.958695652173915,18.958695652173915,18.553695652173914,18.553695652173914,18.148695652173917,18.148695652173917,17.311304347826088,17.311304347826088,16.423043478260869,16.423043478260869,15.949565217391303,15.949565217391303,15.476086956521739,15.476086956521739,null,1.0532608695652175,1.0307608695652175,1.0082608695652175,0.96173913043478265,0.91239130434782612,0.88608695652173908,0.85978260869565215,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.958695652173915,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.553695652173914},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.148695652173917},17.311304347826088,16.423043478260869,15.949565217391303,15.476086956521739]

{"sheet":"(C,H,T)4A4_60","index":17,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)4A4_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.413898305084746},{"$f":"IF(AM8>C8,C8,AM8)","v":10.921088135593221},{"$f":"S8*$I$13","v":20.925762711864408},{"$f":"IF(AN8>E8,E8,AN8)","v":10.776767796610171},{"$f":"T8*$I$13","v":20.437627118644066},{"$f":"IF(AO8>G8,G8,AO8)","v":10.627566101694915},{"$f":"U8*$I$13","v":19.403389830508477},{"$f":"IF(AP8>I8,I8,AP8)","v":10.283796610169492},{"$f":"V8*$I$13","v":18.295932203389832},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.87980338983051},{"$f":"W8*$I$13","v":17.691864406779658},{"$f":"IF(AR8>M8,M8,AR8)","v":9.6420661016949136},{"$f":"X8*$I$13","v":17.087796610169491},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3982881355932211},null,1.1896610169491526,1.162542372881356,1.1354237288135591,1.0779661016949154,1.0164406779661017,0.98288135593220327,0.94932203389830505,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.921088135593221},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.776767796610171},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.627566101694915},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.283796610169492},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.87980338983051},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.6420661016949136},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3982881355932211}]
[null,67,19.549830508474574,13.489383050847456,19.107457627118642,{"$f":"IF(AN9>E9,E9,AN9)","v":13.279683050847455},18.665084745762712,{"$f":"IF(AO9>G9,G9,AO9)","v":13.065559322033899},{"$f":"U9*$I$13","v":17.72542372881356},{"$f":"IF(AP9>I9,I9,AP9)","v":12.762305084745762},16.715593220338981,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.202383050847455},16.166440677966101,{"$f":"IF(AR9>M9,M9,AR9)","v":12.043998305084745},15.617288135593219,{"$f":"IF(AS9>O9,O9,AS9)","v":11.869138983050846},null,1.0861016949152542,1.0615254237288134,1.0369491525423729,0.98474576271186443,0.92864406779661013,0.89813559322033887,0.86762711864406772,0.69,0.69499999999999995,0.7,0.72,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.489383050847456},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.279683050847455},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.065559322033899},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.762305084745762},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.202383050847455},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.043998305084745},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.869138983050846}]
[null,62,17.884067796610168,15.916820338983049,17.487457627118644,15.738711864406779,17.09084745762712,15.55267118644068,{"$f":"U10*$I$13","v":16.257966101694915},15.119908474576272,15.373220338983051,14.758291525423729,14.914067796610171,14.615786440677967,14.454915254237289,14.454915254237289,null,0.9935593220338983,0.97152542372881356,0.94949152542372883,0.90322033898305087,0.85406779661016952,0.82855932203389837,0.80305084745762711,0.89,0.9,0.91,0.93,0.96,0.98,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.916820338983049,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.738711864406779},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.55267118644068},15.119908474576272,14.758291525423729,14.615786440677967,14.454915254237289]
[null,57,17.319661016949155,17.319661016949155,17.003898305084746,17.003898305084746,16.688135593220341,16.688135593220341,{"$f":"U11*$I$13","v":16.010847457627118},16.010847457627118,15.275593220338983,15.275593220338983,14.868305084745762,14.868305084745762,14.461016949152542,14.461016949152542,null,0.96220338983050857,0.9446610169491525,0.92711864406779665,0.88949152542372878,0.84864406779661017,0.82601694915254231,0.80338983050847457,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.319661016949155,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.003898305084746},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.688135593220341},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.010847457627118},15.275593220338983,14.868305084745762,14.461016949152542]
[2000,72,21.798305084745763,11.553101694915256,21.285762711864407,11.387883050847458,20.773220338983052,11.217538983050849,{"$f":"U12*$I$13","v":19.69322033898305},10.831271186440679,18.536949152542373,10.38069152542373,17.91,10.119149999999999,17.283050847457627,9.8513389830508462,null,1.2110169491525424,1.182542372881356,1.1540677966101696,1.0940677966101695,1.0298305084745762,0.995,0.96016949152542375,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.553101694915256},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.387883050847458},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.217538983050849},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.831271186440679},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.38069152542373},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.119149999999999},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8513389830508462}]
[null,67,19.915932203389833,14.339471186440679,19.449152542372882,14.100635593220339,18.982372881355932,13.857132203389829,18,13.5,16.950508474576271,13.051891525423729,16.381525423728814,12.859497457627119,15.812542372881355,12.650033898305084,null,1.1064406779661018,1.0805084745762712,1.0545762711864406,1,0.94169491525423732,0.91008474576271192,0.87847457627118641,0.72,0.72499999999999998,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.339471186440679},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.100635593220339},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.857132203389829},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.051891525423729},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.859497457627119},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.650033898305084}]
[null,62,18.283728813559321,17.003867796610169,17.876440677966102,16.803854237288135,17.469152542372882,16.595694915254239,{"$f":"U14*$I$13","v":16.630169491525422},16.463867796610167,15.818644067796612,15.818644067796612,15.380847457627118,15.380847457627118,14.943050847457625,14.943050847457625,null,1.0157627118644068,0.99313559322033895,0.97050847457627121,0.92389830508474569,0.87881355932203398,0.85449152542372875,0.83016949152542363,0.93,0.94,0.95,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.003867796610169,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.803854237288135},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.595694915254239},16.463867796610167,15.818644067796612,15.380847457627118,14.943050847457625]
[null,57,18.024406779661017,18.024406779661017,17.68271186440678,17.68271186440678,17.341016949152543,17.341016949152543,16.611864406779663,16.611864406779663,15.818644067796612,15.818644067796612,15.382372881355934,15.382372881355934,14.946101694915255,14.946101694915255,null,1.0013559322033898,0.98237288135593226,0.9633898305084746,0.92288135593220344,0.87881355932203398,0.85457627118644075,0.83033898305084752,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.024406779661017,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.68271186440678},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.341016949152543},16.611864406779663,15.818644067796612,15.382372881355934,14.946101694915255]
[2250,72,22.082033898305081,11.924298305084745,21.551186440677967,11.745396610169493,21.020338983050848,11.561186440677968,19.900677966101696,11.14437966101695,18.707796610169492,10.850522033898304,18.061016949152542,10.565694915254236,17.414237288135592,10.274399999999998,null,1.226779661016949,1.1972881355932203,1.1677966101694917,1.1055932203389831,1.0393220338983051,1.0033898305084745,0.96745762711864403,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.58499999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.924298305084745},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.745396610169493},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.561186440677968},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.14437966101695},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.850522033898304},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.565694915254236},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.274399999999998}]
[null,67,20.178305084745762,15.133728813559323,19.694745762711868,14.86953305084746,19.211186440677963,14.600501694915252,18.198305084745762,14.376661016949152,17.11830508474576,13.865827118644066,16.53406779661017,13.640605932203389,15.949830508474577,13.397857627118643,null,1.1210169491525424,1.0941525423728815,1.0672881355932202,1.0110169491525423,0.95101694915254231,0.91855932203389834,0.88610169491525426,0.75,0.755,0.76,0.79,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.133728813559323},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.86953305084746},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.600501694915252},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.376661016949152},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.865827118644066},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.640605932203389},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.397857627118643}]
[null,62,18.643728813559324,18.084416949152544,18.259322033898307,17.985432203389834,17.87491525423729,17.87491525423729,17.099999999999998,17.099999999999998,16.261016949152541,16.261016949152541,15.79728813559322,15.79728813559322,15.333559322033899,15.333559322033899,null,1.0357627118644068,1.014406779661017,0.99305084745762717,0.95,0.90338983050847455,0.87762711864406784,0.85186440677966102,0.97,0.98499999999999999,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.084416949152544,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.985432203389834},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.87491525423729},17.099999999999998,16.261016949152541,15.79728813559322,15.333559322033899]
[null,57,18.60406779661017,18.60406779661017,18.23949152542373,18.23949152542373,17.87491525423729,17.87491525423729,17.099999999999998,17.099999999999998,16.261016949152541,16.261016949152541,15.798813559322033,15.798813559322033,15.336610169491527,15.336610169491527,null,1.0335593220338983,1.0133050847457628,0.99305084745762717,0.95,0.90338983050847455,0.87771186440677962,0.8520338983050848,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.60406779661017,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.23949152542373},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.87491525423729},17.099999999999998,16.261016949152541,15.798813559322033,15.336610169491527]

{"sheet":"(C,H,T)XA6_18","index":18,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.41},{"$f":"IF(AM8>C8,C8,AM8)","v":10.2768},{"$f":"S8*$I$13","v":20.945},{"$f":"IF(AN8>E8,E8,AN8)","v":10.158325},{"$f":"T8*$I$13","v":20.48},{"$f":"IF(AO8>G8,G8,AO8)","v":10.0352},{"$f":"U8*$I$13","v":19.46},{"$f":"IF(AP8>I8,I8,AP8)","v":9.73},{"$f":"V8*$I$13","v":18.329999999999998},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3483000000000001},{"$f":"W8*$I$13","v":17.739999999999998},{"$f":"IF(AR8>M8,M8,AR8)","v":9.136099999999999},{"$f":"X8*$I$13","v":17.149999999999999},{"$f":"IF(AS8>O8,O8,AS8)","v":8.9179999999999993},null,1.1894444444444445,1.1636111111111112,1.1377777777777778,1.0811111111111111,1.0183333333333333,0.98555555555555552,0.95277777777777772,0.48,0.48499999999999999,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.2768},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.158325},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.0352},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.73},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3483000000000001},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.136099999999999},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.9179999999999993}]
[null,67,19.54,12.701000000000001,19.100000000000001,{"$f":"IF(AN9>E9,E9,AN9)","v":12.510500000000002},18.66,{"$f":"IF(AO9>G9,G9,AO9)","v":12.3156},{"$f":"U9*$I$13","v":17.690000000000001},{"$f":"IF(AP9>I9,I9,AP9)","v":11.852300000000001},16.649999999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.488499999999998},16.105,{"$f":"IF(AR9>M9,M9,AR9)","v":11.354025},15.56,{"$f":"IF(AS9>O9,O9,AS9)","v":11.203200000000001},null,1.0855555555555556,1.0611111111111111,1.0366666666666666,0.98277777777777786,0.92499999999999993,0.8947222222222222,0.86444444444444446,0.65,0.65500000000000003,0.66,0.67,0.69,0.70499999999999996,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.701000000000001},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.510500000000002},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.3156},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.852300000000001},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.488499999999998},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.354025},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.203200000000001}]
[null,62,17.82,14.9688,17.405000000000001,14.79425,16.989999999999998,14.611399999999998,{"$f":"U10*$I$13","v":16.12},14.185600000000001,15.2,13.831999999999999,14.77,14.105350000000001,14.34,14.34,null,0.99,0.9669444444444445,0.94388888888888878,0.89555555555555566,0.84444444444444444,0.82055555555555548,0.79666666666666663,0.84,0.85,0.86,0.88,0.91,0.95500000000000007,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,14.9688,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":14.79425},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.611399999999998},14.185600000000001,13.831999999999999,14.105350000000001,14.34]
[null,57,17.23,17.23,16.905000000000001,16.905000000000001,16.579999999999998,16.579999999999998,{"$f":"U11*$I$13","v":15.88},15.88,15.13,15.13,14.725000000000001,14.725000000000001,14.32,14.32,null,0.9572222222222222,0.93916666666666671,0.92111111111111099,0.88222222222222224,0.84055555555555561,0.81805555555555565,0.79555555555555557,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.23,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.905000000000001},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.579999999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.88},15.13,14.725000000000001,14.32]
[600,72,21.81,10.904999999999999,21.32,10.7666,20.83,10.623299999999999,{"$f":"U12*$I$13","v":19.78},10.087800000000001,18.61,9.8633000000000006,17.994999999999997,9.627324999999999,17.38,9.3851999999999993,null,1.2116666666666667,1.1844444444444444,1.1572222222222222,1.098888888888889,1.0338888888888889,0.99972222222222207,0.9655555555555555,0.5,0.505,0.51,0.51,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.904999999999999},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.7666},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.623299999999999},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.087800000000001},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8633000000000006},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.627324999999999},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.3851999999999993}]
[null,67,19.920000000000002,13.545600000000002,19.465000000000003,13.333525000000003,19.010000000000002,13.116899999999999,18,12.78,16.93,12.3589,16.36,12.1882,15.79,12.000399999999999,null,1.1066666666666667,1.0813888888888892,1.0561111111111112,1,0.94055555555555559,0.90888888888888886,0.87722222222222213,0.68,0.68500000000000005,0.69,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.545600000000002},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.333525000000003},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.116899999999999},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.78},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.3589},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.1882},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.000399999999999}]
[null,62,18.260000000000002,16.068800000000003,17.835000000000001,15.873150000000001,17.41,15.669,{"$f":"U14*$I$13","v":16.59},16.59,15.78,15.78,15.344999999999999,15.344999999999999,14.91,14.91,null,1.0144444444444445,0.99083333333333334,0.96722222222222221,0.92166666666666663,0.87666666666666659,0.85249999999999992,0.82833333333333337,0.88,0.89,0.9,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.068800000000003,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":15.873150000000001},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.669},16.59,15.78,15.344999999999999,14.91]
[null,57,18.02,18.02,17.664999999999999,17.664999999999999,17.309999999999999,17.309999999999999,16.559999999999999,16.559999999999999,15.75,15.75,15.315000000000001,15.315000000000001,14.879999999999999,14.879999999999999,null,1.0011111111111111,0.98138888888888887,0.96166666666666656,0.91999999999999993,0.875,0.85083333333333344,0.82666666666666666,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.02,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.664999999999999},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.309999999999999},16.559999999999999,15.75,15.315000000000001,14.879999999999999]
[675,72,22.09,11.486800000000001,21.585000000000001,11.224200000000002,21.08,10.961599999999999,20.010000000000002,10.605300000000002,18.8,10.340000000000002,18.164999999999999,10.081575000000001,17.53,9.8168000000000024,null,1.2272222222222222,1.1991666666666667,1.171111111111111,1.1116666666666668,1.0444444444444445,1.0091666666666665,0.97388888888888892,0.52,0.52,0.52,0.53,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.486800000000001},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.224200000000002},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.961599999999999},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.605300000000002},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.340000000000002},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.081575000000001},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.8168000000000024}]
[null,67,20.2,14.341999999999999,19.729999999999997,14.205599999999997,19.260000000000002,14.059800000000001,18.23,13.672499999999999,17.12,13.182400000000001,16.54,12.9839,15.96,12.768000000000001,null,1.1222222222222222,1.096111111111111,1.07,1.0127777777777778,0.95111111111111113,0.91888888888888887,0.88666666666666671,0.71,0.72,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.341999999999999},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.205599999999997},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.059800000000001},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.672499999999999},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.182400000000001},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.9839},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.768000000000001}]
[null,62,18.68,18.68,18.314999999999998,18.314999999999998,17.95,17.95,17.149999999999999,17.149999999999999,16.29,16.29,15.824999999999999,15.824999999999999,15.36,15.36,null,1.0377777777777777,1.0174999999999998,0.99722222222222223,0.95277777777777772,0.90499999999999992,0.87916666666666665,0.85333333333333328,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.68,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.314999999999998},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.95},17.149999999999999,16.29,15.824999999999999,15.36]
[null,57,18.66,18.66,18.29,18.29,17.920000000000002,17.920000000000002,17.12,17.12,16.260000000000002,16.260000000000002,15.8,15.8,15.34,15.34,null,1.0366666666666666,1.016111111111111,0.99555555555555564,0.95111111111111113,0.90333333333333343,0.87777777777777777,0.85222222222222221,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.66,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.29},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.920000000000002},17.12,16.260000000000002,15.8,15.34]

{"sheet":"(C,H,T)XA6_24","index":19,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.516101694915253},{"$f":"IF(AM8>C8,C8,AM8)","v":10.327728813559322},{"$f":"S8*$I$13","v":21.024152542372882},{"$f":"IF(AN8>E8,E8,AN8)","v":10.196713983050847},{"$f":"T8*$I$13","v":20.53220338983051},{"$f":"IF(AO8>G8,G8,AO8)","v":10.06077966101695},{"$f":"U8*$I$13","v":19.479661016949152},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7398305084745758},{"$f":"V8*$I$13","v":18.373728813559321},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3706016949152531},{"$f":"W8*$I$13","v":17.790254237288131},{"$f":"IF(AR8>M8,M8,AR8)","v":9.1619809322033881},{"$f":"X8*$I$13","v":17.206779661016949},{"$f":"IF(AS8>O8,O8,AS8)","v":8.9475254237288144},null,1.1953389830508474,1.1680084745762711,1.140677966101695,1.0822033898305083,1.0207627118644067,0.98834745762711851,0.95593220338983043,0.48,0.48499999999999999,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.327728813559322},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.196713983050847},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.06077966101695},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7398305084745758},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3706016949152531},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.1619809322033881},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.9475254237288144}]
[null,67,19.54830508474576,12.706398305084745,19.094491525423727,{"$f":"IF(AN9>E9,E9,AN9)","v":12.60236440677966},18.640677966101695,{"$f":"IF(AO9>G9,G9,AO9)","v":12.489254237288137},{"$f":"U9*$I$13","v":17.687288135593221},{"$f":"IF(AP9>I9,I9,AP9)","v":12.027355932203392},16.680508474576271,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.676355932203389},16.146610169491524,{"$f":"IF(AR9>M9,M9,AR9)","v":11.464093220338981},15.612711864406778,{"$f":"IF(AS9>O9,O9,AS9)","v":11.24115254237288},null,1.0860169491525422,1.0608050847457626,1.035593220338983,0.98262711864406782,0.92669491525423731,0.89703389830508473,0.86737288135593216,0.65,0.66,0.67,0.68,0.7,0.71,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.706398305084745},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.60236440677966},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.489254237288137},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.027355932203392},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.676355932203389},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.464093220338981},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.24115254237288}]
[null,62,17.786440677966102,15.118474576271186,17.378389830508475,14.945415254237288,16.970338983050848,14.764194915254237,{"$f":"U10*$I$13","v":16.123728813559321},14.350118644067797,15.254237288135592,15.254237288135592,14.853813559322033,14.853813559322033,14.453389830508474,14.453389830508474,null,0.98813559322033895,0.9654661016949152,0.94279661016949146,0.8957627118644067,0.84745762711864403,0.82521186440677963,0.80296610169491522,0.85,0.86,0.87,0.89,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.118474576271186,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":14.945415254237288},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.764194915254237},14.350118644067797,15.254237288135592,14.853813559322033,14.453389830508474]
[null,57,17.298305084745763,17.298305084745763,16.977966101694911,16.977966101694911,16.657627118644069,16.657627118644069,{"$f":"U11*$I$13","v":15.963559322033896},15.963559322033896,15.223728813559323,15.223728813559323,14.827118644067797,14.827118644067797,14.430508474576271,14.430508474576271,null,0.96101694915254232,0.94322033898305069,0.92542372881355928,0.88686440677966094,0.84576271186440677,0.82372881355932204,0.80169491525423731,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.298305084745763,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.977966101694911},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.657627118644069},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.963559322033896},15.223728813559323,14.827118644067797,14.430508474576271]
[800,72,21.905084745762711,10.952542372881355,21.394067796610166,10.804004237288133,20.883050847457625,10.650355932203389,{"$f":"U12*$I$13","v":19.792372881355931},10.292033898305084,18.640677966101695,9.8795593220338986,18.034322033898306,9.6483622881355942,17.427966101694913,9.4111016949152546,null,1.2169491525423728,1.1885593220338981,1.1601694915254237,1.0995762711864405,1.035593220338983,1.001906779661017,0.96822033898305082,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.952542372881355},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.804004237288133},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.650355932203389},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.292033898305084},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8795593220338986},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.6483622881355942},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.4111016949152546}]
[null,67,19.952542372881354,13.767254237288133,19.475847457627115,13.535713983050844,18.99915254237288,13.299406779661014,18,12.959999999999999,16.947457627118641,12.541118644067794,16.390677966101695,12.37496186440678,15.833898305084746,12.192101694915255,null,1.1084745762711863,1.0819915254237287,1.0555084745762711,1,0.94152542372881343,0.91059322033898304,0.87966101694915255,0.69,0.69499999999999995,0.7,0.72,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.767254237288133},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.535713983050844},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.299406779661014},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.959999999999999},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.541118644067794},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.37496186440678},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.192101694915255}]
[null,62,18.236440677966101,16.230432203389832,17.832203389830511,16.851432203389834,17.427966101694913,17.427966101694913,{"$f":"U14*$I$13","v":16.665254237288135},16.665254237288135,15.872033898305084,15.872033898305084,15.444915254237287,15.444915254237287,15.017796610169491,15.017796610169491,null,1.013135593220339,0.99067796610169501,0.96822033898305082,0.92584745762711862,0.88177966101694905,0.85805084745762705,0.83432203389830506,0.89,0.94500000000000006,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.230432203389832,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.851432203389834},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.427966101694913},16.665254237288135,15.872033898305084,15.444915254237287,15.017796610169491]
[null,57,18.076271186440678,18.076271186440678,17.72923728813559,17.72923728813559,17.382203389830508,17.382203389830508,16.642372881355932,16.642372881355932,15.849152542372881,15.849152542372881,15.422033898305083,15.422033898305083,14.994915254237286,14.994915254237286,null,1.0042372881355932,0.98495762711864387,0.96567796610169487,0.92457627118644059,0.88050847457627113,0.85677966101694902,0.83305084745762703,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.076271186440678,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.72923728813559},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.382203389830508},16.642372881355932,15.849152542372881,15.422033898305083,14.994915254237286]
[900,72,22.179661016949147,11.533423728813556,21.66101694915254,11.372033898305084,21.142372881355929,11.205457627118642,20.005932203389829,10.803203389830509,18.82372881355932,10.353050847457627,18.202118644067799,10.193186440677968,17.58050847457627,10.020889830508473,null,1.2322033898305083,1.2033898305084745,1.1745762711864405,1.1114406779661017,1.0457627118644066,1.0112288135593221,0.97669491525423724,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.533423728813556},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.372033898305084},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.205457627118642},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.803203389830509},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.353050847457627},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.193186440677968},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.020889830508473}]
[null,67,20.242372881355934,14.574508474576271,19.750423728813558,14.417809322033897,19.258474576271183,14.251271186440675,18.228813559322035,13.853898305084746,17.145762711864407,13.373694915254237,16.57372881355932,13.176114406779661,16.001694915254237,12.961372881355933,null,1.1245762711864407,1.0972457627118644,1.0699152542372881,1.0127118644067796,0.9525423728813559,0.92076271186440672,0.88898305084745755,0.72,0.73,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.574508474576271},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.417809322033897},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.251271186440675},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.853898305084746},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.373694915254237},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.176114406779661},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.961372881355933}]
[null,62,18.762711864406779,18.762711864406779,18.388983050847457,18.388983050847457,18.015254237288136,18.015254237288136,17.222033898305082,17.222033898305082,16.383050847457625,16.383050847457625,15.929237288135591,15.929237288135591,15.475423728813558,15.475423728813558,null,1.0423728813559321,1.0216101694915254,1.0008474576271187,0.956779661016949,0.9101694915254237,0.8849576271186439,0.85974576271186431,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.762711864406779,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.388983050847457},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.015254237288136},17.222033898305082,16.383050847457625,15.929237288135591,15.475423728813558]
[null,57,18.732203389830506,18.732203389830506,18.362288135593218,18.362288135593218,17.992372881355934,17.992372881355934,17.199152542372882,17.199152542372882,16.360169491525422,16.360169491525422,15.910169491525421,15.910169491525421,15.460169491525424,15.460169491525424,null,1.0406779661016947,1.0201271186440677,0.99957627118644066,0.95550847457627119,0.90889830508474567,0.88389830508474565,0.85889830508474574,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.732203389830506,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.362288135593218},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.992372881355934},17.199152542372882,16.360169491525422,15.910169491525421,15.460169491525424]

{"sheet":"(C,H,T)XA6_30","index":20,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":21.455244755244756},{"$f":"IF(AM8>C8,C8,AM8)","v":10.51306993006993},{"$f":"S8*$I$13","v":20.980069930069931},{"$f":"IF(AN8>E8,E8,AN8)","v":10.385134615384615},{"$f":"T8*$I$13","v":20.504895104895102},{"$f":"IF(AO8>G8,G8,AO8)","v":10.252447552447551},{"$f":"U8*$I$13","v":19.51048951048951},{"$f":"IF(AP8>I8,I8,AP8)","v":9.755244755244755},{"$f":"V8*$I$13","v":18.453146853146855},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.4111048951048968},{"$f":"W8*$I$13","v":17.883566433566433},{"$f":"IF(AR8>M8,M8,AR8)","v":9.2994545454545445},{"$f":"X8*$I$13","v":17.313986013986014},{"$f":"IF(AS8>O8,O8,AS8)","v":9.176412587412587},null,1.191958041958042,1.1655594405594405,1.139160839160839,1.083916083916084,1.0251748251748252,0.99353146853146845,0.96188811188811185,0.49,0.495,0.5,0.5,0.51,0.52,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.51306993006993},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.385134615384615},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.252447552447551},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.755244755244755},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.4111048951048968},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.2994545454545445},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.176412587412587}]
[null,67,19.504195804195803,12.872769230769231,19.06993006993007,{"$f":"IF(AN9>E9,E9,AN9)","v":12.776853146853147},18.635664335664334,{"$f":"IF(AO9>G9,G9,AO9)","v":12.672251748251748},{"$f":"U9*$I$13","v":17.723076923076921},{"$f":"IF(AP9>I9,I9,AP9)","v":12.228923076923074},16.747552447552447,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.890762237762237},16.22202797202797,{"$f":"IF(AR9>M9,M9,AR9)","v":11.679860139860137},15.696503496503496,{"$f":"IF(AS9>O9,O9,AS9)","v":11.458447552447552},null,1.0835664335664335,1.0594405594405594,1.0353146853146853,0.98461538461538456,0.93041958041958039,0.90122377622377614,0.872027972027972,0.66,0.67,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.872769230769231},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.776853146853147},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.672251748251748},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.228923076923074},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.890762237762237},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.679860139860137},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.458447552447552}]
[null,62,17.817482517482517,15.323034965034966,17.430419580419578,15.164465034965033,17.043356643356642,14.998153846153844,{"$f":"U10*$I$13","v":16.237762237762237},14.613986013986013,15.457342657342656,15.457342657342656,15.054545454545455,15.054545454545455,14.651748251748252,14.651748251748252,null,0.98986013986013976,0.96835664335664329,0.9468531468531467,0.90209790209790208,0.85874125874125862,0.83636363636363642,0.813986013986014,0.86,0.87,0.88,0.9,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.323034965034966,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.164465034965033},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.998153846153844},14.613986013986013,15.457342657342656,15.054545454545455,14.651748251748252]
[null,57,17.471328671328671,17.471328671328671,17.156643356643357,17.156643356643357,16.841958041958044,16.841958041958044,{"$f":"U11*$I$13","v":16.168531468531469},16.168531468531469,15.432167832167831,15.432167832167831,15.032517482517481,15.032517482517481,14.632867132867133,14.632867132867133,null,0.9706293706293706,0.9531468531468531,0.93566433566433571,0.89825174825174825,0.85734265734265724,0.83513986013986008,0.81293706293706292,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.471328671328671,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.156643356643357},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.841958041958044},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.168531468531469},15.432167832167831,15.032517482517481,14.632867132867133]
[1000,72,21.820279720279721,11.128342657342658,21.323076923076922,10.87476923076923,20.825874125874126,10.621195804195805,{"$f":"U12*$I$13","v":19.793706293706293},10.292727272727273,18.698601398601397,10.097244755244756,18.106993006993005,9.8683111888111874,17.515384615384612,9.6334615384615372,null,1.2122377622377623,1.1846153846153846,1.156993006993007,1.0996503496503496,1.0388111888111888,1.0059440559440558,0.97307692307692295,0.51,0.51,0.51,0.52,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.128342657342658},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.87476923076923},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.621195804195805},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.292727272727273},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.097244755244756},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8683111888111874},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6334615384615372}]
[null,67,19.856643356643357,13.899650349650349,19.400349650349654,13.677246503496505,18.944055944055947,13.450279720279722,18,13.14,16.993006993006993,12.744755244755245,16.448601398601397,12.583180069930069,15.904195804195803,12.405272727272727,null,1.1031468531468531,1.0777972027972029,1.0524475524475525,1,0.94405594405594406,0.91381118881118872,0.8835664335664335,0.7,0.70499999999999996,0.71,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.899650349650349},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.677246503496505},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.450279720279722},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.744755244755245},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.583180069930069},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.405272727272727}]
[null,62,18.270629370629372,18.087923076923079,17.911888111888111,17.82232867132867,17.553146853146853,17.553146853146853,{"$f":"U14*$I$13","v":16.829370629370629},16.829370629370629,16.048951048951047,16.048951048951047,15.62097902097902,15.62097902097902,15.193006993006993,15.193006993006993,null,1.015034965034965,0.99510489510489508,0.97517482517482512,0.93496503496503491,0.89160839160839156,0.86783216783216777,0.84405594405594409,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.087923076923079,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.82232867132867},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.553146853146853},16.829370629370629,16.048951048951047,15.62097902097902,15.193006993006993]
[null,57,18.207692307692305,18.207692307692305,17.864685314685314,17.864685314685314,17.521678321678319,17.521678321678319,16.804195804195803,16.804195804195803,16.023776223776224,16.023776223776224,15.598951048951047,15.598951048951047,15.174125874125874,15.174125874125874,null,1.0115384615384615,0.99248251748251737,0.97342657342657335,0.93356643356643354,0.89020979020979019,0.86660839160839154,0.843006993006993,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.207692307692305,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.864685314685314},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.521678321678319},16.804195804195803,16.023776223776224,15.598951048951047,15.174125874125874]
[1125,72,22.084615384615386,11.484000000000002,21.568531468531468,11.323479020979022,21.052447552447553,11.157797202797203,19.988811188811191,10.993846153846155,18.862237762237761,10.562853146853147,18.254895104895102,10.314015734265732,17.647552447552446,10.059104895104893,null,1.226923076923077,1.1982517482517483,1.1695804195804196,1.1104895104895105,1.0479020979020979,1.014160839160839,0.98041958041958033,0.52,0.52500000000000002,0.53,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.484000000000002},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.323479020979022},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.157797202797203},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.993846153846155},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.562853146853147},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.314015734265732},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.059104895104893}]
[null,67,20.114685314685314,14.683720279720278,19.645804195804196,14.537895104895105,19.176923076923078,14.382692307692309,18.207692307692305,14.019923076923074,17.175524475524472,13.568664335664334,16.618531468531469,13.377917832167832,16.061538461538461,13.170461538461538,null,1.1174825174825174,1.0914335664335664,1.0653846153846154,1.0115384615384615,0.95419580419580408,0.92325174825174827,0.89230769230769225,0.73,0.74,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.683720279720278},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.537895104895105},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.382692307692309},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.019923076923074},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.568664335664334},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.377917832167832},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.170461538461538}]
[null,62,18.837062937062939,18.837062937062939,18.475174825174822,18.475174825174822,18.113286713286712,18.113286713286712,17.351748251748251,17.351748251748251,16.527272727272727,16.527272727272727,16.077272727272728,16.077272727272728,15.627272727272725,15.627272727272725,null,1.0465034965034965,1.0263986013986013,1.0062937062937063,0.96398601398601391,0.91818181818181821,0.89318181818181819,0.86818181818181805,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.837062937062939,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.475174825174822},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.113286713286712},17.351748251748251,16.527272727272727,16.077272727272728,15.627272727272725]
[null,57,18.811888111888113,18.811888111888113,18.45,18.45,18.088111888111886,18.088111888111886,17.326573426573425,17.326573426573425,16.502097902097901,16.502097902097901,16.055244755244754,16.055244755244754,15.608391608391607,15.608391608391607,null,1.0451048951048951,1.0249999999999999,1.0048951048951047,0.96258741258741254,0.91678321678321673,0.89195804195804185,0.86713286713286708,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.811888111888113,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.45},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.088111888111886},17.326573426573425,16.502097902097901,16.055244755244754,15.608391608391607]

{"sheet":"(C,H,T)XA6_36","index":21,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.484883720930235},{"$f":"IF(AM8>C8,C8,AM8)","v":10.742441860465117},{"$f":"S8*$I$13","v":21.003488372093024},{"$f":"IF(AN8>E8,E8,AN8)","v":10.501744186046512},{"$f":"T8*$I$13","v":20.522093023255813},{"$f":"IF(AO8>G8,G8,AO8)","v":10.261046511627907},{"$f":"U8*$I$13","v":19.501744186046515},{"$f":"IF(AP8>I8,I8,AP8)","v":9.9458895348837224},{"$f":"V8*$I$13","v":18.418604651162791},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.5776744186046514},{"$f":"W8*$I$13","v":17.845639534883723},{"$f":"IF(AR8>M8,M8,AR8)","v":9.4581889534883743},{"$f":"X8*$I$13","v":17.272674418604652},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3272441860465118},null,1.1936046511627909,1.1668604651162791,1.1401162790697674,1.0834302325581397,1.0232558139534884,0.99142441860465136,0.95959302325581397,0.5,0.5,0.5,0.51,0.52,0.53,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.742441860465117},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.501744186046512},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.261046511627907},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.9458895348837224},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.5776744186046514},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.4581889534883743},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3272441860465118}]
[null,67,19.533139534883723,13.087203488372095,19.093604651162789,{"$f":"IF(AN9>E9,E9,AN9)","v":12.983651162790695},18.654069767441861,{"$f":"IF(AO9>G9,G9,AO9)","v":12.871308139534882},{"$f":"U9*$I$13","v":17.722674418604651},{"$f":"IF(AP9>I9,I9,AP9)","v":12.405872093023255},16.723255813953489,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.040744186046512},16.197383720930233,{"$f":"IF(AR9>M9,M9,AR9)","v":11.905077034883721},15.671511627906977,{"$f":"IF(AS9>O9,O9,AS9)","v":11.753633720930232},null,1.0851744186046512,1.0607558139534883,1.0363372093023255,0.98459302325581388,0.92906976744186054,0.89985465116279073,0.87063953488372092,0.67,0.67999999999999994,0.69,0.7,0.72,0.73499999999999999,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.087203488372095},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.983651162790695},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.871308139534882},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.405872093023255},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.040744186046512},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.905077034883721},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.753633720930232}]
[null,62,17.837790697674421,15.697255813953491,17.442732558139536,15.524031976744187,17.04767441860465,15.342906976744185,{"$f":"U10*$I$13","v":16.220930232558139},14.923255813953489,15.420348837209303,15.420348837209303,15.022674418604652,15.022674418604652,14.625,14.625,null,0.99098837209302337,0.96904069767441869,0.9470930232558139,0.90116279069767447,0.85668604651162794,0.83459302325581397,0.8125,0.88,0.89,0.9,0.92,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.697255813953491,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.524031976744187},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.342906976744185},14.923255813953489,15.420348837209303,15.022674418604652,14.625]
[null,57,17.466279069767445,17.466279069767445,17.147093023255813,17.147093023255813,16.827906976744185,16.827906976744185,{"$f":"U11*$I$13","v":16.142441860465116},16.142441860465116,15.399418604651164,15.399418604651164,15.001744186046514,15.001744186046514,14.604069767441862,14.604069767441862,null,0.97034883720930243,0.95261627906976731,0.93488372093023253,0.89680232558139539,0.8555232558139535,0.83343023255813964,0.81133720930232567,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.466279069767445,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.147093023255813},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.827906976744185},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.142441860465116},15.399418604651164,15.001744186046514,14.604069767441862]
[1200,72,21.856395348837214,11.365325581395352,21.351453488372098,11.102755813953491,20.846511627906981,10.840186046511631,{"$f":"U12*$I$13","v":19.789534883720933},10.488453488372095,18.664534883720933,10.265494186046514,18.068023255813955,10.027752906976746,17.471511627906978,9.7840465116279081,null,1.2142441860465119,1.1861918604651165,1.1581395348837211,1.0994186046511629,1.0369186046511629,1.003779069767442,0.97063953488372101,0.52,0.52,0.52,0.53,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.365325581395352},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.102755813953491},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.840186046511631},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.488453488372095},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.265494186046514},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.027752906976746},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7840465116279081}]
[null,67,19.894186046511631,14.124872093023258,19.431104651162794,13.893239825581396,18.968023255813954,13.656976744186046,18,13.32,16.974418604651163,13.070302325581396,16.42761627906977,12.813540697674421,15.880813953488374,12.545843023255816,null,1.105232558139535,1.0795058139534885,1.0537790697674418,1,0.94302325581395341,0.91264534883720938,0.88226744186046524,0.71,0.71499999999999997,0.72,0.74,0.77,0.78,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.124872093023258},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.893239825581396},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.656976744186046},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.070302325581396},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.813540697674421},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.545843023255816}]
[null,62,18.282558139534881,16.819953488372093,17.913662790697675,17.197116279069768,17.544767441860468,17.544767441860468,{"$f":"U14*$I$13","v":16.806976744186045},16.806976744186045,16.011627906976745,16.011627906976745,15.585174418604652,15.585174418604652,15.158720930232558,15.158720930232558,null,1.0156976744186046,0.99520348837209305,0.97470930232558151,0.93372093023255809,0.88953488372093026,0.86584302325581397,0.84215116279069768,0.92,0.96,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.819953488372093,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.197116279069768},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.544767441860468},16.806976744186045,16.011627906976745,15.585174418604652,15.158720930232558]
[null,57,18.209302325581397,18.209302325581397,17.861337209302327,17.861337209302327,17.513372093023257,17.513372093023257,16.780813953488373,16.780813953488373,15.98546511627907,15.98546511627907,15.561627906976746,15.561627906976746,15.137790697674419,15.137790697674419,null,1.0116279069767442,0.992296511627907,0.97296511627906979,0.93226744186046517,0.88808139534883723,0.86453488372093035,0.84098837209302324,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.209302325581397,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.861337209302327},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.513372093023257},16.780813953488373,15.98546511627907,15.561627906976746,15.137790697674419]
[1350,72,22.123255813953488,11.725325581395349,21.602616279069768,11.557399709302326,21.081976744186047,11.384267441860466,19.983139534883719,11.190558139534884,18.826744186046511,10.73124418604651,18.217151162790696,10.565947674418602,17.607558139534884,10.388459302325581,null,1.2290697674418605,1.2001453488372094,1.1712209302325582,1.1101744186046512,1.0459302325581394,1.012063953488372,0.97819767441860461,0.53,0.53500000000000003,0.54,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.725325581395349},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.557399709302326},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.384267441860466},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.190558139534884},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.73124418604651},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.565947674418602},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.388459302325581}]
[null,67,20.150581395348837,14.911430232558139,19.677034883720935,14.757776162790702,19.203488372093027,14.594651162790701,18.209302325581397,14.20325581395349,17.152325581395349,13.893383720930233,16.595058139534885,13.690922965116279,16.037790697674421,13.471744186046513,null,1.1194767441860465,1.0931686046511631,1.0668604651162792,1.0116279069767442,0.95290697674418612,0.9219476744186047,0.89098837209302328,0.74,0.75,0.76,0.78,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.911430232558139},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.757776162790702},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.594651162790701},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.20325581395349},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.893383720930233},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.690922965116279},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.471744186046513}]
[null,62,18.842441860465119,18.842441860465119,18.476162790697675,18.476162790697675,18.109883720930231,18.109883720930231,17.330232558139535,17.330232558139535,16.48779069767442,16.48779069767442,16.040406976744187,16.040406976744187,15.593023255813955,15.593023255813955,null,1.0468023255813954,1.026453488372093,1.0061046511627907,0.96279069767441861,0.91598837209302331,0.89113372093023258,0.86627906976744196,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.842441860465119,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.476162790697675},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.109883720930231},17.330232558139535,16.48779069767442,16.040406976744187,15.593023255813955]
[null,57,18.816279069767447,18.816279069767447,18.450000000000003,18.450000000000003,18.083720930232559,18.083720930232559,17.309302325581395,17.309302325581395,16.46686046511628,16.46686046511628,16.019476744186047,16.019476744186047,15.572093023255816,15.572093023255816,null,1.0453488372093025,1.0250000000000001,1.0046511627906978,0.96162790697674416,0.91482558139534886,0.88997093023255824,0.86511627906976751,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.816279069767447,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.450000000000003},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.083720930232559},17.309302325581395,16.46686046511628,16.019476744186047,15.572093023255816]

{"sheet":"(C,H,T)XA6_42","index":22,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.504578313253013},{"$f":"IF(AM8>C8,C8,AM8)","v":10.537243373493975},{"$f":"S8*$I$13","v":21.012289156626508},{"$f":"IF(AN8>E8,E8,AN8)","v":10.29602168674699},{"$f":"T8*$I$13","v":20.520000000000003},{"$f":"IF(AO8>G8,G8,AO8)","v":10.054800000000002},{"$f":"U8*$I$13","v":19.466024096385542},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7330120481927711},{"$f":"V8*$I$13","v":18.346987951807229},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3569638554216876},{"$f":"W8*$I$13","v":17.757108433734938},{"$f":"IF(AR8>M8,M8,AR8)","v":9.1449108433734931},{"$f":"X8*$I$13","v":17.167228915662651},{"$f":"IF(AS8>O8,O8,AS8)","v":8.926959036144579},null,1.1946987951807229,1.1673493975903615,1.1400000000000001,1.0814457831325301,1.0192771084337349,0.98650602409638544,0.95373493975903612,0.49,0.49,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.537243373493975},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.29602168674699},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.054800000000002},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7330120481927711},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3569638554216876},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.1449108433734931},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.926959036144579}]
[null,67,19.591807228915663,12.930592771084338,19.142891566265064,{"$f":"IF(AN9>E9,E9,AN9)","v":12.730022891566268},18.693975903614458,{"$f":"IF(AO9>G9,G9,AO9)","v":12.524963855421687},{"$f":"U9*$I$13","v":17.739759036144576},{"$f":"IF(AP9>I9,I9,AP9)","v":12.240433734939757},16.720481927710843,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.871542168674697},16.182650602409637,{"$f":"IF(AR9>M9,M9,AR9)","v":11.651508433734939},15.644819277108434,{"$f":"IF(AS9>O9,O9,AS9)","v":11.420718072289157},null,1.088433734939759,1.0634939759036146,1.03855421686747,0.98554216867469879,0.92891566265060233,0.89903614457831327,0.8691566265060241,0.66,0.66500000000000004,0.67,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.930592771084338},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.730022891566268},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.524963855421687},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.240433734939757},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.871542168674697},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.651508433734939},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.420718072289157}]
[null,62,17.921927710843374,15.233638554216867,17.525060240963853,15.071551807228914,17.128192771084336,14.901527710843373,{"$f":"U10*$I$13","v":16.2910843373494},14.499065060240966,15.462650602409639,15.462650602409639,15.057108433734941,15.057108433734941,14.651566265060241,14.651566265060241,null,0.99566265060240966,0.97361445783132528,0.951566265060241,0.90506024096385551,0.85903614457831323,0.83650602409638564,0.81397590361445782,0.85,0.86,0.87,0.89,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.233638554216867,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.071551807228914},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.901527710843373},14.499065060240966,15.462650602409639,15.057108433734941,14.651566265060241]
[null,57,17.544578313253012,17.544578313253012,17.22144578313253,17.22144578313253,16.898313253012049,16.898313253012049,{"$f":"U11*$I$13","v":16.195662650602412},16.195662650602412,15.440963855421687,15.440963855421687,15.035421686746988,15.035421686746988,14.629879518072288,14.629879518072288,null,0.974698795180723,0.95674698795180724,0.93879518072289159,0.89975903614457842,0.85783132530120487,0.83530120481927705,0.81277108433734935,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.544578313253012,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.22144578313253},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.898313253012049},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.195662650602412},15.440963855421687,15.035421686746988,14.629879518072288]
[1400,72,21.860240963855421,10.930120481927711,21.344096385542169,10.778768674698796,20.827951807228917,10.622255421686749,{"$f":"U12*$I$13","v":19.726265060240966},10.257657831325302,18.572530120481925,9.8434409638554214,17.958795180722891,9.6977493975903624,17.345060240963857,9.5397831325301219,null,1.2144578313253012,1.1857831325301205,1.1571084337349398,1.0959036144578314,1.0318072289156626,0.99771084337349403,0.96361445783132538,0.5,0.505,0.51,0.52,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.930120481927711},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.778768674698796},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.622255421686749},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.257657831325302},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8434409638554214},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.6977493975903624},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.5397831325301219}]
[null,67,19.930120481927712,13.75178313253012,19.463855421686745,13.62469879518072,18.997590361445781,13.488289156626504,18,12.959999999999999,16.946024096385543,12.709518072289157,16.390843373493976,12.457040963855421,15.835662650602409,12.193460240963855,null,1.1072289156626507,1.0813253012048192,1.0554216867469879,1,0.94144578313253013,0.91060240963855421,0.87975903614457829,0.69,0.7,0.71,0.72,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.75178313253012},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.62469879518072},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.488289156626504},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.959999999999999},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.709518072289157},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.457040963855421},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.193460240963855}]
[null,62,18.351325301204817,16.332679518072286,17.969638554216868,16.981308433734942,17.587951807228915,17.587951807228915,{"$f":"U14*$I$13","v":16.837590361445784},16.837590361445784,16.022168674698793,16.022168674698793,15.586265060240965,15.586265060240965,15.150361445783131,15.150361445783131,null,1.0195180722891566,0.99831325301204821,0.97710843373493972,0.935421686746988,0.89012048192771076,0.86590361445783137,0.84168674698795176,0.89,0.94500000000000006,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.332679518072286,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.981308433734942},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.587951807228915},16.837590361445784,16.022168674698793,15.586265060240965,15.150361445783131]
[null,57,18.260240963855424,18.260240963855424,17.913253012048191,17.913253012048191,17.566265060240966,17.566265060240966,16.81156626506024,16.81156626506024,16.000481927710844,16.000481927710844,15.566746987951808,15.566746987951808,15.133012048192771,15.133012048192771,null,1.0144578313253012,0.99518072289156623,0.97590361445783136,0.93397590361445781,0.8889156626506024,0.86481927710843376,0.84072289156626512,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.260240963855424,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.913253012048191},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.566265060240966},16.81156626506024,16.000481927710844,15.566746987951808,15.133012048192771]
[1575,72,22.111807228915662,11.498139759036144,21.578313253012048,11.328614457831327,21.044819277108438,11.153754216867473,19.912771084337351,10.75289638554217,18.719999999999995,10.483199999999998,18.088915662650603,10.220237349397589,17.457831325301203,9.9509638554216853,null,1.2284337349397589,1.1987951807228916,1.1691566265060243,1.1062650602409638,1.0399999999999998,1.0049397590361446,0.96987951807228912,0.52,0.52500000000000002,0.53,0.54,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.498139759036144},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.328614457831327},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.153754216867473},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.75289638554217},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.483199999999998},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.220237349397589},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.9509638554216853}]
[null,67,20.181686746987953,14.530814457831326,19.700240963855421,14.381175903614457,19.218795180722893,14.22190843373494,18.195180722891568,13.828337349397591,17.110843373493978,13.517566265060243,16.54265060240964,13.31683373493976,15.974457831325299,13.099055421686744,null,1.1212048192771085,1.0944578313253013,1.0677108433734941,1.0108433734939759,0.95060240963855425,0.91903614457831329,0.88746987951807221,0.72,0.73,0.74,0.76,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.530814457831326},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.381175903614457},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.22190843373494},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.828337349397591},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.517566265060243},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.31683373493976},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.099055421686744}]
[null,62,18.876144578313252,18.876144578313252,18.507469879518077,18.507469879518077,18.138795180722894,18.138795180722894,17.332048192771083,17.332048192771083,16.47325301204819,16.47325301204819,16.013493975903614,16.013493975903614,15.553734939759035,15.553734939759035,null,1.0486746987951807,1.0281927710843375,1.007710843373494,0.96289156626506023,0.91518072289156616,0.88963855421686755,0.86409638554216861,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.876144578313252,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.507469879518077},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.138795180722894},17.332048192771083,16.47325301204819,16.013493975903614,15.553734939759035]
[null,57,18.850120481927711,18.850120481927711,18.481445783132529,18.481445783132529,18.112771084337346,18.112771084337346,17.31036144578313,17.31036144578313,16.45156626506024,16.45156626506024,15.991807228915665,15.991807228915665,15.532048192771084,15.532048192771084,null,1.0472289156626506,1.0267469879518072,1.0062650602409637,0.96168674698795176,0.9139759036144578,0.88843373493975919,0.86289156626506025,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.850120481927711,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.481445783132529},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.112771084337346},17.31036144578313,16.45156626506024,15.991807228915665,15.532048192771084]

{"sheet":"(C,H,T)XA6_48","index":23,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.78},{"$f":"IF(AM8>C8,C8,AM8)","v":10.89},{"$f":"S8*$I$13","v":21.23413043478261},{"$f":"IF(AN8>E8,E8,AN8)","v":10.723235869565219},{"$f":"T8*$I$13","v":20.688260869565216},{"$f":"IF(AO8>G8,G8,AO8)","v":10.55101304347826},{"$f":"U8*$I$13","v":19.569130434782611},{"$f":"IF(AP8>I8,I8,AP8)","v":10.175947826086958},{"$f":"V8*$I$13","v":18.399130434782609},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.751539130434784},{"$f":"W8*$I$13","v":17.788695652173914},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5169521739130438},{"$f":"X8*$I$13","v":17.178260869565214},{"$f":"IF(AS8>O8,O8,AS8)","v":9.2762608695652169},null,1.21,1.1796739130434784,1.1493478260869565,1.0871739130434783,1.0221739130434784,0.98826086956521741,0.95434782608695645,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.89},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.723235869565219},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.55101304347826},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.175947826086958},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.751539130434784},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5169521739130438},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.2762608695652169}]
[null,67,19.721739130434781,13.410782608695651,19.232608695652171,{"$f":"IF(AN9>E9,E9,AN9)","v":13.270499999999997},18.743478260869562,{"$f":"IF(AO9>G9,G9,AO9)","v":13.120434782608692},{"$f":"U9*$I$13","v":17.745652173913044},{"$f":"IF(AP9>I9,I9,AP9)","v":12.776869565217391},16.704782608695652,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.361539130434782},16.155000000000001,{"$f":"IF(AR9>M9,M9,AR9)","v":12.116250000000001},15.605217391304349,{"$f":"IF(AS9>O9,O9,AS9)","v":11.859965217391306},null,1.0956521739130434,1.0684782608695651,1.0413043478260868,0.98586956521739133,0.92804347826086953,0.89749999999999996,0.86695652173913051,0.68,0.69,0.7,0.72,0.74,0.75,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.410782608695651},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.270499999999997},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.120434782608692},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.776869565217391},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.361539130434782},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.116250000000001},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.859965217391306}]
[null,62,17.95304347826087,15.978208695652174,17.534347826086957,15.780913043478263,17.115652173913045,15.575243478260871,{"$f":"U10*$I$13","v":16.282173913043479},16.119352173913043,15.487826086956522,15.487826086956522,15.076956521739129,15.076956521739129,14.666086956521738,14.666086956521738,null,0.99739130434782619,0.97413043478260875,0.9508695652173913,0.90456521739130435,0.86043478260869566,0.83760869565217388,0.81478260869565211,0.89,0.9,0.91,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.978208695652174,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.780913043478263},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.575243478260871},16.119352173913043,15.487826086956522,15.076956521739129,14.666086956521738]
[null,57,17.624347826086954,17.624347826086954,17.283913043478261,17.283913043478261,16.943478260869565,16.943478260869565,{"$f":"U11*$I$13","v":16.231304347826086},16.231304347826086,15.464347826086957,15.464347826086957,15.055434782608698,15.055434782608698,14.646521739130435,14.646521739130435,null,0.97913043478260864,0.96021739130434791,0.94130434782608685,0.90173913043478249,0.85913043478260875,0.83641304347826095,0.81369565217391304,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.624347826086954,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.283913043478261},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.943478260869565},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.231304347826086},15.464347826086957,15.055434782608698,14.646521739130435]
[1600,72,22.15173913043478,11.518904347826087,21.578478260869563,11.328701086956521,21.005217391304349,11.132765217391306,{"$f":"U12*$I$13","v":19.831304347826087},10.708904347826088,18.618260869565219,10.240043478260871,17.982391304347825,10.070139130434782,17.346521739130434,9.8875173913043461,null,1.2306521739130434,1.1988043478260868,1.1669565217391304,1.1017391304347826,1.0343478260869565,0.99902173913043479,0.96369565217391295,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.518904347826087},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.328701086956521},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.132765217391306},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.708904347826088},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.240043478260871},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.070139130434782},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8875173913043461}]
[null,67,20.062173913043477,14.444765217391303,19.553478260869564,14.176271739130433,19.044782608695655,13.902691304347828,18,13.5,16.916086956521738,13.194547826086957,16.348695652173916,12.997213043478263,15.781304347826087,12.782856521739131,null,1.1145652173913043,1.086304347826087,1.0580434782608696,1,0.93978260869565211,0.90826086956521745,0.87673913043478258,0.72,0.72499999999999998,0.73,0.75,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.444765217391303},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.176271739130433},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.902691304347828},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.194547826086957},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.997213043478263},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.782856521739131}]
[null,62,18.422608695652173,18.238382608695652,18.037173913043478,17.94698804347826,17.651739130434784,17.651739130434784,{"$f":"U14*$I$13","v":16.869130434782608},16.869130434782608,16.039565217391306,16.039565217391306,15.595434782608697,15.595434782608697,15.151304347826086,15.151304347826086,null,1.0234782608695652,1.0020652173913043,0.98065217391304349,0.9371739130434783,0.89108695652173919,0.86641304347826098,0.84173913043478255,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.238382608695652,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.94698804347826},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.651739130434784},16.869130434782608,16.039565217391306,15.595434782608697,15.151304347826086]
[null,57,18.363913043478259,18.363913043478259,17.996086956521737,17.996086956521737,17.628260869565217,17.628260869565217,16.845652173913042,16.845652173913042,16.01608695652174,16.01608695652174,15.573913043478258,15.573913043478258,15.131739130434783,15.131739130434783,null,1.0202173913043477,0.99978260869565205,0.97934782608695647,0.93586956521739129,0.88978260869565218,0.86521739130434772,0.84065217391304348,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.363913043478259,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.996086956521737},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.628260869565217},16.845652173913042,16.01608695652174,15.573913043478258,15.131739130434783]
[1800,72,22.41391304347826,12.103513043478261,21.821086956521739,11.89249239130435,21.228260869565219,11.675543478260872,20.015217391304351,11.208521739130438,18.759130434782605,10.88029565217391,18.105652173913043,10.59180652173913,17.452173913043481,10.296782608695652,null,1.2452173913043478,1.2122826086956522,1.1793478260869565,1.1119565217391305,1.0421739130434782,1.0058695652173912,0.96956521739130441,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.58499999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.103513043478261},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.89249239130435},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.675543478260872},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.208521739130438},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.88029565217391},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.59180652173913},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.296782608695652}]
[null,67,20.316521739130437,15.237391304347828,19.790217391304349,15.040565217391306,19.263913043478261,14.833213043478262,18.187826086956523,14.368382608695654,17.072608695652175,13.999539130434782,16.491521739130434,13.770420652173911,15.910434782608695,13.523869565217391,null,1.1286956521739131,1.0994565217391306,1.0702173913043478,1.0104347826086957,0.94847826086956533,0.91619565217391297,0.88391304347826083,0.75,0.76,0.77,0.79,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.237391304347828},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.040565217391306},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.833213043478262},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.368382608695654},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.999539130434782},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.770420652173911},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.523869565217391}]
[null,62,18.989999999999998,18.989999999999998,18.590869565217393,18.590869565217393,18.191739130434787,18.191739130434787,17.358260869565218,17.358260869565218,16.473913043478262,16.473913043478262,16.004347826086956,16.004347826086956,15.534782608695652,15.534782608695652,null,1.0549999999999999,1.0328260869565218,1.0106521739130436,0.96434782608695646,0.91521739130434787,0.88913043478260878,0.86304347826086958,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.989999999999998,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.590869565217393},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.191739130434787},17.358260869565218,16.473913043478262,16.004347826086956,15.534782608695652]
[null,57,18.966521739130432,18.966521739130432,18.567391304347826,18.567391304347826,18.16826086956522,18.16826086956522,17.334782608695651,17.334782608695651,16.458260869565219,16.458260869565219,15.986739130434785,15.986739130434785,15.515217391304347,15.515217391304347,null,1.0536956521739129,1.0315217391304348,1.0093478260869566,0.96304347826086956,0.91434782608695653,0.88815217391304357,0.8619565217391304,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.966521739130432,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.567391304347826},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.16826086956522},17.334782608695651,16.458260869565219,15.986739130434785,15.515217391304347]

{"sheet":"(C,H,T)XA6_49","index":24,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_49"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.494999999999997},{"$f":"IF(AM8>C8,C8,AM8)","v":10.747499999999999},{"$f":"S8*$I$13","v":20.977499999999999},{"$f":"IF(AN8>E8,E8,AN8)","v":10.5936375},{"$f":"T8*$I$13","v":20.46},{"$f":"IF(AO8>G8,G8,AO8)","v":10.434600000000001},{"$f":"U8*$I$13","v":19.4175},{"$f":"IF(AP8>I8,I8,AP8)","v":10.097100000000001},{"$f":"V8*$I$13","v":18.356249999999999},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7288125000000001},{"$f":"W8*$I$13","v":17.799375000000001},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5226656250000019},{"$f":"X8*$I$13","v":17.2425},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3109500000000001},null,1.1941666666666666,1.1654166666666665,1.1366666666666667,1.0787500000000001,1.0197916666666667,0.9888541666666667,0.95791666666666664,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.747499999999999},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.5936375},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.434600000000001},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.097100000000001},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7288125000000001},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5226656250000019},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3109500000000001}]
[null,67,19.612500000000001,13.336500000000001,19.147500000000001,{"$f":"IF(AN9>E9,E9,AN9)","v":13.116037500000001},18.682499999999997,{"$f":"IF(AO9>G9,G9,AO9)","v":12.890924999999998},{"$f":"U9*$I$13","v":17.73},{"$f":"IF(AP9>I9,I9,AP9)","v":12.5883},16.758749999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.066299999999998},16.248750000000001,{"$f":"IF(AR9>M9,M9,AR9)","v":11.942831250000001},15.73875,{"$f":"IF(AS9>O9,O9,AS9)","v":11.804062500000001},null,1.0895833333333333,1.06375,1.0379166666666666,0.98499999999999999,0.93104166666666666,0.90270833333333333,0.87437500000000001,0.68,0.68500000000000005,0.69,0.71,0.72,0.73499999999999999,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.336500000000001},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.116037500000001},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.890924999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.5883},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.066299999999998},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.942831250000001},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.804062500000001}]
[null,62,17.924999999999997,15.594749999999998,17.512500000000003,15.411000000000003,17.100000000000001,15.219000000000001,{"$f":"U10*$I$13","v":16.259999999999998},14.959199999999999,15.404999999999999,14.480699999999999,14.996249999999998,14.546362499999997,14.5875,14.5875,null,0.99583333333333324,0.97291666666666676,0.95000000000000007,0.90333333333333332,0.85583333333333333,0.83312499999999989,0.81041666666666667,0.87,0.88,0.89,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.594749999999998,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.411000000000003},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.219000000000001},14.959199999999999,14.480699999999999,14.546362499999997,14.5875]
[null,57,17.388749999999998,17.388749999999998,17.05875,17.05875,16.728749999999998,16.728749999999998,{"$f":"U11*$I$13","v":16.049999999999997},16.049999999999997,15.33,15.33,14.9475,14.9475,14.565000000000001,14.565000000000001,null,0.96604166666666658,0.94770833333333326,0.92937499999999995,0.89166666666666661,0.85166666666666668,0.83041666666666669,0.8091666666666667,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.388749999999998,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.05875},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.728749999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.049999999999997},15.33,14.9475,14.565000000000001]
[1600,72,21.866250000000001,11.37045,21.326250000000002,11.196281250000002,20.786249999999999,11.016712500000001,{"$f":"U12*$I$13","v":19.69875},10.637325000000001,18.592500000000001,10.225875000000002,18.016874999999999,9.9993656249999994,17.44125,9.767100000000001,null,1.2147916666666667,1.1847916666666667,1.1547916666666667,1.0943750000000001,1.0329166666666667,1.0009375,0.96895833333333325,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.37045},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.196281250000002},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.016712500000001},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.637325000000001},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.225875000000002},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9993656249999994},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.767100000000001}]
[null,67,19.96875,14.1778125,19.477499999999999,13.9264125,18.986250000000002,13.670100000000001,18,13.32,16.987500000000001,12.910500000000001,16.460625,12.756984375,15.93375,12.5876625,null,1.109375,1.0820833333333333,1.0547916666666668,1,0.94374999999999998,0.91447916666666662,0.88520833333333337,0.71,0.71499999999999997,0.72,0.74,0.76,0.77500000000000002,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.1778125},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.9264125},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.670100000000001},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.910500000000001},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.756984375},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.5876625}]
[null,62,18.333750000000002,16.867050000000003,17.910000000000004,16.656300000000002,17.486250000000002,16.437075,{"$f":"U14*$I$13","v":16.69125},16.69125,15.914999999999999,15.914999999999999,15.504375,15.504375,15.09375,15.09375,null,1.0185416666666667,0.99500000000000011,0.97145833333333342,0.92729166666666663,0.88416666666666666,0.86135416666666664,0.83854166666666663,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.867050000000003,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.656300000000002},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.437075},16.69125,15.914999999999999,15.504375,15.09375]
[null,57,18.116250000000001,18.116250000000001,17.758125000000003,17.758125000000003,17.399999999999999,17.399999999999999,16.668750000000003,16.668750000000003,15.89625,15.89625,15.485625000000001,15.485625000000001,15.075000000000001,15.075000000000001,null,1.0064583333333335,0.98656250000000012,0.96666666666666667,0.92604166666666676,0.88312500000000005,0.86031250000000004,0.83750000000000002,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.116250000000001,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.758125000000003},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.399999999999999},16.668750000000003,15.89625,15.485625000000001,15.075000000000001]
[1800,72,22.143750000000001,11.957625000000002,21.581250000000001,11.761781250000002,21.018750000000001,11.560312500000002,19.897500000000001,11.142600000000002,18.757500000000004,10.691775000000002,18.164999999999999,10.535699999999999,17.572499999999998,10.367774999999998,null,1.2302083333333333,1.1989583333333333,1.1677083333333333,1.1054166666666667,1.0420833333333335,1.0091666666666665,0.97624999999999995,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.957625000000002},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.761781250000002},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.560312500000002},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.142600000000002},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.691775000000002},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.535699999999999},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.367774999999998}]
[null,67,20.227499999999999,14.968349999999999,19.723125,14.792343750000001,19.21875,14.606249999999999,18.191249999999997,14.189174999999997,17.15625,13.725000000000001,16.616250000000001,13.542243749999999,16.076249999999998,13.343287499999997,null,1.12375,1.0957291666666666,1.0677083333333333,1.0106249999999999,0.953125,0.92312500000000008,0.89312499999999995,0.74,0.75,0.76,0.78,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.968349999999999},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.792343750000001},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.606249999999999},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.189174999999997},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.725000000000001},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.542243749999999},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.343287499999997}]
[null,62,18.727499999999999,18.727499999999999,18.348749999999999,18.348749999999999,17.970000000000002,17.970000000000002,17.186249999999998,17.186249999999998,16.365000000000002,16.365000000000002,15.93375,15.93375,15.502500000000001,15.502500000000001,null,1.0404166666666665,1.0193749999999999,0.99833333333333341,0.95479166666666659,0.90916666666666668,0.88520833333333337,0.86125000000000007,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.727499999999999,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.348749999999999},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.970000000000002},17.186249999999998,16.365000000000002,15.93375,15.502500000000001]
[null,57,18.708749999999998,18.708749999999998,18.328125,18.328125,17.947499999999998,17.947499999999998,17.16375,17.16375,16.346250000000001,16.346250000000001,15.914999999999999,15.914999999999999,15.483750000000001,15.483750000000001,null,1.0393749999999999,1.0182291666666667,0.99708333333333332,0.95354166666666673,0.90812500000000007,0.88416666666666666,0.86020833333333335,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.708749999999998,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.328125},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.947499999999998},17.16375,16.346250000000001,15.914999999999999,15.483750000000001]

{"sheet":"(C,H,T)XA6_60","index":25,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.734999999999999},{"$f":"IF(AM8>C8,C8,AM8)","v":10.8675},{"$f":"S8*$I$13","v":21.180535714285718},{"$f":"IF(AN8>E8,E8,AN8)","v":10.696170535714288},{"$f":"T8*$I$13","v":20.626071428571432},{"$f":"IF(AO8>G8,G8,AO8)","v":10.519296428571431},{"$f":"U8*$I$13","v":19.47214285714286},{"$f":"IF(AP8>I8,I8,AP8)","v":10.125514285714287},{"$f":"V8*$I$13","v":18.25392857142857},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.6745821428571421},{"$f":"W8*$I$13","v":17.609464285714285},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5091107142857147},{"$f":"X8*$I$13","v":16.965},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3307500000000001},null,1.2075,1.1766964285714288,1.1458928571428573,1.0817857142857144,1.0141071428571429,0.97830357142857138,0.9425,0.5,0.505,0.51,0.52,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.8675},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.696170535714288},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.519296428571431},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.125514285714287},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.6745821428571421},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5091107142857147},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3307500000000001}]
[null,67,19.803214285714287,13.466185714285716,19.311428571428568,{"$f":"IF(AN9>E9,E9,AN9)","v":13.324885714285712},18.819642857142856,{"$f":"IF(AO9>G9,G9,AO9)","v":13.173749999999998},{"$f":"U9*$I$13","v":17.78142857142857},{"$f":"IF(AP9>I9,I9,AP9)","v":12.802628571428571},16.682142857142857,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.344785714285713},16.100357142857145,{"$f":"IF(AR9>M9,M9,AR9)","v":12.155769642857145},15.51857142857143,{"$f":"IF(AS9>O9,O9,AS9)","v":11.949300000000001},null,1.1001785714285715,1.0728571428571427,1.0455357142857142,0.98785714285714288,0.92678571428571421,0.89446428571428582,0.86214285714285721,0.68,0.69,0.7,0.72,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.466185714285716},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.324885714285712},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.173749999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.802628571428571},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.344785714285713},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.155769642857145},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.949300000000001}]
[null,62,18.205714285714283,16.203085714285713,17.792678571428574,16.725117857142859,17.379642857142859,17.20584642857143,{"$f":"U10*$I$13","v":16.588928571428571},16.588928571428571,15.746785714285716,15.746785714285716,15.290357142857141,15.290357142857141,14.83392857142857,14.83392857142857,null,1.0114285714285713,0.98848214285714298,0.96553571428571427,0.92160714285714285,0.87482142857142864,0.84946428571428567,0.82410714285714282,0.89,0.94,0.99,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.203085714285713,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.725117857142859},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":17.20584642857143},16.588928571428571,15.746785714285716,15.290357142857141,14.83392857142857]
[null,57,18.061071428571431,18.061071428571431,17.701071428571428,17.701071428571428,17.341071428571428,17.341071428571428,{"$f":"U11*$I$13","v":16.563214285714285},16.563214285714285,15.727500000000001,15.727500000000001,15.271071428571432,15.271071428571432,14.814642857142857,14.814642857142857,null,1.0033928571428572,0.98339285714285718,0.96339285714285716,0.9201785714285714,0.87375000000000003,0.84839285714285728,0.82303571428571431,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.061071428571431,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.701071428571428},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.341071428571428},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.563214285714285},15.727500000000001,15.271071428571432,14.814642857142857]
[2000,72,22.033928571428572,11.457642857142858,21.458571428571425,11.265749999999999,20.883214285714288,11.068103571428573,{"$f":"U12*$I$13","v":19.681071428571428},10.627778571428571,18.42107142857143,10.315800000000001,17.754107142857144,10.031070535714285,17.087142857142855,9.7396714285714268,null,1.2241071428571428,1.1921428571428569,1.1601785714285715,1.0933928571428571,1.0233928571428572,0.98633928571428575,0.94928571428571418,0.52,0.52500000000000002,0.53,0.54,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.457642857142858},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.265749999999999},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.068103571428573},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.627778571428571},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.315800000000001},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.031070535714285},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7396714285714268}]
[null,67,20.102142857142859,14.473542857142858,19.587857142857139,14.299135714285711,19.073571428571427,14.114442857142855,18,13.68,16.865357142857142,13.323632142857143,16.265892857142859,13.094043750000001,15.666428571428574,12.84647142857143,null,1.1167857142857143,1.0882142857142856,1.0596428571428571,1,0.93696428571428569,0.90366071428571437,0.87035714285714294,0.72,0.73,0.74,0.76,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.473542857142858},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.299135714285711},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.114442857142855},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.68},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.323632142857143},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.094043750000001},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.84647142857143}]
[null,62,18.765000000000001,18.765000000000001,18.374464285714286,18.374464285714286,17.983928571428571,17.983928571428571,{"$f":"U14*$I$13","v":17.145},17.145,16.245000000000001,16.245000000000001,15.758035714285713,15.758035714285713,15.271071428571426,15.271071428571426,null,1.0425,1.0208035714285715,0.99910714285714286,0.95250000000000001,0.90249999999999997,0.87544642857142851,0.84839285714285706,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.765000000000001,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":18.374464285714286},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.983928571428571},17.145,16.245000000000001,15.758035714285713,15.271071428571426]
[null,57,18.7425,18.7425,18.351964285714288,18.351964285714288,17.961428571428574,17.961428571428574,17.125714285714285,17.125714285714285,16.225714285714286,16.225714285714286,15.73875,15.73875,15.251785714285717,15.251785714285717,null,1.04125,1.0195535714285715,0.99785714285714289,0.9514285714285714,0.90142857142857136,0.87437500000000001,0.84732142857142867,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.7425,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18.351964285714288},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.961428571428574},17.125714285714285,16.225714285714286,15.73875,15.251785714285717]
[2250,72,22.242857142857144,12.011142857142858,21.648214285714282,11.798276785714284,21.053571428571431,11.579464285714288,19.816071428571426,11.097,18.520714285714284,10.742014285714284,17.840892857142855,10.526126785714284,17.161071428571429,10.296642857142857,null,1.2357142857142858,1.2026785714285713,1.1696428571428572,1.1008928571428571,1.0289285714285714,0.99116071428571417,0.95339285714285715,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.011142857142858},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.798276785714284},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.579464285714288},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.097},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.742014285714284},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.526126785714284},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.296642857142857}]
[null,67,20.317499999999999,15.238125,19.790357142857143,15.139623214285715,19.263214285714284,15.025307142857143,18.157499999999999,14.526,17.000357142857144,14.110296428571429,16.394464285714285,13.853322321428571,15.788571428571428,13.578171428571428,null,1.1287499999999999,1.0994642857142858,1.0701785714285714,1.00875,0.94446428571428576,0.91080357142857138,0.87714285714285711,0.75,0.76500000000000001,0.78,0.8,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.238125},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.139623214285715},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.025307142857143},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.526},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.110296428571429},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.853322321428571},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.578171428571428}]
[null,62,19.317857142857143,19.317857142857143,18.901607142857141,18.901607142857141,18.485357142857143,18.485357142857143,17.594999999999999,17.594999999999999,16.640357142857145,16.640357142857145,16.126071428571429,16.126071428571429,15.611785714285714,15.611785714285714,null,1.0732142857142857,1.0500892857142856,1.0269642857142858,0.97750000000000004,0.92446428571428574,0.89589285714285716,0.86732142857142858,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,19.317857142857143,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.901607142857141},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.485357142857143},17.594999999999999,16.640357142857145,16.126071428571429,15.611785714285714]
[null,57,19.295357142857142,19.295357142857142,18.879107142857141,18.879107142857141,18.462857142857139,18.462857142857139,17.575714285714284,17.575714285714284,16.62107142857143,16.62107142857143,16.108392857142857,16.108392857142857,15.595714285714285,15.595714285714285,null,1.0719642857142857,1.0488392857142856,1.0257142857142856,0.97642857142857142,0.92339285714285713,0.89491071428571434,0.86642857142857144,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,19.295357142857142,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.879107142857141},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.462857142857139},17.575714285714284,16.62107142857143,16.108392857142857,15.595714285714285]

{"sheet":"(C,H,T)XA6_61","index":26,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["(C,H,T)XA6_61"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.581848739495801},{"$f":"IF(AM8>C8,C8,AM8)","v":10.7909243697479},{"$f":"S8*$I$13","v":21.067563025210085},{"$f":"IF(AN8>E8,E8,AN8)","v":10.639119327731093},{"$f":"T8*$I$13","v":20.553277310924372},{"$f":"IF(AO8>G8,G8,AO8)","v":10.48217142857143},{"$f":"U8*$I$13","v":19.455126050420169},{"$f":"IF(AP8>I8,I8,AP8)","v":10.116665546218488},{"$f":"V8*$I$13","v":18.269243697478991},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.6826991596638656},{"$f":"W8*$I$13","v":17.632436974789915},{"$f":"IF(AR8>M8,M8,AR8)","v":9.4333537815126043},{"$f":"X8*$I$13","v":16.995630252100842},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1776403361344556},null,1.1989915966386555,1.1704201680672268,1.1418487394957983,1.0808403361344538,1.0149579831932773,0.97957983193277309,0.94420168067226895,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.7909243697479},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.639119327731093},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.48217142857143},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.116665546218488},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.6826991596638656},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.4333537815126043},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1776403361344556}]
[null,67,19.663865546218485,13.37142857142857,19.201008403361346,{"$f":"IF(AN9>E9,E9,AN9)","v":13.152690756302523},18.7381512605042,{"$f":"IF(AO9>G9,G9,AO9)","v":12.929324369747897},{"$f":"U9*$I$13","v":17.74890756302521},{"$f":"IF(AP9>I9,I9,AP9)","v":12.601724369747899},16.687058823529412,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.18155294117647},16.113781512605044,{"$f":"IF(AR9>M9,M9,AR9)","v":12.004767226890758},15.540504201680672,{"$f":"IF(AS9>O9,O9,AS9)","v":11.810783193277311},null,1.0924369747899159,1.0667226890756303,1.0410084033613445,0.98605042016806721,0.92705882352941171,0.89521008403361346,0.8633613445378151,0.68,0.68500000000000005,0.69,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.37142857142857},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.152690756302523},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.929324369747897},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.601724369747899},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.18155294117647},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.004767226890758},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.810783193277311}]
[null,62,18.015126050420168,15.853310924369747,17.608235294117645,15.671329411764704,17.201344537815125,15.481210084033613,{"$f":"U10*$I$13","v":16.345210084033614},15.037593277310926,15.495126050420168,15.495126050420168,15.061008403361344,15.061008403361344,14.626890756302521,14.626890756302521,null,1.0008403361344538,0.97823529411764698,0.95563025210084029,0.90806722689075636,0.86084033613445377,0.83672268907563019,0.81260504201680672,0.88,0.89,0.9,0.92,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.853310924369747,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.671329411764704},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.481210084033613},15.037593277310926,15.495126050420168,15.061008403361344,14.626890756302521]
[null,57,17.649075630252103,17.649075630252103,17.317815126050423,17.317815126050423,16.98655462184874,16.98655462184874,{"$f":"U11*$I$13","v":16.263529411764704},16.263529411764704,15.473949579831931,15.473949579831931,15.03983193277311,15.03983193277311,14.605714285714287,14.605714285714287,null,0.98050420168067232,0.96210084033613452,0.94369747899159662,0.9035294117647058,0.85966386554621843,0.83554621848739496,0.8114285714285715,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.649075630252103,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.317815126050423},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.98655462184874},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.263529411764704},15.473949579831931,15.03983193277311,14.605714285714287]
[2000,72,21.932773109243694,11.405042016806721,21.394285714285715,11.232000000000001,20.855798319327732,11.053573109243699,{"$f":"U12*$I$13","v":19.703193277310923},10.639724369747899,18.477983193277307,10.16289075630252,17.816974789915967,9.9775058823529434,17.155966386554621,9.7789008403361333,null,1.2184873949579831,1.1885714285714286,1.1586554621848739,1.0946218487394956,1.0265546218487394,0.98983193277310921,0.95310924369747896,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.405042016806721},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.232000000000001},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.053573109243699},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.639724369747899},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.16289075630252},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9775058823529434},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7789008403361333}]
[null,67,19.999663865546218,14.199761344537814,19.517142857142858,14.052342857142857,19.034621848739498,13.895273949579833,18,13.5,16.898823529411764,13.012094117647059,16.305882352941175,12.800117647058823,15.712941176470588,12.570352941176472,null,1.1110924369747899,1.0842857142857143,1.0574789915966387,1,0.93882352941176472,0.90588235294117647,0.87294117647058822,0.71,0.72,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.199761344537814},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.052342857142857},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.895273949579833},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.012094117647059},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.800117647058823},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.570352941176472}]
[null,62,18.444705882352942,16.969129411764708,18.054453781512603,17.332275630252099,17.664201680672271,17.664201680672271,{"$f":"U14*$I$13","v":16.883697478991596},16.883697478991596,16.030588235294118,16.030588235294118,15.563193277310925,15.563193277310925,15.095798319327731,15.095798319327731,null,1.0247058823529411,1.0030252100840336,0.98134453781512609,0.93798319327731094,0.89058823529411768,0.86462184873949577,0.83865546218487397,0.92,0.96,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.969129411764708,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.332275630252099},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.664201680672271},16.883697478991596,16.030588235294118,15.563193277310925,15.095798319327731]
[null,57,18.356974789915963,18.356974789915963,18,18,17.643025210084033,17.643025210084033,16.856470588235293,16.856470588235293,16.009411764705881,16.009411764705881,15.543529411764705,15.543529411764705,15.077647058823532,15.077647058823532,null,1.0198319327731091,1,0.98016806722689076,0.93647058823529405,0.88941176470588235,0.86352941176470588,0.83764705882352952,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.356974789915963,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.643025210084033},16.856470588235293,16.009411764705881,15.543529411764705,15.077647058823532]
[2250,72,22.180840336134452,11.977653781512604,21.622689075630252,11.784365546218488,21.064537815126052,11.585495798319329,19.881680672268907,11.133741176470588,18.614117647058826,10.796188235294119,17.934957983193275,10.581625210084031,17.255798319327731,10.353478991596639,null,1.2322689075630251,1.2012605042016806,1.1702521008403362,1.1045378151260503,1.0341176470588236,0.99638655462184866,0.95865546218487396,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.977653781512604},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.784365546218488},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.585495798319329},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.133741176470588},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.796188235294119},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.581625210084031},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.353478991596639}]
[null,67,20.250756302521005,15.188067226890754,19.750084033613447,15.01006386554622,19.249411764705886,14.822047058823532,18.184537815126053,14.365784873949583,17.053109243697477,13.98354957983193,16.44655462184874,13.732873109243698,15.84,13.464,null,1.1250420168067226,1.0972268907563025,1.0694117647058825,1.0102521008403362,0.94739495798319329,0.91369747899159659,0.88,0.75,0.76,0.77,0.79,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.188067226890754},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.01006386554622},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.822047058823532},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.365784873949583},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.98354957983193},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.732873109243698},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.464}]
[null,62,18.968067226890756,18.968067226890756,18.585378151260503,18.585378151260503,18.202689075630254,18.202689075630254,17.36470588235294,17.36470588235294,16.460168067226892,16.460168067226892,15.965546218487393,15.965546218487393,15.4709243697479,15.4709243697479,null,1.053781512605042,1.0325210084033614,1.0112605042016807,0.96470588235294119,0.91445378151260504,0.88697478991596634,0.85949579831932776,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.968067226890756,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.585378151260503},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.202689075630254},17.36470588235294,16.460168067226892,15.965546218487393,15.4709243697479]
[null,57,18.943865546218486,18.943865546218486,18.561176470588236,18.561176470588236,18.178487394957983,18.178487394957983,17.346554621848743,17.346554621848743,16.442016806722688,16.442016806722688,15.947394957983194,15.947394957983194,15.452773109243697,15.452773109243697,null,1.0524369747899158,1.0311764705882354,1.0099159663865547,0.96369747899159675,0.91344537815126048,0.8859663865546219,0.85848739495798321,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.943865546218486,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.561176470588236},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.178487394957983},17.346554621848743,16.442016806722688,15.947394957983194,15.452773109243697]

{"sheet":"N4A3_18","index":27,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.233720930232558},{"$f":"IF(AM8>C8,C8,AM8)","v":10.616860465116279},{"$f":"S8*$I$13","v":20.768023255813954},{"$f":"IF(AN8>E8,E8,AN8)","v":10.384011627906977},{"$f":"T8*$I$13","v":20.302325581395348},{"$f":"IF(AO8>G8,G8,AO8)","v":10.151162790697674},{"$f":"U8*$I$13","v":19.308139534883718},{"$f":"IF(AP8>I8,I8,AP8)","v":9.8471511627906967},{"$f":"V8*$I$13","v":18.334883720930232},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.534139534883721},{"$f":"W8*$I$13","v":17.795930232558138},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3428633720930225},{"$f":"X8*$I$13","v":17.256976744186048},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1461976744186053},null,1.1796511627906976,1.1537790697674419,1.1279069767441861,1.0726744186046511,1.0186046511627906,0.98866279069767438,0.95872093023255811,0.5,0.5,0.5,0.51,0.52,0.52500000000000002,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.616860465116279},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.384011627906977},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.151162790697674},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.8471511627906967},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.534139534883721},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3428633720930225},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1461976744186053}]
[null,67,19.548837209302327,13.09772093023256,19.109302325581393,{"$f":"IF(AN9>E9,E9,AN9)","v":12.898779069767441},18.669767441860468,{"$f":"IF(AO9>G9,G9,AO9)","v":12.69544186046512},{"$f":"U9*$I$13","v":17.738372093023255},{"$f":"IF(AP9>I9,I9,AP9)","v":12.239476744186044},16.79651162790698,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.925523255813955},16.283720930232562,{"$f":"IF(AR9>M9,M9,AR9)","v":11.724279069767444},15.77093023255814,{"$f":"IF(AS9>O9,O9,AS9)","v":11.512779069767442},null,1.086046511627907,1.061627906976744,1.0372093023255815,0.98546511627906974,0.93313953488372103,0.90465116279069779,0.87616279069767444,0.67,0.67500000000000004,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.09772093023256},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.898779069767441},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.69544186046512},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.239476744186044},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.925523255813955},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.724279069767444},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.512779069767442}]
[null,62,17.989534883720932,15.471000000000002,17.586627906976744,15.300366279069767,17.18372093023256,15.121674418604654,{"$f":"U10*$I$13","v":16.325581395348838},14.693023255813955,15.456976744186047,14.220418604651163,15.017441860465118,14.416744186046513,14.577906976744185,14.577906976744185,null,0.99941860465116295,0.97703488372093028,0.95465116279069784,0.90697674418604657,0.85872093023255813,0.83430232558139539,0.80988372093023253,0.86,0.87,0.88,0.9,0.92,0.96,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.471000000000002,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.300366279069767},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.121674418604654},14.693023255813955,14.220418604651163,14.416744186046513,14.577906976744185]
[null,57,17.466279069767445,17.466279069767445,17.136627906976745,17.136627906976745,16.806976744186045,16.806976744186045,{"$f":"U11*$I$13","v":16.105813953488372},16.105813953488372,15.373255813953488,15.373255813953488,14.975581395348836,14.975581395348836,14.577906976744185,14.577906976744185,null,0.97034883720930243,0.95203488372093026,0.93372093023255809,0.8947674418604652,0.85406976744186047,0.8319767441860465,0.80988372093023253,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.466279069767445,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.136627906976745},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.806976744186045},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.105813953488372},15.373255813953488,14.975581395348836,14.577906976744185]
[600,72,21.61046511627907,11.021337209302326,21.092441860465119,10.862607558139537,20.574418604651164,10.698697674418606,{"$f":"U12*$I$13","v":19.559302325581399},10.366430232558143,18.554651162790702,10.019511627906979,18.000000000000004,9.8100000000000023,17.445348837209306,9.5949418604651182,null,1.2005813953488371,1.1718023255813954,1.1430232558139535,1.0866279069767444,1.0308139534883722,1.0000000000000002,0.9691860465116281,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.021337209302326},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.862607558139537},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.698697674418606},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.366430232558143},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.019511627906979},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8100000000000023},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.5949418604651182}]
[null,67,19.86279069767442,13.903953488372093,19.412790697674421,13.686017441860466,18.962790697674418,13.463581395348836,18,13.14,17.037209302325582,12.777906976744188,16.50872093023256,12.546627906976745,15.980232558139535,12.304779069767443,null,1.1034883720930233,1.0784883720930234,1.0534883720930233,1,0.94651162790697685,0.91715116279069775,0.88779069767441865,0.7,0.70499999999999996,0.71,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.903953488372093},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.686017441860466},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.463581395348836},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.777906976744188},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.546627906976745},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.304779069767443}]
[null,62,18.376744186046512,16.539069767441863,17.968604651162792,16.35143023255814,17.560465116279072,16.155627906976747,{"$f":"U14*$I$13","v":16.70232558139535},16.70232558139535,15.948837209302326,15.948837209302326,15.525,15.525,15.101162790697675,15.101162790697675,null,1.0209302325581395,0.9982558139534885,0.97558139534883737,0.9279069767441861,0.88604651162790704,0.86250000000000004,0.83895348837209305,0.9,0.91,0.92,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.539069767441863,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.35143023255814},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.155627906976747},16.70232558139535,15.948837209302326,15.525,15.101162790697675]
[null,57,18.156976744186046,18.156976744186046,17.811627906976749,17.811627906976749,17.466279069767445,17.466279069767445,16.723255813953489,16.723255813953489,15.948837209302326,15.948837209302326,15.530232558139534,15.530232558139534,15.111627906976743,15.111627906976743,null,1.0087209302325582,0.98953488372093046,0.97034883720930243,0.92906976744186054,0.88604651162790704,0.86279069767441863,0.83953488372093021,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.156976744186046,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.811627906976749},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.466279069767445},16.723255813953489,15.948837209302326,15.530232558139534,15.111627906976743]
[675,72,21.851162790697675,11.581116279069768,21.306976744186048,11.399232558139536,20.762790697674419,11.211906976744187,19.716279069767442,10.843953488372094,18.70116279069768,10.472651162790701,18.136046511627903,10.246866279069764,17.57093023255814,10.015430232558138,null,1.213953488372093,1.1837209302325582,1.1534883720930234,1.0953488372093023,1.0389534883720932,1.0075581395348836,0.97616279069767442,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.581116279069768},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.399232558139536},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.211906976744187},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.843953488372094},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.472651162790701},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.246866279069764},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.015430232558138}]
[null,67,20.082558139534886,14.660267441860466,19.622093023255815,14.422238372093023,19.161627906976747,14.179604651162792,18.17790697674419,13.815209302325584,17.2046511627907,13.591674418604654,16.665697674418606,13.332558139534886,16.126744186046512,13.062662790697676,null,1.1156976744186047,1.0901162790697674,1.0645348837209303,1.0098837209302327,0.95581395348837217,0.9258720930232559,0.89593023255813953,0.73,0.73499999999999999,0.74,0.76,0.79,0.8,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.660267441860466},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.422238372093023},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.179604651162792},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.815209302325584},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.591674418604654},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.332558139534886},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.062662790697676}]
[null,62,18.743023255813952,18.555593023255813,18.366279069767444,18.274447674418607,17.989534883720932,17.989534883720932,17.2046511627907,17.2046511627907,16.409302325581397,16.409302325581397,15.969767441860466,15.969767441860466,15.530232558139534,15.530232558139534,null,1.0412790697674419,1.0203488372093024,0.99941860465116295,0.95581395348837217,0.91162790697674423,0.88720930232558137,0.86279069767441863,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.555593023255813,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.274447674418607},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.989534883720932},17.2046511627907,16.409302325581397,15.969767441860466,15.530232558139534]
[null,57,18.722093023255816,18.722093023255816,18.355813953488372,18.355813953488372,17.989534883720932,17.989534883720932,17.2046511627907,17.2046511627907,16.409302325581397,16.409302325581397,15.969767441860466,15.969767441860466,15.530232558139534,15.530232558139534,null,1.0401162790697676,1.0197674418604652,0.99941860465116295,0.95581395348837217,0.91162790697674423,0.88720930232558137,0.86279069767441863,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.722093023255816,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.355813953488372},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.989534883720932},17.2046511627907,16.409302325581397,15.969767441860466,15.530232558139534]

{"sheet":"N4A3_24","index":28,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.177391304347825},{"$f":"IF(AM8>C8,C8,AM8)","v":10.800469565217391},{"$f":"S8*$I$13","v":20.692173913043476},{"$f":"IF(AN8>E8,E8,AN8)","v":10.553008695652172},{"$f":"T8*$I$13","v":20.20695652173913},{"$f":"IF(AO8>G8,G8,AO8)","v":10.305547826086956},{"$f":"U8*$I$13","v":19.283478260869568},{"$f":"IF(AP8>I8,I8,AP8)","v":10.027408695652175},{"$f":"V8*$I$13","v":18.344347826086956},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7225043478260869},{"$f":"W8*$I$13","v":17.82391304347826},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5357934782608691},{"$f":"X8*$I$13","v":17.303478260869564},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3438782608695661},null,1.1765217391304348,1.1495652173913042,1.1226086956521739,1.0713043478260871,1.0191304347826087,0.99021739130434772,0.96130434782608698,0.51,0.51,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.800469565217391},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.553008695652172},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.305547826086956},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.027408695652175},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7225043478260869},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5357934782608691},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3438782608695661}]
[null,67,19.463478260869568,13.235165217391307,19.052608695652172,{"$f":"IF(AN9>E9,E9,AN9)","v":13.051036956521738},18.641739130434782,{"$f":"IF(AO9>G9,G9,AO9)","v":12.862799999999998},{"$f":"U9*$I$13","v":17.765217391304347},{"$f":"IF(AP9>I9,I9,AP9)","v":12.613304347826086},16.865217391304348,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.311608695652174},16.376086956521739,{"$f":"IF(AR9>M9,M9,AR9)","v":12.118304347826086},15.88695652173913,{"$f":"IF(AS9>O9,O9,AS9)","v":11.915217391304347},null,1.0813043478260871,1.0584782608695651,1.0356521739130435,0.9869565217391304,0.93695652173913047,0.9097826086956522,0.88260869565217392,0.68,0.68500000000000005,0.69,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.235165217391307},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.051036956521738},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.862799999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.613304347826086},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.311608695652174},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.118304347826086},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.915217391304347}]
[null,62,17.984347826086957,15.826226086956522,17.600869565217394,15.664773913043481,17.217391304347828,15.495652173913046,{"$f":"U10*$I$13","v":16.411304347826086},15.0984,15.589565217391305,14.654191304347826,15.182608695652172,14.727130434782607,14.775652173913043,14.775652173913043,null,0.99913043478260877,0.97782608695652184,0.95652173913043481,0.91173913043478261,0.86608695652173917,0.84347826086956512,0.82086956521739129,0.88,0.89,0.9,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.826226086956522,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.664773913043481},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.495652173913046},15.0984,14.654191304347826,14.727130434782607,14.775652173913043]
[null,57,17.538260869565217,17.538260869565217,17.225217391304348,17.225217391304348,16.912173913043478,16.912173913043478,{"$f":"U11*$I$13","v":16.239130434782609},16.239130434782609,15.534782608695652,15.534782608695652,15.155217391304349,15.155217391304349,14.775652173913043,14.775652173913043,null,0.97434782608695658,0.95695652173913037,0.93956521739130427,0.90217391304347827,0.86304347826086958,0.84195652173913049,0.82086956521739129,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.538260869565217,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.225217391304348},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.912173913043478},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.239130434782609},15.534782608695652,15.155217391304349,14.775652173913043]
[800,72,21.521739130434781,11.191304347826087,20.989565217391302,11.019521739130434,20.457391304347826,10.842417391304348,{"$f":"U12*$I$13","v":19.510434782608698},10.535634782608698,18.54,10.197000000000001,18.007826086956523,9.9943434782608715,17.475652173913041,9.7863652173913032,null,1.1956521739130435,1.1660869565217391,1.1365217391304347,1.0839130434782609,1.03,1.0004347826086957,0.97086956521739121,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.191304347826087},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.019521739130434},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.842417391304348},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.535634782608698},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.197000000000001},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9943434782608715},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7863652173913032}]
[null,67,19.753043478260871,14.024660869565217,19.326521739130438,13.915095652173916,18.900000000000002,13.797000000000001,18,13.5,17.084347826086955,12.984104347826086,16.579565217391306,12.849163043478262,16.074782608695649,12.699078260869564,null,1.0973913043478261,1.0736956521739132,1.05,1,0.94913043478260861,0.92108695652173911,0.89304347826086949,0.71,0.72,0.73,0.75,0.76,0.77500000000000002,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.024660869565217},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.915095652173916},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.797000000000001},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.984104347826086},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.849163043478262},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.699078260869564}]
[null,62,18.344347826086956,16.876799999999999,17.960869565217394,16.703608695652175,17.577391304347827,16.522747826086956,{"$f":"U14*$I$13","v":16.818260869565215},16.818260869565215,16.082608695652176,16.082608695652176,15.679565217391305,15.679565217391305,15.276521739130436,15.276521739130436,null,1.0191304347826087,0.99782608695652186,0.97652173913043483,0.93434782608695643,0.89347826086956528,0.87108695652173918,0.84869565217391307,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.876799999999999,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.703608695652175},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.522747826086956},16.818260869565215,16.082608695652176,15.679565217391305,15.276521739130436]
[null,57,18.195652173913043,18.195652173913043,17.866956521739127,17.866956521739127,17.538260869565217,17.538260869565217,16.818260869565215,16.818260869565215,16.082608695652176,16.082608695652176,15.679565217391305,15.679565217391305,15.276521739130436,15.276521739130436,null,1.0108695652173914,0.9926086956521738,0.97434782608695658,0.93434782608695643,0.89347826086956528,0.87108695652173918,0.84869565217391307,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.195652173913043,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.866956521739127},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.538260869565217},16.818260869565215,16.082608695652176,15.679565217391305,15.276521739130436]
[900,72,21.740869565217395,11.740069565217395,21.193043478260865,11.550208695652172,20.64521739130435,11.354869565217394,19.659130434782607,11.009113043478262,18.673043478260869,10.643634782608695,18.12521739130435,10.512626086956523,17.577391304347827,10.370660869565217,null,1.2078260869565218,1.1773913043478259,1.1469565217391304,1.0921739130434782,1.037391304347826,1.0069565217391305,0.97652173913043483,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.740069565217395},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.550208695652172},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.354869565217394},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.009113043478262},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.643634782608695},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.512626086956523},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.370660869565217}]
[null,67,19.964347826086957,14.973260869565218,19.526086956521741,14.742195652173915,19.087826086956522,14.506747826086956,18.164347826086956,14.168191304347827,17.233043478260868,13.786434782608694,16.720434782608699,13.627154347826089,16.207826086956523,13.452495652173914,null,1.1091304347826088,1.0847826086956522,1.0604347826086957,1.0091304347826087,0.95739130434782604,0.92891304347826098,0.90043478260869569,0.75,0.755,0.76,0.78,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.973260869565218},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.742195652173915},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.506747826086956},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.168191304347827},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.786434782608694},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.627154347826089},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.452495652173914}]
[null,62,18.72,18.72,18.375652173913046,18.375652173913046,18.031304347826083,18.031304347826083,17.28,17.28,16.513043478260869,16.513043478260869,16.09434782608696,16.09434782608696,15.675652173913043,15.675652173913043,null,1.04,1.0208695652173914,1.0017391304347825,0.96,0.91739130434782612,0.89413043478260879,0.87086956521739134,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.72,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.375652173913046},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.031304347826083},17.28,16.513043478260869,16.09434782608696,15.675652173913043]
[null,57,18.727826086956522,18.727826086956522,18.379565217391303,18.379565217391303,18.031304347826083,18.031304347826083,17.28,17.28,16.513043478260869,16.513043478260869,16.09434782608696,16.09434782608696,15.675652173913043,15.675652173913043,null,1.0404347826086957,1.0210869565217391,1.0017391304347825,0.96,0.91739130434782612,0.89413043478260879,0.87086956521739134,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.727826086956522,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.379565217391303},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.031304347826083},17.28,16.513043478260869,16.09434782608696,15.675652173913043]

{"sheet":"N4A3_30","index":29,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":21.189705882352943},{"$f":"IF(AM8>C8,C8,AM8)","v":10.806750000000001},{"$f":"S8*$I$13","v":20.746323529411764},{"$f":"IF(AN8>E8,E8,AN8)","v":10.684356617647058},{"$f":"T8*$I$13","v":20.30294117647059},{"$f":"IF(AO8>G8,G8,AO8)","v":10.557529411764706},{"$f":"U8*$I$13","v":19.356617647058826},{"$f":"IF(AP8>I8,I8,AP8)","v":10.259007352941179},{"$f":"V8*$I$13","v":18.370588235294122},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7364117647058848},{"$f":"W8*$I$13","v":17.82463235294118},{"$f":"IF(AR8>M8,M8,AR8)","v":9.6253014705882372},{"$f":"X8*$I$13","v":17.278676470588238},{"$f":"IF(AS8>O8,O8,AS8)","v":9.5032720588235318},null,1.1772058823529412,1.1525735294117647,1.1279411764705882,1.0753676470588236,1.0205882352941178,0.99025735294117656,0.95992647058823533,0.51,0.51500000000000001,0.52,0.53,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.806750000000001},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.684356617647058},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.557529411764706},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.259007352941179},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7364117647058848},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.6253014705882372},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.5032720588235318}]
[null,67,19.548529411764704,13.488485294117645,19.131617647058825,{"$f":"IF(AN9>E9,E9,AN9)","v":13.296474264705882},18.714705882352941,{"$f":"IF(AO9>G9,G9,AO9)","v":13.100294117647058},{"$f":"U9*$I$13","v":17.814705882352943},{"$f":"IF(AP9>I9,I9,AP9)","v":12.826588235294118},16.875,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.487500000000001},16.358823529411765,{"$f":"IF(AR9>M9,M9,AR9)","v":12.269117647058824},15.84264705882353,{"$f":"IF(AS9>O9,O9,AS9)","v":12.040411764705883},null,1.0860294117647058,1.0628676470588236,1.0397058823529413,0.98970588235294121,0.9375,0.9088235294117647,0.8801470588235295,0.69,0.69499999999999995,0.7,0.72,0.74,0.75,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.488485294117645},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.296474264705882},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.100294117647058},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.826588235294118},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.487500000000001},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.269117647058824},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.040411764705883}]
[null,62,18.099264705882355,16.108345588235295,17.715441176470591,15.943897058823532,17.331617647058824,15.77177205882353,{"$f":"U10*$I$13","v":16.517647058823531},16.352470588235295,15.756617647058823,15.756617647058823,15.346323529411764,15.346323529411764,14.936029411764707,14.936029411764707,null,1.005514705882353,0.9841911764705884,0.96286764705882355,0.91764705882352948,0.87536764705882353,0.85257352941176467,0.82977941176470593,0.89,0.9,0.91,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.108345588235295,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.943897058823532},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.77177205882353},16.352470588235295,15.756617647058823,15.346323529411764,14.936029411764707]
[null,57,17.854411764705883,17.854411764705883,17.526838235294118,17.526838235294118,17.199264705882353,17.199264705882353,{"$f":"U11*$I$13","v":16.497794117647057},16.497794117647057,15.756617647058823,15.756617647058823,15.349632352941176,15.349632352941176,14.942647058823528,14.942647058823528,null,0.99191176470588238,0.97371323529411768,0.95551470588235288,0.91654411764705879,0.87536764705882353,0.85275735294117649,0.83014705882352935,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.854411764705883,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.526838235294118},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.199264705882353},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.497794117647057},15.756617647058823,15.349632352941176,14.942647058823528]
[1000,72,21.427941176470593,11.356808823529414,20.961397058823529,11.214347426470589,20.494852941176472,11.067220588235296,{"$f":"U12*$I$13","v":19.528676470588238},10.740772058823531,18.516176470588238,10.369058823529414,17.956985294117647,10.14569669117647,17.397794117647059,9.9167426470588236,null,1.1904411764705884,1.1645220588235294,1.1386029411764707,1.0849264705882353,1.0286764705882354,0.99761029411764701,0.96654411764705883,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.356808823529414},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.214347426470589},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.067220588235296},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.740772058823531},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.369058823529414},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.14569669117647},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.9167426470588236}]
[null,67,19.78014705882353,14.439507352941177,19.350000000000001,14.222250000000001,18.919852941176469,14.000691176470587,18,13.68,17.040441176470591,13.291544117647062,16.514338235294119,13.128898897058825,15.988235294117649,12.950470588235296,null,1.0988970588235294,1.0750000000000002,1.0511029411764705,1,0.94669117647058831,0.91746323529411766,0.88823529411764712,0.73,0.73499999999999999,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.439507352941177},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.222250000000001},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.000691176470587},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.68},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.291544117647062},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.128898897058825},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.950470588235296}]
[null,62,18.46985294117647,18.285154411764704,18.119117647058829,18.028522058823533,17.768382352941178,17.768382352941178,{"$f":"U14*$I$13","v":17.027205882352941},17.027205882352941,16.246323529411764,16.246323529411764,15.819485294117648,15.819485294117648,15.392647058823531,15.392647058823531,null,1.0261029411764706,1.0066176470588237,0.98713235294117652,0.94595588235294126,0.90257352941176472,0.8788602941176471,0.85514705882352948,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.285154411764704,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":18.028522058823533},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.768382352941178},17.027205882352941,16.246323529411764,15.819485294117648,15.392647058823531]
[null,57,18.456617647058824,18.456617647058824,18.112500000000001,18.112500000000001,17.768382352941178,17.768382352941178,17.027205882352941,17.027205882352941,16.252941176470589,16.252941176470589,15.822794117647058,15.822794117647058,15.392647058823531,15.392647058823531,null,1.0253676470588236,1.0062500000000001,0.98713235294117652,0.94595588235294126,0.90294117647058825,0.87904411764705881,0.85514705882352948,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.456617647058824,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18.112500000000001},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.768382352941178},17.027205882352941,16.252941176470589,15.822794117647058,15.392647058823531]
[1125,72,21.57352941176471,11.865441176470592,21.097058823529412,11.708867647058824,20.620588235294115,11.547529411764705,19.63455882352941,11.191698529411763,18.602205882352941,10.789279411764705,18.029779411764704,10.637569852941175,17.45735294117647,10.474411764705883,null,1.1985294117647061,1.1720588235294118,1.1455882352941176,1.0908088235294118,1.0334558823529412,1.0016544117647057,0.96985294117647058,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.865441176470592},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.708867647058824},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.547529411764705},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.191698529411763},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.789279411764705},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.637569852941175},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.474411764705883}]
[null,67,19.938970588235293,15.153617647058823,19.49889705882353,15.014150735294118,19.058823529411764,14.865882352941178,18.12573529411765,14.500588235294121,17.152941176470588,14.236941176470587,16.616911764705883,13.95820588235294,16.080882352941178,13.668750000000001,null,1.1077205882352941,1.0832720588235294,1.0588235294117647,1.0069852941176471,0.95294117647058829,0.9231617647058824,0.89338235294117652,0.76,0.77,0.78,0.8,0.83,0.84,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.153617647058823},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.014150735294118},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.865882352941178},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.500588235294121},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.236941176470587},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.95820588235294},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.668750000000001}]
[null,62,18.926470588235293,18.926470588235293,18.569117647058825,18.569117647058825,18.211764705882352,18.211764705882352,17.437500000000004,17.437500000000004,16.630147058823528,16.630147058823528,16.183455882352941,16.183455882352941,15.736764705882354,15.736764705882354,null,1.0514705882352942,1.0316176470588236,1.0117647058823529,0.96875000000000011,0.92389705882352935,0.89908088235294115,0.87426470588235305,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.926470588235293,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.569117647058825},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.211764705882352},17.437500000000004,16.630147058823528,16.183455882352941,15.736764705882354]
[null,57,18.926470588235293,18.926470588235293,18.569117647058825,18.569117647058825,18.211764705882352,18.211764705882352,17.437500000000004,17.437500000000004,16.630147058823528,16.630147058823528,16.183455882352941,16.183455882352941,15.736764705882354,15.736764705882354,null,1.0514705882352942,1.0316176470588236,1.0117647058823529,0.96875000000000011,0.92389705882352935,0.89908088235294115,0.87426470588235305,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.926470588235293,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.569117647058825},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.211764705882352},17.437500000000004,16.630147058823528,16.183455882352941,15.736764705882354]

{"sheet":"N4A3_36","index":30,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.418934911242605},{"$f":"IF(AM8>C8,C8,AM8)","v":11.137846153846155},{"$f":"S8*$I$13","v":20.960946745562129},{"$f":"IF(AN8>E8,E8,AN8)","v":11.004497041420118},{"$f":"T8*$I$13","v":20.50295857988166},{"$f":"IF(AO8>G8,G8,AO8)","v":10.86656804733728},{"$f":"U8*$I$13","v":19.523076923076921},{"$f":"IF(AP8>I8,I8,AP8)","v":10.542461538461538},{"$f":"V8*$I$13","v":18.473964497041418},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.16068047337278},{"$f":"W8*$I$13","v":17.906804733727814},{"$f":"IF(AR8>M8,M8,AR8)","v":9.9382766272189382},{"$f":"X8*$I$13","v":17.339644970414206},{"$f":"IF(AS8>O8,O8,AS8)","v":9.7102011834319555},null,1.1899408284023669,1.1644970414201183,1.13905325443787,1.0846153846153845,1.0263313609467455,0.9948224852071007,0.96331360946745581,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.137846153846155},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.004497041420118},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.86656804733728},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.542461538461538},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.16068047337278},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.9382766272189382},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.7102011834319555}]
[null,67,19.496449704142012,13.647514792899408,19.067751479289942,{"$f":"IF(AN9>E9,E9,AN9)","v":13.538103550295858},18.639053254437872,{"$f":"IF(AO9>G9,G9,AO9)","v":13.420118343195268},{"$f":"U9*$I$13","v":17.728402366863907},{"$f":"IF(AP9>I9,I9,AP9)","v":12.941733727810652},16.753846153846155,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.565384615384616},16.229289940828405,{"$f":"IF(AR9>M9,M9,AR9)","v":12.334260355029588},15.704733727810652,{"$f":"IF(AS9>O9,O9,AS9)","v":12.092644970414202},null,1.0831360946745563,1.0593195266272191,1.0355029585798818,0.98491124260355034,0.9307692307692309,0.90162721893491138,0.87248520710059174,0.7,0.71,0.72,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.647514792899408},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.538103550295858},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.420118343195268},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.941733727810652},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.565384615384616},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.334260355029588},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.092644970414202}]
[null,62,17.797633136094678,16.195846153846158,17.411538461538463,16.018615384615387,17.025443786982251,15.833662721893495,{"$f":"U10*$I$13","v":16.215976331360949},15.4051775147929,15.369230769230771,15.061846153846156,14.951183431952662,14.801671597633135,14.533136094674557,14.533136094674557,null,0.98875739644970428,0.96730769230769242,0.94585798816568056,0.90088757396449715,0.85384615384615392,0.83062130177514792,0.80739644970414204,0.91,0.92,0.93,0.95,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.195846153846158,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.018615384615387},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.833662721893495},15.4051775147929,15.061846153846156,14.801671597633135,14.533136094674557]
[null,57,17.334319526627219,17.334319526627219,17.022781065088758,17.022781065088758,16.711242603550296,16.711242603550296,{"$f":"U11*$I$13","v":16.040236686390536},16.040236686390536,15.32130177514793,15.32130177514793,14.927218934911245,14.927218934911245,14.533136094674557,14.533136094674557,null,0.96301775147928992,0.94571005917159756,0.92840236686390543,0.89112426035502967,0.85118343195266277,0.82928994082840246,0.80739644970414204,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.334319526627219,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.022781065088758},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.711242603550296},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.040236686390536},15.32130177514793,14.927218934911245,14.533136094674557]
[1200,72,21.781065088757398,11.761775147928995,21.304437869822483,11.504396449704142,20.827810650887578,11.247017751479293,{"$f":"U12*$I$13","v":19.810650887573967},10.895857988165682,18.729585798816572,10.675863905325444,18.141124260355031,10.431146449704142,17.552662721893494,10.180544378698226,null,1.2100591715976332,1.1835798816568046,1.1571005917159765,1.1005917159763314,1.0405325443786984,1.0078402366863906,0.97514792899408298,0.54,0.54,0.54,0.55000000000000004,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.761775147928995},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.504396449704142},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.247017751479293},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.895857988165682},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.675863905325444},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.431146449704142},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.180544378698226}]
[null,67,19.837278106508879,14.481213017751482,19.389940828402366,14.348556213017751,18.942603550295861,14.206952662721896,18,13.86,16.993491124260355,13.424857988165682,16.45295857988166,13.162366863905328,15.912426035502961,12.889065088757398,null,1.1020710059171599,1.0772189349112427,1.0523668639053256,1,0.94408284023668643,0.91405325443786989,0.88402366863905335,0.73,0.74,0.75,0.77,0.79,0.8,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.481213017751482},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.348556213017751},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.206952662721896},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.424857988165682},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.162366863905328},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.889065088757398}]
[null,62,18.207692307692305,17.29730769230769,17.8189349112426,17.106177514792897,17.430177514792899,16.907272189349111,{"$f":"U14*$I$13","v":16.636686390532546},16.636686390532546,15.885798816568048,15.885798816568048,15.467751479289944,15.467751479289944,15.049704142011835,15.049704142011835,null,1.0115384615384615,0.98994082840236675,0.96834319526627222,0.92426035502958581,0.88254437869822489,0.85931952662721911,0.83609467455621311,0.95,0.96,0.97,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.29730769230769,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.106177514792897},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.907272189349111},16.636686390532546,15.885798816568048,15.467751479289944,15.049704142011835]
[null,57,18.037278106508875,18.037278106508875,17.701775147928995,17.701775147928995,17.366272189349115,17.366272189349115,16.652662721893492,16.652662721893492,15.885798816568048,15.885798816568048,15.467751479289944,15.467751479289944,15.049704142011835,15.049704142011835,null,1.0020710059171598,0.98343195266272188,0.96479289940828405,0.92514792899408294,0.88254437869822489,0.85931952662721911,0.83609467455621311,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.037278106508875,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.701775147928995},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.366272189349115},16.652662721893492,15.885798816568048,15.467751479289944,15.049704142011835]
[1350,72,22.047337278106511,12.126035502958581,21.55473372781065,11.962877218934912,21.062130177514792,11.794792899408284,20.023668639053255,11.413491124260355,18.905325443786985,10.965088757396451,18.303550295857992,10.799094674556214,17.701775147928995,10.621065088757396,null,1.2248520710059172,1.1974852071005917,1.1701183431952662,1.1124260355029587,1.0502958579881658,1.016863905325444,0.98343195266272199,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.126035502958581},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.962877218934912},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.794792899408284},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.413491124260355},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.965088757396451},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.799094674556214},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.621065088757396}]
[null,67,20.087573964497043,15.266556213017752,19.629585798816571,15.11478106508876,19.171597633136095,14.953846153846154,18.207692307692305,14.566153846153846,17.179881656804735,14.259301775147929,16.628698224852073,14.051250000000001,16.077514792899411,13.826662721893493,null,1.1159763313609468,1.0905325443786984,1.0650887573964498,1.0115384615384615,0.95443786982248524,0.92381656804733736,0.89319526627218948,0.76,0.77,0.78,0.8,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.266556213017752},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.11478106508876},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.953846153846154},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.566153846153846},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.259301775147929},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":14.051250000000001},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.826662721893493}]
[null,62,18.585798816568047,18.585798816568047,18.247633136094677,18.247633136094677,17.909467455621304,17.909467455621304,17.158579881656806,17.158579881656806,16.349112426035504,16.349112426035504,15.909763313609469,15.909763313609469,15.470414201183434,15.470414201183434,null,1.0325443786982249,1.0137573964497042,0.9949704142011836,0.95325443786982256,0.90828402366863914,0.88387573964497046,0.85946745562130189,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.585798816568047,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.247633136094677},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.909467455621304},17.158579881656806,16.349112426035504,15.909763313609469,15.470414201183434]
[null,57,18.617751479289943,18.617751479289943,18.266272189349113,18.266272189349113,17.914792899408287,17.914792899408287,17.163905325443785,17.163905325443785,16.349112426035504,16.349112426035504,15.909763313609469,15.909763313609469,15.470414201183434,15.470414201183434,null,1.0343195266272192,1.014792899408284,0.99526627218934927,0.95355029585798812,0.90828402366863914,0.88387573964497046,0.85946745562130189,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.617751479289943,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.266272189349113},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.914792899408287},17.163905325443785,16.349112426035504,15.909763313609469,15.470414201183434]

{"sheet":"N4A3_42","index":31,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.310243902439023},{"$f":"IF(AM8>C8,C8,AM8)","v":11.294429268292683},{"$f":"S8*$I$13","v":20.842682926829266},{"$f":"IF(AN8>E8,E8,AN8)","v":11.046621951219512},{"$f":"T8*$I$13","v":20.375121951219512},{"$f":"IF(AO8>G8,G8,AO8)","v":10.798814634146343},{"$f":"U8*$I$13","v":19.382926829268293},{"$f":"IF(AP8>I8,I8,AP8)","v":10.466780487804879},{"$f":"V8*$I$13","v":18.342439024390245},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.088341463414636},{"$f":"W8*$I$13","v":17.782682926829267},{"$f":"IF(AR8>M8,M8,AR8)","v":9.8693890243902445},{"$f":"X8*$I$13","v":17.222926829268292},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6448390243902455},null,1.1839024390243902,1.1579268292682925,1.131951219512195,1.076829268292683,1.0190243902439025,0.98792682926829256,0.95682926829268289,0.53,0.53,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.294429268292683},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.046621951219512},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.798814634146343},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.466780487804879},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.088341463414636},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.8693890243902445},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6448390243902455}]
[null,67,19.545365853658538,13.877209756097562,19.112926829268293,{"$f":"IF(AN9>E9,E9,AN9)","v":13.66574268292683},18.680487804878048,{"$f":"IF(AO9>G9,G9,AO9)","v":13.449951219512194},{"$f":"U9*$I$13","v":17.76731707317073},{"$f":"IF(AP9>I9,I9,AP9)","v":13.147814634146339},16.801463414634146,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.60109756097561},16.285609756097561,{"$f":"IF(AR9>M9,M9,AR9)","v":12.458491463414633},15.769756097560975,{"$f":"IF(AS9>O9,O9,AS9)","v":12.300409756097562},null,1.0858536585365854,1.0618292682926829,1.0378048780487805,0.98707317073170731,0.93341463414634152,0.90475609756097564,0.87609756097560976,0.71,0.71499999999999997,0.72,0.74,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.877209756097562},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.66574268292683},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.449951219512194},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":13.147814634146339},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.60109756097561},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.458491463414633},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.300409756097562}]
[null,62,17.951707317073172,16.336053658536589,17.560975609756099,16.156097560975613,17.170243902439022,15.968326829268291,{"$f":"U10*$I$13","v":16.353658536585368},15.535975609756099,15.506341463414634,15.19621463414634,15.082682926829269,14.931856097560976,14.659024390243903,14.659024390243903,null,0.9973170731707317,0.97560975609756095,0.9539024390243902,0.90853658536585369,0.86146341463414633,0.83792682926829276,0.81439024390243908,0.91,0.92,0.93,0.95,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.336053658536589,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.156097560975613},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.968326829268291},15.535975609756099,15.19621463414634,14.931856097560976,14.659024390243903]
[null,57,17.477560975609759,17.477560975609759,17.159268292682928,17.159268292682928,16.840975609756097,16.840975609756097,{"$f":"U11*$I$13","v":16.164878048780487},16.164878048780487,15.444878048780488,15.444878048780488,15.054146341463413,15.054146341463413,14.66341463414634,14.66341463414634,null,0.97097560975609765,0.95329268292682934,0.93560975609756092,0.8980487804878049,0.85804878048780486,0.83634146341463411,0.81463414634146336,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.477560975609759,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.159268292682928},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.840975609756097},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.164878048780487},15.444878048780488,15.054146341463413,14.66341463414634]
[1400,72,21.621951219512194,11.675853658536585,21.136829268292679,11.519571951219511,20.651707317073168,11.358439024390243,{"$f":"U12*$I$13","v":19.619999999999997},10.9872,18.544390243902441,10.57030243902439,17.964878048780488,10.32980487804878,17.385365853658538,10.083512195121951,null,1.2012195121951219,1.1742682926829267,1.1473170731707316,1.0899999999999999,1.0302439024390244,0.99804878048780488,0.96585365853658545,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.675853658536585},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.519571951219511},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.358439024390243},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.9872},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.57030243902439},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.32980487804878},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.083512195121951}]
[null,67,19.848292682926832,14.687736585365856,19.400487804878047,14.453363414634145,18.952682926829269,14.214512195121952,18,13.86,17.00780487804878,13.436165853658537,16.476585365853659,13.263651219512195,15.945365853658537,13.075199999999999,null,1.1026829268292684,1.0778048780487803,1.0529268292682927,1,0.94487804878048787,0.91536585365853662,0.88585365853658538,0.74,0.745,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.687736585365856},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.453363414634145},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.214512195121952},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.436165853658537},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.263651219512195},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.075199999999999}]
[null,62,18.329268292682926,17.596097560975608,17.934146341463414,17.396121951219513,17.539024390243902,17.188243902439023,{"$f":"U14*$I$13","v":16.718048780487806},16.718048780487806,15.971707317073172,15.971707317073172,15.556829268292685,15.556829268292685,15.141951219512197,15.141951219512197,null,1.0182926829268293,0.99634146341463414,0.97439024390243911,0.92878048780487799,0.88731707317073172,0.86426829268292693,0.84121951219512203,0.96,0.97,0.98,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.596097560975608,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.396121951219513},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.188243902439023},16.718048780487806,15.971707317073172,15.556829268292685,15.141951219512197]
[null,57,18.149268292682926,18.149268292682926,17.809024390243902,17.809024390243902,17.468780487804878,17.468780487804878,16.744390243902441,16.744390243902441,15.97609756097561,15.97609756097561,15.559024390243902,15.559024390243902,15.141951219512197,15.141951219512197,null,1.0082926829268293,0.98939024390243901,0.97048780487804875,0.93024390243902444,0.88756097560975611,0.86439024390243901,0.84121951219512203,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.149268292682926,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.809024390243902},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.468780487804878},16.744390243902441,15.97609756097561,15.559024390243902,15.141951219512197]
[1575,72,21.854634146341464,12.238595121951221,21.354146341463412,12.065092682926826,20.853658536585364,11.886585365853657,19.79121951219512,11.478907317073169,18.689268292682929,11.026668292682928,18.094390243902442,10.856634146341465,17.499512195121952,10.67470243902439,null,1.2141463414634146,1.1863414634146341,1.1585365853658536,1.0995121951219511,1.0382926829268293,1.0052439024390245,0.97219512195121949,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.57999999999999996,0.59,0.6,0.61,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.238595121951221},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.065092682926826},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.886585365853657},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.478907317073169},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.026668292682928},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.856634146341465},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.67470243902439}]
[null,67,20.080975609756099,15.462351219512197,19.61780487804878,15.301887804878049,19.154634146341465,15.132160975609757,18.18,14.725800000000001,17.165853658536587,14.247658536585368,16.623658536585367,14.046991463414635,16.081463414634147,13.830058536585366,null,1.1156097560975611,1.0898780487804878,1.0641463414634147,1.01,0.95365853658536592,0.9235365853658537,0.89341463414634148,0.77,0.78,0.79,0.81,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.462351219512197},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.301887804878049},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.132160975609757},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.725800000000001},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.247658536585368},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":14.046991463414635},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.830058536585366}]
[null,62,18.698048780487806,18.511068292682928,18.333658536585368,18.241990243902443,17.969268292682926,17.969268292682926,17.209756097560977,17.209756097560977,16.397560975609757,16.397560975609757,15.958536585365854,15.958536585365854,15.519512195121951,15.519512195121951,null,1.0387804878048781,1.0185365853658537,0.99829268292682927,0.95609756097560983,0.91097560975609759,0.88658536585365855,0.8621951219512195,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.511068292682928,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.241990243902443},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.969268292682926},17.209756097560977,16.397560975609757,15.958536585365854,15.519512195121951]
[null,57,18.689268292682929,18.689268292682929,18.331463414634143,18.331463414634143,17.973658536585365,17.973658536585365,17.209756097560977,17.209756097560977,16.397560975609757,16.397560975609757,15.958536585365854,15.958536585365854,15.519512195121951,15.519512195121951,null,1.0382926829268293,1.0184146341463414,0.99853658536585366,0.95609756097560983,0.91097560975609759,0.88658536585365855,0.8621951219512195,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.689268292682929,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.331463414634143},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.973658536585365},17.209756097560977,16.397560975609757,15.958536585365854,15.519512195121951]

{"sheet":"N4A3_48","index":32,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.318260869565215},{"$f":"IF(AM8>C8,C8,AM8)","v":10.232765217391302},{"$f":"S8*$I$13","v":20.868260869565219},{"$f":"IF(AN8>E8,E8,AN8)","v":10.121106521739131},{"$f":"T8*$I$13","v":20.41826086956522},{"$f":"IF(AO8>G8,G8,AO8)","v":10.004947826086958},{"$f":"U8*$I$13","v":19.459565217391305},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7297826086956523},{"$f":"V8*$I$13","v":18.442173913043479},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.4055086956521752},{"$f":"W8*$I$13","v":17.896304347826089},{"$f":"IF(AR8>M8,M8,AR8)","v":9.216596739130436},{"$f":"X8*$I$13","v":17.350434782608698},{"$f":"IF(AS8>O8,O8,AS8)","v":9.0222260869565236},null,1.1843478260869564,1.1593478260869565,1.1343478260869566,1.0810869565217391,1.0245652173913045,0.99423913043478263,0.9639130434782609,0.48,0.48499999999999999,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.232765217391302},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.121106521739131},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.004947826086958},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7297826086956523},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.4055086956521752},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.216596739130436},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.0222260869565236}]
[null,67,19.486956521739131,12.666521739130436,19.062391304347827,{"$f":"IF(AN9>E9,E9,AN9)","v":12.581178260869565},18.637826086956526,{"$f":"IF(AO9>G9,G9,AO9)","v":12.487343478260874},{"$f":"U9*$I$13","v":17.741739130434784},{"$f":"IF(AP9>I9,I9,AP9)","v":12.064382608695654},16.798695652173912,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.759086956521738},16.291956521739131,{"$f":"IF(AR9>M9,M9,AR9)","v":11.567289130434782},15.78521739130435,{"$f":"IF(AS9>O9,O9,AS9)","v":11.365356521739132},null,1.0826086956521739,1.0590217391304348,1.0354347826086958,0.98565217391304361,0.93326086956521737,0.905108695652174,0.87695652173913052,0.65,0.66,0.67,0.68,0.7,0.71,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.666521739130436},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.581178260869565},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.487343478260874},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.064382608695654},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.759086956521738},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.567289130434782},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.365356521739132}]
[null,62,17.835652173913044,15.160304347826086,17.450217391304349,15.007186956521741,17.064782608695651,14.846360869565217,{"$f":"U10*$I$13","v":16.258695652173913},14.470239130434782,15.436956521739132,15.28258695652174,15.049565217391304,14.974317391304348,14.662173913043477,14.662173913043477,null,0.99086956521739122,0.96945652173913044,0.94804347826086954,0.90326086956521734,0.85760869565217401,0.83608695652173914,0.81456521739130427,0.85,0.86,0.87,0.89,0.99,0.995,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.160304347826086,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.007186956521741},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.846360869565217},14.470239130434782,15.28258695652174,14.974317391304348,14.662173913043477]
[null,57,17.432608695652171,17.432608695652171,17.117608695652173,17.117608695652173,16.802608695652175,16.802608695652175,{"$f":"U11*$I$13","v":16.133478260869566},16.133478260869566,15.425217391304349,15.425217391304349,15.043695652173914,15.043695652173914,14.662173913043477,14.662173913043477,null,0.96847826086956512,0.95097826086956516,0.9334782608695652,0.89630434782608692,0.85695652173913051,0.83576086956521745,0.81456521739130427,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.432608695652171,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.117608695652173},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.802608695652175},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.133478260869566},15.425217391304349,15.043695652173914,14.662173913043477]
[1600,72,21.654782608695655,10.827391304347827,21.187173913043477,10.699522826086955,20.719565217391306,10.566978260869567,{"$f":"U12*$I$13","v":19.729565217391308},10.259373913043481,18.676956521739132,9.8987869565217412,18.111521739130435,9.6896641304347835,17.546086956521741,9.4748869565217415,null,1.2030434782608697,1.1770652173913043,1.1510869565217392,1.0960869565217393,1.037608695652174,1.006195652173913,0.97478260869565225,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.827391304347827},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.699522826086955},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.566978260869567},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.259373913043481},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8987869565217412},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.6896641304347835},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.4748869565217415}]
[null,67,19.807826086956521,13.469321739130436,19.369565217391301,13.364999999999997,18.931304347826089,13.251913043478261,18,12.78,17.025652173913045,12.428726086956523,16.503260869565217,12.294929347826086,15.980869565217391,12.145460869565218,null,1.1004347826086955,1.076086956521739,1.0517391304347827,1,0.94586956521739129,0.91684782608695647,0.88782608695652177,0.68,0.69,0.7,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.469321739130436},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.364999999999997},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.251913043478261},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.78},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.428726086956523},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.294929347826086},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.145460869565218}]
[null,62,18.22695652173913,16.221991304347824,17.841521739130435,16.77103043478261,17.456086956521737,17.281526086956521,{"$f":"U14*$I$13","v":16.724347826086955},16.724347826086955,15.97304347826087,15.97304347826087,15.568043478260869,15.568043478260869,15.163043478260869,15.163043478260869,null,1.0126086956521738,0.99119565217391303,0.96978260869565214,0.92913043478260871,0.88739130434782609,0.86489130434782602,0.84239130434782605,0.89,0.94,0.99,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.221991304347824,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.77103043478261},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.281526086956521},16.724347826086955,15.97304347826087,15.568043478260869,15.163043478260869]
[null,57,18.105652173913047,18.105652173913047,17.771086956521742,17.771086956521742,17.436521739130434,17.436521739130434,16.728260869565219,16.728260869565219,15.97304347826087,15.97304347826087,15.568043478260869,15.568043478260869,15.163043478260869,15.163043478260869,null,1.0058695652173915,0.98728260869565232,0.96869565217391307,0.92934782608695654,0.88739130434782609,0.86489130434782602,0.84239130434782605,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.105652173913047,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.771086956521742},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.436521739130434},16.728260869565219,15.97304347826087,15.568043478260869,15.163043478260869]
[1800,72,21.897391304347828,11.38664347826087,21.41804347826087,11.137382608695653,20.938695652173912,10.888121739130435,19.917391304347824,10.556217391304347,18.841304347826089,10.362717391304349,18.260217391304348,10.134420652173914,17.679130434782607,9.9003130434782616,null,1.2165217391304348,1.1898913043478261,1.1632608695652173,1.1065217391304347,1.0467391304347826,1.0144565217391304,0.98217391304347823,0.52,0.52,0.52,0.53,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.38664347826087},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.137382608695653},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.888121739130435},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.556217391304347},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.362717391304349},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.134420652173914},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.9003130434782616}]
[null,67,20.03869565217391,14.227473913043475,19.588695652173914,14.103860869565217,19.138695652173912,13.971247826086955,18.187826086956523,13.640869565217393,17.189999999999998,13.236299999999998,16.65586956521739,13.074857608695652,16.121739130434783,12.897391304347828,null,1.1132608695652173,1.0882608695652174,1.0632608695652173,1.0104347826086957,0.95499999999999996,0.92532608695652174,0.89565217391304353,0.71,0.72,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.227473913043475},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.103860869565217},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":13.971247826086955},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.640869565217393},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.236299999999998},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.074857608695652},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.897391304347828}]
[null,62,18.649565217391302,18.649565217391302,18.299347826086958,18.299347826086958,17.94913043478261,17.94913043478261,17.205652173913045,17.205652173913045,16.411304347826086,16.411304347826086,15.986739130434785,15.986739130434785,15.56217391304348,15.56217391304348,null,1.036086956521739,1.0166304347826087,0.99717391304347824,0.9558695652173913,0.91173913043478261,0.88815217391304357,0.86456521739130443,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.649565217391302,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.299347826086958},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.94913043478261},17.205652173913045,16.411304347826086,15.986739130434785,15.56217391304348]
[null,57,18.653478260869566,18.653478260869566,18.303260869565221,18.303260869565221,17.95304347826087,17.95304347826087,17.205652173913045,17.205652173913045,16.415217391304349,16.415217391304349,15.988695652173911,15.988695652173911,15.56217391304348,15.56217391304348,null,1.0363043478260869,1.0168478260869567,0.99739130434782619,0.9558695652173913,0.91195652173913044,0.88826086956521733,0.86456521739130443,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.653478260869566,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.303260869565221},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.95304347826087},17.205652173913045,16.415217391304349,15.988695652173911,15.56217391304348]

{"sheet":"N4A3_60","index":33,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A3_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.224987128882784},{"$f":"IF(AM8>C8,C8,AM8)","v":10.82474343573022},{"$f":"S8*$I$13","v":20.769349579543505},{"$f":"IF(AN8>E8,E8,AN8)","v":10.592368285567188},{"$f":"T8*$I$13","v":20.313712030204222},{"$f":"IF(AO8>G8,G8,AO8)","v":10.359993135404153},{"$f":"U8*$I$13","v":19.334477432641151},{"$f":"IF(AP8>I8,I8,AP8)","v":10.053928264973399},{"$f":"V8*$I$13","v":18.290372404324696},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.6938973742920886},{"$f":"W8*$I$13","v":17.723528402265316},{"$f":"IF(AR8>M8,M8,AR8)","v":9.4820876952119448},{"$f":"X8*$I$13","v":17.156684400205936},{"$f":"IF(AS8>O8,O8,AS8)","v":9.2646095761112068},null,1.1791659516045991,1.1538527544190835,1.1285395572335679,1.0741376351467307,1.0161318002402608,0.98464046679251749,0.95314913334477425,0.51,0.51,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.82474343573022},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.592368285567188},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.359993135404153},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.053928264973399},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.6938973742920886},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.4820876952119448},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.2646095761112068}]
[null,67,19.510554316114636,13.267176934957954,19.088896516217609,{"$f":"IF(AN9>E9,E9,AN9)","v":13.075894113609063},18.667238716320576,{"$f":"IF(AO9>G9,G9,AO9)","v":12.880394714261197},{"$f":"U9*$I$13","v":17.762141753904238},{"$f":"IF(AP9>I9,I9,AP9)","v":12.611120645272008},16.801441565127853,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.265052342543331},16.282478119100738,{"$f":"IF(AR9>M9,M9,AR9)","v":12.049033808134546},15.763514673073622,{"$f":"IF(AS9>O9,O9,AS9)","v":11.822636004805217},null,1.083919684228591,1.0604942509009783,1.0370688175733653,0.98678565299467991,0.93341342028488072,0.90458211772781871,0.87575081517075681,0.68,0.68500000000000005,0.69,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.267176934957954},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.075894113609063},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.880394714261197},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.611120645272008},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.265052342543331},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.049033808134546},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.822636004805217}]
[null,62,17.959842114295519,15.804661060580056,17.575253131971852,15.641975287454949,17.190664149648189,15.471597734683371,{"$f":"U10*$I$13","v":16.375150163034149},15.065138149991418,15.528745495108975,14.597020765402435,15.1086322292775,14.655373262399175,14.688518963446025,14.688518963446025,null,0.99776900634975108,0.97640295177621406,0.95503689720267715,0.90973056461300827,0.86270808306160973,0.83936845718208331,0.81602883130255699,0.88,0.89,0.9,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.804661060580056,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.641975287454949},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.471597734683371},15.065138149991418,14.597020765402435,14.655373262399175,14.688518963446025]
[null,57,17.493392826497342,17.493392826497342,17.179852411189291,17.179852411189291,16.86631199588124,16.86631199588124,{"$f":"U11*$I$13","v":16.19289514329844},16.19289514329844,15.473142268748928,15.473142268748928,15.080830616097476,15.080830616097476,14.688518963446025,14.688518963446025,null,0.97185515702763003,0.95443624506607172,0.93701733310451341,0.89960528573880216,0.85961901493049597,0.83782392311652643,0.81602883130255699,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.493392826497342,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.179852411189291},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.86631199588124},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.19289514329844},15.473142268748928,15.080830616097476,14.688518963446025]
[2000,72,21.533893941994162,11.197624849836965,21.06435558606487,11.058786682684058,20.594817230135575,10.915253131971856,{"$f":"U12*$I$13","v":19.578513814999141},10.572397460099538,18.497339969109319,10.173536983010127,17.908872490132143,9.9394242320233399,17.320405011154968,9.6994268062467821,null,1.1963274412218978,1.1702419770036039,1.1441565127853097,1.0876952119443968,1.027629998283851,0.99493736056289683,0.96224472284194262,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.197624849836965},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.058786682684058},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.915253131971856},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.572397460099538},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.173536983010127},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9394242320233399},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6994268062467821}]
[null,67,19.816372061094903,14.06962416337738,19.377724386476746,13.951961558263257,18.93907671185859,13.825525999656771,18,13.32,17.005320061781362,13.094096447571649,16.46936674103312,12.846106058005834,15.933413420284881,12.587396602025056,null,1.1009095589497169,1.0765402436931526,1.0521709284365883,1,0.9447400034322978,0.91496481894628445,0.8851896344602711,0.71,0.72,0.73,0.74,0.77,0.78,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.06962416337738},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.951961558263257},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.825525999656771},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.094096447571649},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.846106058005834},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.587396602025056}]
[null,62,18.327441221898056,16.86124592414621,17.936674103312168,16.681106916080314,17.545906984726273,16.493152565642696,{"$f":"U14*$I$13","v":16.752016475030029},16.752016475030029,15.992105714776041,15.992105714776041,15.571992448944567,15.571992448944567,15.151879183113092,15.151879183113092,null,1.0181911789943365,0.99648189462845371,0.97477261026257067,0.93066758194611277,0.88845031748755787,0.86511069160803145,0.84177106572850513,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.86124592414621,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.681106916080314},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.493152565642696},16.752016475030029,15.992105714776041,15.571992448944567,15.151879183113092]
[null,57,18.14827527029346,18.14827527029346,17.814655912133173,17.814655912133173,17.481036553972885,17.481036553972885,16.761283679423371,16.761283679423371,15.992105714776041,15.992105714776041,15.571992448944567,15.571992448944567,15.151879183113092,15.151879183113092,null,1.0082375150163034,0.98970310622962065,0.9711686974429381,0.9311824266346318,0.88845031748755787,0.86511069160803145,0.84177106572850513,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.14827527029346,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.814655912133173},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.481036553972885},16.761283679423371,15.992105714776041,15.571992448944567,15.151879183113092]
[2250,72,21.75939591556547,11.750073794405354,21.275956753046167,11.595396430410162,20.792517590526856,11.435884674789772,19.748412562210397,11.059111034837823,18.636348035009437,10.622718379955378,18.030890681311138,10.45791659516046,17.425433327612833,10.281005663291571,null,1.2088553286425261,1.1819975973914536,1.1551398661403809,1.0971340312339111,1.0353526686116354,1.0017161489617299,0.96807962931182412,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.750073794405354},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.595396430410162},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.435884674789772},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.059111034837823},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.622718379955378},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.45791659516046},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.281005663291571}]
[null,67,20.032606830272865,14.82412905440192,19.583147417195811,14.687360562896858,19.133688004118756,14.541602883130254,18.169898747211256,14.17252102282478,17.150506263943711,13.72040501115497,16.600652136605458,13.529531491333447,16.050798009267204,13.322162347691778,null,1.1129226016818259,1.0879526342886561,1.0629826668954865,1.0094388192895143,0.95280590355242833,0.92225845203363654,0.89171100051484464,0.74,0.75,0.76,0.78,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.82412905440192},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.687360562896858},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.541602883130254},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.17252102282478},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.72040501115497},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.529531491333447},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.322162347691778}]
[null,62,18.67032778445169,18.67032778445169,18.321263085635834,18.321263085635834,17.972198386819976,17.972198386819976,17.212287626565985,17.212287626565985,16.402951776214174,16.402951776214174,15.959670499399346,15.959670499399346,15.516389222584518,15.516389222584518,null,1.0372404324695383,1.0178479492019907,0.99845546593444301,0.95623820147588801,0.91127509867856527,0.88664836107774148,0.86202162347691769,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.67032778445169,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.321263085635834},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.972198386819976},17.212287626565985,16.402951776214174,15.959670499399346,15.516389222584518]
[null,57,18.679594988845029,18.679594988845029,18.327441221898056,18.327441221898056,17.97528745495109,17.97528745495109,17.215376694697099,17.215376694697099,16.402951776214174,16.402951776214174,15.959670499399346,15.959670499399346,15.516389222584518,15.516389222584518,null,1.0377552771580572,1.0181911789943365,0.99862708083061602,0.95640981637206102,0.91127509867856527,0.88664836107774148,0.86202162347691769,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.679594988845029,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.327441221898056},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.97528745495109},17.215376694697099,16.402951776214174,15.959670499399346,15.516389222584518]

{"sheet":"N4A4_18","index":34,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.57},{"$f":"IF(AM8>C8,C8,AM8)","v":11.2164},{"$f":"S8*$I$13","v":21.045000000000002},{"$f":"IF(AN8>E8,E8,AN8)","v":11.048625000000001},{"$f":"T8*$I$13","v":20.52},{"$f":"IF(AO8>G8,G8,AO8)","v":10.8756},{"$f":"U8*$I$13","v":19.45},{"$f":"IF(AP8>I8,I8,AP8)","v":10.3085},{"$f":"V8*$I$13","v":18.329999999999998},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.8981999999999992},{"$f":"W8*$I$13","v":17.754999999999999},{"$f":"IF(AR8>M8,M8,AR8)","v":9.76525},{"$f":"X8*$I$13","v":17.18},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6208000000000009},null,1.1983333333333333,1.1691666666666667,1.1399999999999999,1.0805555555555555,1.0183333333333333,0.98638888888888887,0.95444444444444443,0.52,0.52500000000000002,0.53,0.53,0.54,0.55000000000000004,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.2164},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.048625000000001},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.8756},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.3085},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.8981999999999992},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.76525},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6208000000000009}]
[null,67,19.600000000000001,13.72,19.125,{"$f":"IF(AN9>E9,E9,AN9)","v":13.483124999999999},18.649999999999999,{"$f":"IF(AO9>G9,G9,AO9)","v":13.241499999999998},{"$f":"U9*$I$13","v":17.670000000000002},{"$f":"IF(AP9>I9,I9,AP9)","v":12.899100000000001},16.649999999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.320999999999998},16.125,{"$f":"IF(AR9>M9,M9,AR9)","v":12.174375},15.600000000000001,{"$f":"IF(AS9>O9,O9,AS9)","v":12.012000000000002},null,1.088888888888889,1.0625,1.036111111111111,0.9816666666666668,0.92499999999999993,0.89583333333333337,0.8666666666666667,0.7,0.70499999999999996,0.71,0.73,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.72},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.483124999999999},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.241499999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.899100000000001},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.320999999999998},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.174375},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.012000000000002}]
[null,62,17.82,16.038,17.39,15.824900000000001,16.96,15.603200000000001,{"$f":"U10*$I$13","v":16.079999999999998},15.275999999999998,15.18,14.724599999999999,14.734999999999999,14.513974999999999,14.29,14.29,null,0.99,0.96611111111111114,0.94222222222222229,0.8933333333333332,0.84333333333333327,0.81861111111111107,0.79388888888888887,0.9,0.91,0.92,0.95,0.97,0.98499999999999999,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.038,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.824900000000001},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.603200000000001},15.275999999999998,14.724599999999999,14.513974999999999,14.29]
[null,57,17.16,17.16,16.824999999999999,16.824999999999999,16.489999999999998,16.489999999999998,{"$f":"U11*$I$13","v":15.79},15.79,15.06,15.06,14.675000000000001,14.675000000000001,14.29,14.29,null,0.95333333333333337,0.93472222222222223,0.91611111111111099,0.87722222222222213,0.83666666666666667,0.81527777777777777,0.79388888888888887,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.16,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.824999999999999},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.489999999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.79},15.06,14.675000000000001,14.29]
[600,72,22.010000000000005,11.665300000000004,21.465000000000003,11.483775000000003,20.92,11.296800000000001,{"$f":"U12*$I$13","v":19.79},10.884500000000001,18.62,10.427200000000001,18.020000000000003,10.271400000000003,17.420000000000002,10.1036,null,1.222777777777778,1.1925000000000001,1.1622222222222223,1.0994444444444444,1.0344444444444445,1.0011111111111113,0.96777777777777785,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.57000000000000006,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.665300000000004},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.483775000000003},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.296800000000001},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.884500000000001},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.427200000000001},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.271400000000003},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.1036}]
[null,67,20.03,14.6219,19.53,14.35455,19.03,14.0822,18,13.68,16.940000000000001,13.213200000000002,16.39,13.030050000000001,15.84,12.830400000000001,null,1.1127777777777779,1.085,1.0572222222222223,1,0.94111111111111123,0.91055555555555556,0.88,0.73,0.73499999999999999,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.6219},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.35455},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.0822},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.68},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.213200000000002},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.030050000000001},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.830400000000001}]
[null,62,18.27,17.3565,17.824999999999999,17.111999999999998,17.38,16.858599999999999,{"$f":"U14*$I$13","v":16.5},16.335000000000001,15.7,15.7,15.279999999999998,15.279999999999998,14.86,14.86,null,1.0149999999999999,0.9902777777777777,0.9655555555555555,0.91666666666666663,0.87222222222222223,0.8488888888888888,0.82555555555555549,0.95,0.96,0.97,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.3565,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.111999999999998},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.858599999999999},16.335000000000001,15.7,15.279999999999998,14.86]
[null,57,17.96,17.96,17.594999999999999,17.594999999999999,17.23,17.23,16.48,16.48,15.7,15.7,15.285,15.285,14.869999999999997,14.869999999999997,null,0.99777777777777787,0.97749999999999992,0.9572222222222222,0.91555555555555557,0.87222222222222223,0.84916666666666663,0.82611111111111102,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.96,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.594999999999999},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.23},16.48,15.7,15.285,14.869999999999997]
[675,72,22.34,12.287000000000001,21.769999999999996,12.082349999999998,21.2,11.872,20.03,11.4171,18.829999999999998,11.109699999999998,18.204999999999998,10.831974999999998,17.579999999999998,10.547999999999998,null,1.2411111111111111,1.2094444444444443,1.1777777777777778,1.1127777777777779,1.046111111111111,1.0113888888888889,0.97666666666666657,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.59,0.59499999999999997,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.287000000000001},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.082349999999998},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.872},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.4171},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.109699999999998},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.831974999999998},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.547999999999998}]
[null,67,20.350000000000001,15.466000000000001,19.829999999999998,15.2691,19.309999999999995,15.061799999999996,18.25,14.600000000000001,17.149999999999999,14.062999999999999,16.585000000000001,13.848475000000001,16.02,13.616999999999999,null,1.1305555555555555,1.1016666666666666,1.0727777777777776,1.0138888888888888,0.95277777777777772,0.92138888888888892,0.89,0.76,0.77,0.78,0.8,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.466000000000001},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.2691},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.061799999999996},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.600000000000001},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.062999999999999},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.848475000000001},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.616999999999999}]
[null,62,18.68,18.493199999999998,18.27,18.178650000000001,17.86,17.86,17.059999999999999,17.059999999999999,16.22,16.22,15.774999999999999,15.774999999999999,15.33,15.33,null,1.0377777777777777,1.0149999999999999,0.99222222222222223,0.94777777777777772,0.90111111111111108,0.87638888888888877,0.85166666666666668,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.493199999999998,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.178650000000001},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.86},17.059999999999999,16.22,15.774999999999999,15.33]
[null,57,18.63,18.63,18.244999999999997,18.244999999999997,17.86,17.86,17.059999999999999,17.059999999999999,16.22,16.22,15.774999999999999,15.774999999999999,15.33,15.33,null,1.0349999999999999,1.013611111111111,0.99222222222222223,0.94777777777777772,0.90111111111111108,0.87638888888888877,0.85166666666666668,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.63,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.244999999999997},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.86},17.059999999999999,16.22,15.774999999999999,15.33]

{"sheet":"N4A4_24","index":35,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.468103448275862},{"$f":"IF(AM8>C8,C8,AM8)","v":10.734051724137931},{"$f":"S8*$I$13","v":20.99094827586207},{"$f":"IF(AN8>E8,E8,AN8)","v":10.495474137931035},{"$f":"T8*$I$13","v":20.513793103448275},{"$f":"IF(AO8>G8,G8,AO8)","v":10.256896551724138},{"$f":"U8*$I$13","v":19.520689655172415},{"$f":"IF(AP8>I8,I8,AP8)","v":9.9555517241379317},{"$f":"V8*$I$13","v":18.465517241379313},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.602068965517244},{"$f":"W8*$I$13","v":17.899137931034485},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3970474137931053},{"$f":"X8*$I$13","v":17.332758620689656},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1863620689655185},null,1.1926724137931035,1.1661637931034483,1.1396551724137931,1.0844827586206898,1.0258620689655173,0.99439655172413799,0.96293103448275863,0.5,0.5,0.5,0.51,0.52,0.52500000000000002,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.734051724137931},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.495474137931035},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.256896551724138},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.9555517241379317},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.602068965517244},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3970474137931053},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1863620689655185}]
[null,67,19.489655172413798,13.058068965517245,19.047413793103452,{"$f":"IF(AN9>E9,E9,AN9)","v":12.857004310344831},18.605172413793106,{"$f":"IF(AO9>G9,G9,AO9)","v":12.651517241379313},{"$f":"U9*$I$13","v":17.689655172413794},{"$f":"IF(AP9>I9,I9,AP9)","v":12.205862068965518},16.71206896551724,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.865568965517239},16.188362068965517,{"$f":"IF(AR9>M9,M9,AR9)","v":11.655620689655173},15.664655172413793,{"$f":"IF(AS9>O9,O9,AS9)","v":11.435198275862069},null,1.0827586206896553,1.0581896551724139,1.0336206896551725,0.98275862068965525,0.92844827586206891,0.89935344827586217,0.8702586206896552,0.67,0.67500000000000004,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.058068965517245},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.857004310344831},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.651517241379313},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.205862068965518},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.865568965517239},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.655620689655173},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.435198275862069}]
[null,62,17.751724137931035,15.26648275862069,17.35603448275862,15.099749999999998,16.960344827586205,14.925103448275861,{"$f":"U10*$I$13","v":16.130172413793105},14.678456896551726,15.276724137931037,14.207353448275866,14.85387931034483,14.333993534482762,14.431034482758623,14.431034482758623,null,0.98620689655172411,0.96422413793103445,0.9422413793103448,0.89612068965517244,0.84870689655172427,0.82521551724137943,0.80172413793103459,0.86,0.87,0.88,0.91,0.93,0.96500000000000008,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.26648275862069,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.099749999999998},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.925103448275861},14.678456896551726,14.207353448275866,14.333993534482762,14.431034482758623]
[null,57,17.231896551724141,17.231896551724141,16.913793103448278,16.913793103448278,16.595689655172414,16.595689655172414,{"$f":"U11*$I$13","v":15.92844827586207},15.92844827586207,15.206896551724141,15.206896551724141,14.818965517241381,14.818965517241381,14.431034482758623,14.431034482758623,null,0.95732758620689662,0.93965517241379315,0.92198275862068968,0.88491379310344831,0.84482758620689669,0.82327586206896564,0.80172413793103459,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.231896551724141,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.913793103448278},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.595689655172414},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.92844827586207},15.206896551724141,14.818965517241381,14.431034482758623]
[800,72,21.887068965517241,11.162405172413793,21.39051724137931,11.016116379310345,20.893965517241377,10.864862068965516,{"$f":"U12*$I$13","v":19.846551724137932},10.518672413793105,18.752586206896556,10.126396551724142,18.16293103448276,9.8987974137931047,17.573275862068964,9.6653017241379313,null,1.215948275862069,1.1883620689655172,1.1607758620689654,1.1025862068965517,1.0418103448275864,1.0090517241379311,0.9762931034482758,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.162405172413793},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.016116379310345},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.864862068965516},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.518672413793105},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.126396551724142},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8987974137931047},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6653017241379313}]
[null,67,19.877586206896556,13.914310344827589,19.415948275862068,13.688243534482757,18.954310344827586,13.457560344827586,18,13.14,16.991379310344826,12.743534482758619,16.448275862068968,12.58293103448276,15.905172413793105,12.406034482758622,null,1.1043103448275864,1.0786637931034482,1.0530172413793104,1,0.94396551724137923,0.91379310344827591,0.88362068965517249,0.7,0.70499999999999996,0.71,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.914310344827589},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.688243534482757},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.457560344827586},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.743534482758619},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.58293103448276},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.406034482758622}]
[null,62,18.186206896551727,16.549448275862073,17.782758620689659,16.360137931034487,17.379310344827584,16.162758620689655,{"$f":"U14*$I$13","v":16.572413793103447},16.572413793103447,15.819827586206898,15.819827586206898,15.404741379310346,15.404741379310346,14.989655172413794,14.989655172413794,null,1.010344827586207,0.98793103448275876,0.96551724137931028,0.92068965517241375,0.87887931034482769,0.85581896551724146,0.83275862068965523,0.91,0.92,0.93,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.549448275862073,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.360137931034487},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.162758620689655},16.572413793103447,15.819827586206898,15.404741379310346,14.989655172413794]
[null,57,17.976724137931036,17.976724137931036,17.639224137931034,17.639224137931034,17.301724137931036,17.301724137931036,16.580172413793104,16.580172413793104,15.819827586206898,15.819827586206898,15.404741379310346,15.404741379310346,14.989655172413794,14.989655172413794,null,0.99870689655172429,0.97995689655172413,0.9612068965517242,0.92112068965517246,0.87887931034482769,0.85581896551724146,0.83275862068965523,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.976724137931036,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.639224137931034},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.301724137931036},16.580172413793104,15.819827586206898,15.404741379310346,14.989655172413794]
[900,72,22.197413793103447,11.764629310344828,21.681465517241381,11.59958405172414,21.165517241379312,11.42937931034483,20.087068965517243,11.047887931034484,18.954310344827586,10.614413793103449,18.349137931034484,10.367262931034482,17.743965517241381,10.114060344827587,null,1.2331896551724137,1.2045258620689656,1.1758620689655173,1.1159482758620691,1.0530172413793104,1.0193965517241379,0.98577586206896561,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.764629310344828},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.59958405172414},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.42937931034483},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.047887931034484},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.614413793103449},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.367262931034482},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.114060344827587}]
[null,67,20.164655172413795,14.720198275862071,19.695258620689653,14.476015086206894,19.225862068965519,14.227137931034484,18.232758620689655,13.856896551724137,17.193103448275863,13.582551724137932,16.638362068965517,13.393881465517239,16.083620689655174,13.188568965517241,null,1.1202586206896552,1.0941810344827585,1.0681034482758622,1.0129310344827587,0.95517241379310347,0.92435344827586208,0.89353448275862069,0.73,0.73499999999999999,0.74,0.76,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.720198275862071},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.476015086206894},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.227137931034484},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.856896551724137},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.582551724137932},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.393881465517239},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.188568965517241}]
[null,62,18.605172413793106,18.605172413793106,18.244396551724137,18.244396551724137,17.883620689655174,17.883620689655174,17.123275862068965,17.123275862068965,16.316379310344828,16.316379310344828,15.878017241379311,15.878017241379311,15.439655172413792,15.439655172413792,null,1.0336206896551725,1.0135775862068965,0.99353448275862077,0.95129310344827589,0.90646551724137936,0.8821120689655173,0.85775862068965514,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.605172413793106,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.244396551724137},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.883620689655174},17.123275862068965,16.316379310344828,15.878017241379311,15.439655172413792]
[null,57,18.605172413793106,18.605172413793106,18.244396551724137,18.244396551724137,17.883620689655174,17.883620689655174,17.123275862068965,17.123275862068965,16.316379310344828,16.316379310344828,15.878017241379311,15.878017241379311,15.439655172413792,15.439655172413792,null,1.0336206896551725,1.0135775862068965,0.99353448275862077,0.95129310344827589,0.90646551724137936,0.8821120689655173,0.85775862068965514,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.605172413793106,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.244396551724137},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.883620689655174},17.123275862068965,16.316379310344828,15.878017241379311,15.439655172413792]

{"sheet":"N4A4_30","index":36,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":21.302068965517243},{"$f":"IF(AM8>C8,C8,AM8)","v":10.651034482758622},{"$f":"S8*$I$13","v":20.839655172413796},{"$f":"IF(AN8>E8,E8,AN8)","v":10.524025862068967},{"$f":"T8*$I$13","v":20.377241379310345},{"$f":"IF(AO8>G8,G8,AO8)","v":10.392393103448276},{"$f":"U8*$I$13","v":19.390344827586205},{"$f":"IF(AP8>I8,I8,AP8)","v":10.082979310344827},{"$f":"V8*$I$13","v":18.366206896551724},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7340896551724132},{"$f":"W8*$I$13","v":17.810689655172414},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5287189655172426},{"$f":"X8*$I$13","v":17.255172413793105},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3177931034482775},null,1.183448275862069,1.1577586206896553,1.1320689655172413,1.0772413793103448,1.0203448275862068,0.98948275862068968,0.95862068965517244,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.651034482758622},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.524025862068967},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.392393103448276},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.082979310344827},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7340896551724132},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5287189655172426},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3177931034482775}]
[null,67,19.520689655172411,13.078862068965517,19.089310344827584,{"$f":"IF(AN9>E9,E9,AN9)","v":12.980731034482757},18.657931034482758,{"$f":"IF(AO9>G9,G9,AO9)","v":12.873972413793101},{"$f":"U9*$I$13","v":17.745517241379311},{"$f":"IF(AP9>I9,I9,AP9)","v":12.421862068965517},16.783448275862071,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.08408275862069},16.268275862068965,{"$f":"IF(AR9>M9,M9,AR9)","v":11.875841379310344},15.753103448275862,{"$f":"IF(AS9>O9,O9,AS9)","v":11.657296551724137},null,1.0844827586206895,1.0605172413793102,1.036551724137931,0.9858620689655172,0.9324137931034483,0.9037931034482759,0.8751724137931034,0.67,0.67999999999999994,0.69,0.7,0.72,0.73,0.74,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.078862068965517},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.980731034482757},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.873972413793101},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.421862068965517},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.08408275862069},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.875841379310344},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.657296551724137}]
[null,62,17.888275862068966,15.562799999999999,17.497241379310342,15.397572413793101,17.106206896551722,15.224524137931033,{"$f":"U10*$I$13","v":16.286896551724137},14.821075862068966,15.430344827586207,14.504524137931034,14.99896551724138,14.548996551724139,14.56758620689655,14.56758620689655,null,0.99379310344827587,0.97206896551724131,0.95034482758620686,0.90482758620689652,0.85724137931034483,0.83327586206896553,0.80931034482758613,0.87,0.88,0.89,0.91,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.562799999999999,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.397572413793101},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.224524137931033},14.821075862068966,14.504524137931034,14.548996551724139,14.56758620689655]
[null,57,17.379310344827587,17.379310344827587,17.062758620689657,17.062758620689657,16.746206896551726,16.746206896551726,{"$f":"U11*$I$13","v":16.069655172413793},16.069655172413793,15.355862068965516,15.355862068965516,14.964827586206896,14.964827586206896,14.573793103448276,14.573793103448276,null,0.96551724137931039,0.94793103448275873,0.93034482758620696,0.89275862068965517,0.85310344827586204,0.83137931034482759,0.80965517241379314,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.379310344827587,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.062758620689657},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.746206896551726},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.069655172413793},15.355862068965516,14.964827586206896,14.573793103448276]
[1000,72,21.649655172413794,11.257820689655173,21.165517241379312,11.006068965517242,20.681379310344827,10.75431724137931,{"$f":"U12*$I$13","v":19.651034482758622},10.41504827586207,18.595862068965516,10.04176551724138,18.021724137931038,9.9119482758620716,17.447586206896553,9.7706482758620705,null,1.2027586206896552,1.1758620689655173,1.1489655172413793,1.0917241379310345,1.0331034482758621,1.0012068965517242,0.96931034482758616,0.52,0.52,0.52,0.53,0.54,0.55000000000000004,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.257820689655173},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.006068965517242},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.75431724137931},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.41504827586207},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.04176551724138},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9119482758620716},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7706482758620705}]
[null,67,19.849655172413794,13.894758620689656,19.399655172413794,13.773755172413793,18.949655172413795,13.643751724137932,18,13.14,17.006896551724139,12.755172413793105,16.476206896551727,12.604298275862071,15.945517241379312,12.437503448275864,null,1.1027586206896551,1.0777586206896552,1.0527586206896553,1,0.94482758620689655,0.91534482758620694,0.88586206896551734,0.7,0.71,0.72,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.894758620689656},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.773755172413793},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.643751724137932},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.755172413793105},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.604298275862071},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.437503448275864}]
[null,62,18.273103448275862,16.628524137931034,17.875862068965517,16.445793103448278,17.478620689655173,16.255117241379313,{"$f":"U14*$I$13","v":16.640689655172412},16.640689655172412,15.902068965517241,15.902068965517241,15.486206896551726,15.486206896551726,15.070344827586206,15.070344827586206,null,1.0151724137931035,0.99310344827586206,0.9710344827586207,0.92448275862068963,0.88344827586206898,0.86034482758620701,0.83724137931034481,0.91,0.92,0.93,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.628524137931034,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.445793103448278},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.255117241379313},16.640689655172412,15.902068965517241,15.486206896551726,15.070344827586206]
[null,57,18.062068965517245,18.062068965517245,17.723793103448276,17.723793103448276,17.385517241379311,17.385517241379311,16.665517241379312,16.665517241379312,15.902068965517241,15.902068965517241,15.486206896551726,15.486206896551726,15.070344827586206,15.070344827586206,null,1.0034482758620691,0.98465517241379308,0.9658620689655173,0.92586206896551726,0.88344827586206898,0.86034482758620701,0.83724137931034481,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.062068965517245,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.723793103448276},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.385517241379311},16.665517241379312,15.902068965517241,15.486206896551726,15.070344827586206]
[1125,72,21.891724137931039,11.602613793103451,21.395172413793102,11.44641724137931,20.898620689655175,11.285255172413795,19.837241379310342,10.910482758620688,18.757241379310344,10.504055172413793,18.167586206896551,10.355524137931036,17.577931034482759,10.1952,null,1.2162068965517243,1.1886206896551723,1.1610344827586208,1.1020689655172413,1.0420689655172413,1.0093103448275862,0.97655172413793101,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.57000000000000006,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.602613793103451},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.44641724137931},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.285255172413795},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.910482758620688},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.504055172413793},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.355524137931036},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.1952}]
[null,67,20.085517241379311,14.662427586206896,19.623103448275863,14.521096551724138,19.160689655172416,14.370517241379311,18.18,13.9986,17.168275862068967,13.562937931034485,16.625172413793102,13.383263793103445,16.082068965517241,13.187296551724137,null,1.1158620689655172,1.0901724137931035,1.0644827586206898,1.01,0.95379310344827584,0.92362068965517241,0.89344827586206899,0.73,0.74,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.662427586206896},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.521096551724138},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.370517241379311},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.9986},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.562937931034485},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.383263793103445},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.187296551724137}]
[null,62,18.633103448275865,17.70144827586207,18.266896551724138,17.810224137931034,17.900689655172414,17.900689655172414,17.14344827586207,17.14344827586207,16.336551724137934,16.336551724137934,15.902068965517241,15.902068965517241,15.467586206896552,15.467586206896552,null,1.0351724137931035,1.0148275862068965,0.99448275862068969,0.95241379310344831,0.90758620689655178,0.88344827586206898,0.85931034482758628,0.95,0.97499999999999998,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.70144827586207,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.810224137931034},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.900689655172414},17.14344827586207,16.336551724137934,15.902068965517241,15.467586206896552]
[null,57,18.614482758620689,18.614482758620689,18.257586206896548,18.257586206896548,17.900689655172414,17.900689655172414,17.14344827586207,17.14344827586207,16.336551724137934,16.336551724137934,15.902068965517241,15.902068965517241,15.467586206896552,15.467586206896552,null,1.0341379310344827,1.0143103448275861,0.99448275862068969,0.95241379310344831,0.90758620689655178,0.88344827586206898,0.85931034482758628,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.614482758620689,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.257586206896548},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.900689655172414},17.14344827586207,16.336551724137934,15.902068965517241,15.467586206896552]

{"sheet":"N4A4_36","index":37,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.534636871508383},{"$f":"IF(AM8>C8,C8,AM8)","v":11.198011173184359},{"$f":"S8*$I$13","v":21.05446927374302},{"$f":"IF(AN8>E8,E8,AN8)","v":11.053596368715086},{"$f":"T8*$I$13","v":20.574301675977654},{"$f":"IF(AO8>G8,G8,AO8)","v":10.904379888268158},{"$f":"U8*$I$13","v":19.568715083798885},{"$f":"IF(AP8>I8,I8,AP8)","v":10.567106145251399},{"$f":"V8*$I$13","v":18.492737430167601},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.171005586592182},{"$f":"W8*$I$13","v":17.912011173184357},{"$f":"IF(AR8>M8,M8,AR8)","v":9.9411662011173192},{"$f":"X8*$I$13","v":17.331284916201117},{"$f":"IF(AS8>O8,O8,AS8)","v":9.7055195530726266},null,1.1963687150837989,1.1696927374301678,1.1430167597765364,1.0871508379888271,1.0273743016759778,0.99511173184357549,0.96284916201117321,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.198011173184359},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":11.053596368715086},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.904379888268158},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.567106145251399},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.171005586592182},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.9411662011173192},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.7055195530726266}]
[null,67,19.523463687150837,13.666424581005586,19.07849162011173,{"$f":"IF(AN9>E9,E9,AN9)","v":13.545729050279329},18.633519553072627,{"$f":"IF(AO9>G9,G9,AO9)","v":13.416134078212291},{"$f":"U9*$I$13","v":17.698324022346373},{"$f":"IF(AP9>I9,I9,AP9)","v":12.919776536312852},16.702793296089386,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.52709497206704},16.164804469273744,{"$f":"IF(AR9>M9,M9,AR9)","v":12.285251396648045},15.626815642458102,{"$f":"IF(AS9>O9,O9,AS9)","v":12.032648044692738},null,1.0846368715083798,1.0599162011173184,1.035195530726257,0.98324022346368734,0.9279329608938548,0.89804469273743015,0.86815642458100561,0.7,0.71,0.72,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.666424581005586},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.545729050279329},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.416134078212291},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.919776536312852},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.52709497206704},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.285251396648045},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.032648044692738}]
[null,62,17.768715083798885,16.169530726256987,17.36648044692738,15.97716201117319,16.964245810055868,15.776748603351958,{"$f":"U10*$I$13","v":16.124581005586595},15.318351955307264,15.244692737430169,14.939798882681565,14.807262569832403,14.659189944134079,14.369832402234636,14.369832402234636,null,0.98715083798882697,0.9648044692737433,0.94245810055865931,0.89581005586592188,0.84692737430167608,0.82262569832402244,0.79832402234636868,0.91,0.92,0.93,0.95,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.169530726256987,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.97716201117319},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.776748603351958},15.318351955307264,14.939798882681565,14.659189944134079,14.369832402234636]
[null,57,17.225698324022346,17.225698324022346,16.903910614525142,16.903910614525142,16.582122905027934,16.582122905027934,{"$f":"U11*$I$13","v":15.903351955307263},15.903351955307263,15.169273743016761,15.169273743016761,14.769553072625699,14.769553072625699,14.369832402234636,14.369832402234636,null,0.9569832402234637,0.93910614525139668,0.92122905027932955,0.88351955307262575,0.84273743016759783,0.82053072625698331,0.79832402234636868,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.225698324022346,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.903910614525142},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.582122905027934},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.903351955307263},15.169273743016761,14.769553072625699,14.369832402234636]
[1200,72,21.951955307262569,11.854055865921788,21.451675977653629,11.691163407821229,20.951396648044692,11.523268156424582,{"$f":"U12*$I$13","v":19.900558659217879},10.945307262569834,18.784357541899443,10.707083798882682,18.181005586592178,10.454078212290502,17.577653631284917,10.195039106145252,null,1.2195530726256982,1.1917597765363128,1.1639664804469274,1.1055865921787711,1.0435754189944135,1.0100558659217878,0.97653631284916209,0.54,0.54500000000000004,0.55000000000000004,0.55000000000000004,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.854055865921788},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.691163407821229},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.523268156424582},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.945307262569834},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.707083798882682},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.454078212290502},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.195039106145252}]
[null,67,19.900558659217879,14.527407821229051,19.437988826815641,14.384111731843573,18.97541899441341,14.231564245810057,18,13.86,16.96927374301676,13.405726256983241,16.416201117318437,13.21504189944134,15.863128491620113,13.007765363128492,null,1.1055865921787711,1.0798882681564246,1.0541899441340783,1,0.94273743016759781,0.91201117318435754,0.88128491620111737,0.73,0.74,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.527407821229051},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.384111731843573},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.231564245810057},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.405726256983241},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.21504189944134},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.007765363128492}]
[null,62,18.191061452513971,17.281508379888272,17.78379888268157,17.072446927374305,17.376536312849165,16.855240223463689,{"$f":"U14*$I$13","v":16.5268156424581},16.5268156424581,15.762569832402237,15.762569832402237,15.340223463687153,15.340223463687153,14.91787709497207,14.91787709497207,null,1.010614525139665,0.98798882681564271,0.9653631284916202,0.91815642458100555,0.87569832402234649,0.85223463687150847,0.82877094972067056,0.95,0.96,0.97,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.281508379888272,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.072446927374305},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.855240223463689},16.5268156424581,15.762569832402237,15.340223463687153,14.91787709497207]
[null,57,17.959776536312848,17.959776536312848,17.617877094972069,17.617877094972069,17.275977653631287,17.275977653631287,16.546927374301678,16.546927374301678,15.76759776536313,15.76759776536313,15.342737430167599,15.342737430167599,14.91787709497207,14.91787709497207,null,0.99776536312849162,0.97877094972067047,0.9597765363128492,0.91927374301675979,0.87597765363128499,0.85237430167597772,0.82877094972067056,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.959776536312848,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.617877094972069},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.275977653631287},16.546927374301678,15.76759776536313,15.342737430167599,14.91787709497207]
[1350,72,22.258659217877099,12.242262569832405,21.743296089385478,12.067529329608941,21.22793296089386,11.887642458100563,20.141899441340783,11.480882681564246,18.990502793296091,11.014491620111732,18.372067039106149,10.839519553072627,17.753631284916203,10.652178770949721,null,1.23659217877095,1.2079608938547488,1.1793296089385477,1.1189944134078214,1.055027932960894,1.0206703910614527,0.98631284916201134,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.242262569832405},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.067529329608941},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.887642458100563},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.480882681564246},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.014491620111732},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.839519553072627},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.652178770949721}]
[null,67,20.182122905027931,15.338413407821228,19.704469273743015,15.172441340782122,19.226815642458103,14.996916201117321,18.226256983240226,14.581005586592182,17.170391061452513,14.07972067039106,16.602234636871508,13.945877094972065,16.034078212290503,13.789307262569832,null,1.1212290502793296,1.0946927374301676,1.0681564245810058,1.0125698324022347,0.9539106145251397,0.9223463687150838,0.89078212290502801,0.76,0.77,0.78,0.8,0.82,0.84,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.338413407821228},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.172441340782122},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.996916201117321},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.581005586592182},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.07972067039106},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.945877094972065},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.789307262569832}]
[null,62,18.588268156424579,18.402385474860335,18.216201117318441,18.125120111731849,17.844134078212292,17.844134078212292,17.079888268156424,17.079888268156424,16.255307262569833,16.255307262569833,15.810335195530728,15.810335195530728,15.365363128491619,15.365363128491619,null,1.03268156424581,1.0120111731843577,0.99134078212290522,0.94888268156424582,0.90307262569832403,0.87835195530726262,0.85363128491620111,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.402385474860335,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.125120111731849},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.844134078212292},17.079888268156424,16.255307262569833,15.810335195530728,15.365363128491619]
[null,57,18.573184357541901,18.573184357541901,18.211173184357541,18.211173184357541,17.849162011173185,17.849162011173185,17.079888268156424,17.079888268156424,16.260335195530729,16.260335195530729,15.812849162011176,15.812849162011176,15.365363128491619,15.365363128491619,null,1.0318435754189945,1.011731843575419,0.99162011173184361,0.94888268156424582,0.90335195530726276,0.87849162011173199,0.85363128491620111,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.573184357541901,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.211173184357541},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.849162011173185},17.079888268156424,16.260335195530729,15.812849162011176,15.365363128491619]

{"sheet":"N4A4_42","index":38,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.324444444444445},{"$f":"IF(AM8>C8,C8,AM8)","v":11.088711111111111},{"$f":"S8*$I$13","v":20.866666666666671},{"$f":"IF(AN8>E8,E8,AN8)","v":10.955000000000002},{"$f":"T8*$I$13","v":20.408888888888889},{"$f":"IF(AO8>G8,G8,AO8)","v":10.816711111111111},{"$f":"U8*$I$13","v":19.417777777777779},{"$f":"IF(AP8>I8,I8,AP8)","v":10.485600000000002},{"$f":"V8*$I$13","v":18.351111111111109},{"$f":"IF(AQ8>K8,K8,AQ8)","v":10.09311111111111},{"$f":"W8*$I$13","v":17.77555555555556},{"$f":"IF(AR8>M8,M8,AR8)","v":9.8654333333333373},{"$f":"X8*$I$13","v":17.2},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6319999999999997},null,1.1846913580246914,1.1592592592592594,1.1338271604938273,1.0787654320987654,1.0195061728395061,0.987530864197531,0.9555555555555556,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.088711111111111},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.955000000000002},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.816711111111111},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.485600000000002},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":10.09311111111111},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.8654333333333373},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6319999999999997}]
[null,67,19.493333333333332,13.645333333333332,19.071111111111108,{"$f":"IF(AN9>E9,E9,AN9)","v":13.540488888888886},18.648888888888887,{"$f":"IF(AO9>G9,G9,AO9)","v":13.427199999999999},{"$f":"U9*$I$13","v":17.737777777777776},{"$f":"IF(AP9>I9,I9,AP9)","v":12.948577777777777},16.755555555555556,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.566666666666666},16.224444444444444,{"$f":"IF(AR9>M9,M9,AR9)","v":12.4117},15.693333333333333,{"$f":"IF(AS9>O9,O9,AS9)","v":12.2408},null,1.0829629629629629,1.0595061728395061,1.0360493827160493,0.98543209876543203,0.93086419753086425,0.90135802469135806,0.87185185185185188,0.7,0.71,0.72,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.645333333333332},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.540488888888886},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.427199999999999},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.948577777777777},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.566666666666666},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.4117},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.2408}]
[null,62,17.835555555555558,16.230355555555558,17.45333333333333,16.057066666666664,17.071111111111108,15.876133333333332,{"$f":"U10*$I$13","v":16.253333333333334},15.440666666666667,15.391111111111112,15.083288888888889,14.968888888888889,14.8192,14.546666666666665,14.546666666666665,null,0.9908641975308643,0.96962962962962951,0.94839506172839494,0.90296296296296297,0.85506172839506178,0.83160493827160498,0.80814814814814806,0.91,0.92,0.93,0.95,0.98,0.99,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.230355555555558,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.057066666666664},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.876133333333332},15.440666666666667,15.083288888888889,14.8192,14.546666666666665]
[null,57,17.355555555555554,17.355555555555554,17.048888888888889,17.048888888888889,16.742222222222225,16.742222222222225,{"$f":"U11*$I$13","v":16.075555555555557},16.075555555555557,15.346666666666666,15.346666666666666,14.94888888888889,14.94888888888889,14.551111111111112,14.551111111111112,null,0.96419753086419746,0.9471604938271605,0.93012345679012354,0.89308641975308645,0.85259259259259257,0.83049382716049391,0.80839506172839515,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.355555555555554,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.048888888888889},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.742222222222225},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.075555555555557},15.346666666666666,14.94888888888889,14.551111111111112]
[1400,72,21.68,11.7072,21.202222222222222,11.555211111111111,20.724444444444448,11.398444444444447,{"$f":"U12*$I$13","v":19.693333333333335},11.028266666666669,18.586666666666666,10.594399999999998,17.991111111111113,10.344888888888889,17.395555555555557,10.089422222222222,null,1.2044444444444444,1.1779012345679012,1.1513580246913582,1.0940740740740742,1.0325925925925925,0.99950617283950627,0.96641975308641981,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.7072},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.555211111111111},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.398444444444447},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":11.028266666666669},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.594399999999998},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.344888888888889},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.089422222222222}]
[null,67,19.83111111111111,14.675022222222221,19.388888888888886,14.44472222222222,18.946666666666669,14.21,18,13.86,16.982222222222223,13.415955555555557,16.435555555555556,13.230622222222221,15.888888888888889,13.028888888888888,null,1.1017283950617283,1.0771604938271604,1.0525925925925927,1,0.94345679012345685,0.91308641975308646,0.88271604938271608,0.74,0.745,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.675022222222221},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.44472222222222},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.21},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.415955555555557},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.230622222222221},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.028888888888888}]
[null,62,18.231111111111115,17.501866666666668,17.844444444444445,17.309111111111111,17.457777777777778,17.108622222222223,{"$f":"U14*$I$13","v":16.684444444444445},16.684444444444445,15.906666666666666,15.906666666666666,15.482222222222223,15.482222222222223,15.05777777777778,15.05777777777778,null,1.0128395061728397,0.99135802469135814,0.9698765432098766,0.9269135802469135,0.88370370370370366,0.86012345679012348,0.83654320987654329,0.96,0.97,0.98,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.501866666666668,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.309111111111111},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.108622222222223},16.684444444444445,15.906666666666666,15.482222222222223,15.05777777777778]
[null,57,18.062222222222221,18.062222222222221,17.731111111111112,17.731111111111112,17.399999999999999,17.399999999999999,16.684444444444445,16.684444444444445,15.906666666666666,15.906666666666666,15.482222222222223,15.482222222222223,15.05777777777778,15.05777777777778,null,1.0034567901234568,0.98506172839506168,0.96666666666666667,0.9269135802469135,0.88370370370370366,0.86012345679012348,0.83654320987654329,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.062222222222221,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.731111111111112},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.399999999999999},16.684444444444445,15.906666666666666,15.482222222222223,15.05777777777778]
[1575,72,21.94222222222222,12.287644444444444,21.446666666666665,12.117366666666666,20.951111111111111,11.942133333333333,19.888888888888889,11.535555555555556,18.751111111111111,11.063155555555555,18.137777777777778,10.882666666666667,17.524444444444445,10.689911111111112,null,1.2190123456790123,1.1914814814814814,1.1639506172839507,1.1049382716049383,1.0417283950617284,1.0076543209876543,0.97358024691358025,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.57999999999999996,0.59,0.6,0.61,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.287644444444444},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":12.117366666666666},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.942133333333333},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.535555555555556},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":11.063155555555555},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.882666666666667},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.689911111111112}]
[null,67,20.075555555555557,15.458177777777779,19.619999999999997,15.303599999999998,19.164444444444442,15.139911111111109,18.191111111111113,14.734800000000002,17.146666666666665,14.231733333333331,16.584444444444443,14.013855555555555,16.022222222222222,13.77911111111111,null,1.1153086419753087,1.0899999999999999,1.0646913580246913,1.0106172839506173,0.95259259259259255,0.92135802469135797,0.89012345679012339,0.77,0.78,0.79,0.81,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.458177777777779},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.303599999999998},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.139911111111109},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.734800000000002},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.231733333333331},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":14.013855555555555},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.77911111111111}]
[null,62,18.617777777777775,18.617777777777775,18.273333333333333,18.273333333333333,17.928888888888892,17.928888888888892,17.173333333333332,17.173333333333332,16.351111111111109,16.351111111111109,15.902222222222223,15.902222222222223,15.453333333333335,15.453333333333335,null,1.0343209876543209,1.0151851851851852,0.99604938271604948,0.95407407407407407,0.90839506172839501,0.88345679012345679,0.85851851851851857,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.617777777777775,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.273333333333333},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.928888888888892},17.173333333333332,16.351111111111109,15.902222222222223,15.453333333333335]
[null,57,18.626666666666665,18.626666666666665,18.277777777777779,18.277777777777779,17.928888888888892,17.928888888888892,17.173333333333332,17.173333333333332,16.351111111111109,16.351111111111109,15.904444444444444,15.904444444444444,15.457777777777778,15.457777777777778,null,1.0348148148148146,1.0154320987654322,0.99604938271604948,0.95407407407407407,0.90839506172839501,0.88358024691358017,0.85876543209876544,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.626666666666665,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.277777777777779},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.928888888888892},17.173333333333332,16.351111111111109,15.904444444444444,15.457777777777778]

{"sheet":"N4A4_48","index":39,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.355051546391753},{"$f":"IF(AM8>C8,C8,AM8)","v":10.891076288659795},{"$f":"S8*$I$13","v":20.865154639175259},{"$f":"IF(AN8>E8,E8,AN8)","v":10.641228865979382},{"$f":"T8*$I$13","v":20.375257731958762},{"$f":"IF(AO8>G8,G8,AO8)","v":10.391381443298968},{"$f":"U8*$I$13","v":19.38061855670103},{"$f":"IF(AP8>I8,I8,AP8)","v":10.077921649484535},{"$f":"V8*$I$13","v":18.345154639175259},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7229319587628886},{"$f":"W8*$I$13","v":17.792164948453607},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5188082474226796},{"$f":"X8*$I$13","v":17.239175257731958},{"$f":"IF(AS8>O8,O8,AS8)","v":9.309154639175258},null,1.1863917525773195,1.1591752577319587,1.1319587628865979,1.0767010309278351,1.0191752577319588,0.98845360824742268,0.95773195876288664,0.51,0.51,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.891076288659795},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.641228865979382},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.391381443298968},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.077921649484535},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7229319587628886},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5188082474226796},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.309154639175258}]
[null,67,19.521649484536081,13.274721649484535,19.07443298969072,{"$f":"IF(AN9>E9,E9,AN9)","v":13.065986597938144},18.627216494845364,{"$f":"IF(AO9>G9,G9,AO9)","v":12.8527793814433},{"$f":"U9*$I$13","v":17.714226804123712},{"$f":"IF(AP9>I9,I9,AP9)","v":12.399958762886598},16.76041237113402,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.067496907216494},16.250103092783505,{"$f":"IF(AR9>M9,M9,AR9)","v":11.862575257731958},15.739793814432989,{"$f":"IF(AS9>O9,O9,AS9)","v":11.647447422680411},null,1.0845360824742267,1.0596907216494844,1.0348453608247423,0.98412371134020615,0.93113402061855666,0.90278350515463912,0.87443298969072158,0.68,0.68500000000000005,0.69,0.7,0.72,0.73,0.74,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.274721649484535},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.065986597938144},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.8527793814433},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.399958762886598},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.067496907216494},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.862575257731958},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.647447422680411}]
[null,62,17.866391752577318,15.543760824742266,17.461855670103091,15.36643298969072,17.057319587628868,15.181014432989693,{"$f":"U10*$I$13","v":16.237113402061855},14.938144329896907,15.383505154639177,14.460494845360826,14.938144329896907,14.49,14.492783505154637,14.492783505154637,null,0.99257731958762885,0.97010309278350515,0.94762886597938145,0.90206185567010311,0.85463917525773203,0.82989690721649489,0.80515463917525765,0.87,0.88,0.89,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.543760824742266,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.36643298969072},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.181014432989693},14.938144329896907,14.460494845360826,14.49,14.492783505154637]
[null,57,17.268865979381445,17.268865979381445,16.947835051546392,16.947835051546392,16.626804123711338,16.626804123711338,{"$f":"U11*$I$13","v":15.96618556701031},15.96618556701031,15.261030927835051,15.261030927835051,14.88061855670103,14.88061855670103,14.500206185567011,14.500206185567011,null,0.95938144329896913,0.94154639175257726,0.9237113402061855,0.88701030927835056,0.84783505154639172,0.82670103092783498,0.80556701030927835,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.268865979381445,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.947835051546392},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.626804123711338},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.96618556701031},15.261030927835051,14.88061855670103,14.500206185567011]
[1600,72,21.752164948453608,11.311125773195876,21.238144329896908,11.150025773195877,20.724123711340209,10.983785567010312,{"$f":"U12*$I$13","v":19.681237113402062},10.627868041237114,18.604948453608248,10.232721649484537,18.033402061855675,10.008538144329901,17.461855670103091,9.778639175257732,null,1.2084536082474227,1.1798969072164949,1.1513402061855671,1.0934020618556701,1.0336082474226804,1.001855670103093,0.97010309278350515,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.311125773195876},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.150025773195877},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.983785567010312},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.627868041237114},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.232721649484537},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.008538144329901},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.778639175257732}]
[null,67,19.89278350515464,14.123876288659794,19.423298969072164,13.887658762886597,18.953814432989688,13.646746391752576,18,13.32,17.009072164948453,12.926894845360824,16.4820618556701,12.691187628865977,15.955051546391752,12.444940206185567,null,1.1051546391752578,1.0790721649484536,1.0529896907216494,1,0.94494845360824742,0.91567010309278341,0.88639175257731961,0.71,0.71499999999999997,0.72,0.74,0.76,0.77,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.123876288659794},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.887658762886597},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.646746391752576},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.926894845360824},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.691187628865977},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.444940206185567}]
[null,62,18.270927835051545,16.80925360824742,17.855257731958762,16.605389690721648,17.439587628865979,16.39321237113402,{"$f":"U14*$I$13","v":16.611958762886598},16.445839175257731,15.84,15.84,15.433608247422681,15.433608247422681,15.02721649484536,15.02721649484536,null,1.0150515463917524,0.9919587628865979,0.96886597938144337,0.92288659793814432,0.88,0.85742268041237113,0.83484536082474226,0.92,0.92999999999999994,0.94,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.80925360824742,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.605389690721648},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.39321237113402},16.445839175257731,15.84,15.433608247422681,15.02721649484536]
[null,57,18,18,17.654845360824744,17.654845360824744,17.309690721649485,17.309690721649485,16.59340206185567,16.59340206185567,15.84,15.84,15.433608247422681,15.433608247422681,15.02721649484536,15.02721649484536,null,1,0.98082474226804128,0.96164948453608246,0.92185567010309277,0.88,0.85742268041237113,0.83484536082474226,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.654845360824744},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.309690721649485},16.59340206185567,15.84,15.433608247422681,15.02721649484536]
[1800,72,22.041649484536084,11.902490721649485,21.510927835051547,11.723455670103094,20.98020618556701,11.539113402061856,19.900206185567008,11.144115463917526,18.790515463917526,10.710593814432988,18.202268041237115,10.466304123711341,17.614020618556701,10.216131958762887,null,1.2245360824742269,1.1950515463917526,1.1655670103092783,1.1055670103092783,1.0439175257731959,1.0112371134020619,0.97855670103092784,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.902490721649485},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.723455670103094},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.539113402061856},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.144115463917526},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.710593814432988},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.466304123711341},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.216131958762887}]
[null,67,20.167422680412372,14.923892783505154,19.679381443298972,14.661139175257734,19.191340206185568,14.393505154639175,18.211546391752577,14.022890721649485,17.190927835051546,13.752742268041239,16.650927835051544,13.570506185567007,16.110927835051545,13.372070103092781,null,1.1204123711340206,1.0932989690721651,1.0661855670103093,1.0117525773195877,0.9550515463917526,0.92505154639175247,0.89505154639175255,0.74,0.745,0.75,0.77,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.923892783505154},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.661139175257734},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.393505154639175},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.022890721649485},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.752742268041239},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.570506185567007},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.372070103092781}]
[null,62,18.638350515463916,18.451967010309275,18.252371134020621,18.161109278350516,17.866391752577318,17.866391752577318,17.109278350515464,17.109278350515464,16.311340206185569,16.311340206185569,15.882680412371135,15.882680412371135,15.454020618556701,15.454020618556701,null,1.0354639175257732,1.0140206185567011,0.99257731958762885,0.95051546391752584,0.90618556701030939,0.88237113402061862,0.85855670103092785,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.451967010309275,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.161109278350516},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.866391752577318},17.109278350515464,16.311340206185569,15.882680412371135,15.454020618556701]
[null,57,18.60123711340206,18.60123711340206,18.233814432989689,18.233814432989689,17.866391752577318,17.866391752577318,17.109278350515464,17.109278350515464,16.311340206185569,16.311340206185569,15.882680412371135,15.882680412371135,15.454020618556701,15.454020618556701,null,1.0334020618556701,1.0129896907216493,0.99257731958762885,0.95051546391752584,0.90618556701030939,0.88237113402061862,0.85855670103092785,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.60123711340206,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.233814432989689},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.866391752577318},17.109278350515464,16.311340206185569,15.882680412371135,15.454020618556701]

{"sheet":"N4A4_49","index":40,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_49"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.799565217391308},{"$f":"IF(AM8>C8,C8,AM8)","v":10.899782608695654},{"$f":"S8*$I$13","v":21.251739130434785},{"$f":"IF(AN8>E8,E8,AN8)","v":10.732128260869567},{"$f":"T8*$I$13","v":20.703913043478263},{"$f":"IF(AO8>G8,G8,AO8)","v":10.558995652173914},{"$f":"U8*$I$13","v":19.569130434782611},{"$f":"IF(AP8>I8,I8,AP8)","v":10.175947826086958},{"$f":"V8*$I$13","v":18.39130434782609},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7473913043478273},{"$f":"W8*$I$13","v":17.774999999999999},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5096249999999998},{"$f":"X8*$I$13","v":17.158695652173911},{"$f":"IF(AS8>O8,O8,AS8)","v":9.2656956521739122},null,1.2110869565217393,1.1806521739130436,1.1502173913043479,1.0871739130434783,1.0217391304347827,0.98749999999999993,0.95326086956521738,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.899782608695654},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.732128260869567},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.558995652173914},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.175947826086958},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7473913043478273},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5096249999999998},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.2656956521739122}]
[null,67,19.753043478260871,13.432069565217393,19.260000000000002,{"$f":"IF(AN9>E9,E9,AN9)","v":13.289400000000001},18.766956521739129,{"$f":"IF(AO9>G9,G9,AO9)","v":13.13686956521739},{"$f":"U9*$I$13","v":17.753478260869564},{"$f":"IF(AP9>I9,I9,AP9)","v":12.60496956521739},16.696956521739132,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.188778260869567},16.14521739130435,{"$f":"IF(AR9>M9,M9,AR9)","v":12.02818695652174},15.593478260869567,{"$f":"IF(AS9>O9,O9,AS9)","v":11.851043478260872},null,1.0973913043478261,1.07,1.0426086956521738,0.98630434782608689,0.92760869565217396,0.89695652173913054,0.86630434782608701,0.68,0.69,0.7,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.432069565217393},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.289400000000001},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.13686956521739},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.60496956521739},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.188778260869567},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.02818695652174},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.851043478260872}]
[null,62,17.972608695652173,15.815895652173912,17.546086956521741,15.703747826086959,17.119565217391305,15.578804347826088,{"$f":"U10*$I$13","v":16.258695652173913},16.096108695652173,15.460434782608694,15.460434782608694,15.045652173913046,15.045652173913046,14.63086956521739,14.63086956521739,null,0.99847826086956526,0.97478260869565225,0.95108695652173914,0.90326086956521734,0.85891304347826081,0.83586956521739142,0.8128260869565217,0.88,0.89500000000000002,0.91,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.815895652173912,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.703747826086959},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.578804347826088},16.096108695652173,15.460434782608694,15.045652173913046,14.63086956521739]
[null,57,17.628260869565217,17.628260869565217,17.281956521739129,17.281956521739129,16.935652173913041,16.935652173913041,{"$f":"U11*$I$13","v":16.211739130434783},16.211739130434783,15.436956521739132,15.436956521739132,15.024130434782611,15.024130434782611,14.611304347826087,14.611304347826087,null,0.97934782608695647,0.96010869565217394,0.94086956521739129,0.90065217391304342,0.85760869565217401,0.83467391304347838,0.81173913043478263,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.628260869565217,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.281956521739129},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.935652173913041},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.211739130434783},15.436956521739132,15.024130434782611,14.611304347826087]
[1600,72,22.171304347826084,11.529078260869564,21.592173913043478,11.335891304347827,21.013043478260869,11.136913043478261,{"$f":"U12*$I$13","v":19.827391304347827},10.706791304347828,18.602608695652172,10.231434782608696,17.96086956521739,10.058086956521739,17.319130434782608,9.8719043478260851,null,1.2317391304347824,1.1995652173913043,1.1673913043478261,1.1015217391304348,1.0334782608695652,0.99782608695652175,0.96217391304347821,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.529078260869564},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.335891304347827},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.136913043478261},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.706791304347828},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.231434782608696},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.058086956521739},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8719043478260851}]
[null,67,20.093478260869567,14.266369565217392,19.576956521739131,14.095408695652173,19.060434782608699,13.91411739130435,18,13.5,16.904347826086958,13.185391304347828,16.331086956521737,12.983214130434781,15.757826086956522,12.763839130434784,null,1.116304347826087,1.087608695652174,1.058913043478261,1,0.93913043478260871,0.90728260869565214,0.87543478260869567,0.71,0.72,0.73,0.75,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.266369565217392},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.095408695652173},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.91411739130435},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.185391304347828},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.983214130434781},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.763839130434784}]
[null,62,18.414782608695656,18.2306347826087,18.023478260869567,17.93336086956522,17.632173913043481,17.632173913043481,{"$f":"U14*$I$13","v":16.841739130434782},16.841739130434782,16.008260869565216,16.008260869565216,15.560217391304349,15.560217391304349,15.112173913043478,15.112173913043478,null,1.0230434782608697,1.001304347826087,0.97956521739130442,0.93565217391304345,0.88934782608695639,0.86445652173913046,0.8395652173913043,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.2306347826087,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.93336086956522},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.632173913043481},16.841739130434782,16.008260869565216,15.560217391304349,15.112173913043478]
[null,57,18.36,18.36,17.982391304347825,17.982391304347825,17.60478260869565,17.60478260869565,16.818260869565215,16.818260869565215,15.984782608695653,15.984782608695653,15.538695652173914,15.538695652173914,15.092608695652174,15.092608695652174,null,1.02,0.99902173913043479,0.97804347826086957,0.93434782608695643,0.8880434782608696,0.86326086956521741,0.83847826086956523,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.36,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.982391304347825},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.60478260869565},16.818260869565215,15.984782608695653,15.538695652173914,15.092608695652174]
[1800,72,22.433478260869563,12.114078260869565,21.834782608695651,11.899956521739131,21.236086956521739,11.679847826086958,20.007391304347827,11.204139130434784,18.735652173913046,10.679321739130435,18.078260869565216,10.485391304347825,17.420869565217394,10.278313043478262,null,1.2463043478260869,1.2130434782608694,1.1797826086956522,1.1115217391304348,1.0408695652173914,1.0043478260869565,0.96782608695652184,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.114078260869565},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.899956521739131},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.679847826086958},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.204139130434784},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.679321739130435},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.485391304347825},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.278313043478262}]
[null,67,20.34391304347826,15.257934782608695,19.807826086956524,15.053947826086958,19.271739130434781,14.839239130434782,18.18,14.3622,17.049130434782608,13.980286956521738,16.462173913043479,13.745915217391305,15.875217391304348,13.493934782608695,null,1.1302173913043478,1.1004347826086958,1.0706521739130435,1.01,0.94717391304347831,0.91456521739130436,0.88195652173913042,0.75,0.76,0.77,0.79,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.257934782608695},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.053947826086958},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.839239130434782},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.3622},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.980286956521738},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.745915217391305},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.493934782608695}]
[null,62,18.982173913043475,18.982173913043475,18.577173913043477,18.577173913043477,18.17217391304348,18.17217391304348,17.330869565217391,17.330869565217391,16.442608695652176,16.442608695652176,15.969130434782608,15.969130434782608,15.495652173913044,15.495652173913044,null,1.0545652173913043,1.0320652173913043,1.0095652173913043,0.96282608695652172,0.9134782608695653,0.88717391304347826,0.86086956521739133,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.982173913043475,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.577173913043477},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.17217391304348},17.330869565217391,16.442608695652176,15.969130434782608,15.495652173913044]
[null,57,18.958695652173915,18.958695652173915,18.553695652173914,18.553695652173914,18.148695652173917,18.148695652173917,17.311304347826088,17.311304347826088,16.423043478260869,16.423043478260869,15.949565217391303,15.949565217391303,15.476086956521739,15.476086956521739,null,1.0532608695652175,1.0307608695652175,1.0082608695652175,0.96173913043478265,0.91239130434782612,0.88608695652173908,0.85978260869565215,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.958695652173915,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.553695652173914},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.148695652173917},17.311304347826088,16.423043478260869,15.949565217391303,15.476086956521739]

{"sheet":"N4A4_60","index":41,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["N4A4_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.413898305084746},{"$f":"IF(AM8>C8,C8,AM8)","v":10.921088135593221},{"$f":"S8*$I$13","v":20.925762711864408},{"$f":"IF(AN8>E8,E8,AN8)","v":10.776767796610171},{"$f":"T8*$I$13","v":20.437627118644066},{"$f":"IF(AO8>G8,G8,AO8)","v":10.627566101694915},{"$f":"U8*$I$13","v":19.403389830508477},{"$f":"IF(AP8>I8,I8,AP8)","v":10.283796610169492},{"$f":"V8*$I$13","v":18.295932203389832},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.87980338983051},{"$f":"W8*$I$13","v":17.691864406779658},{"$f":"IF(AR8>M8,M8,AR8)","v":9.6420661016949136},{"$f":"X8*$I$13","v":17.087796610169491},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3982881355932211},null,1.1896610169491526,1.162542372881356,1.1354237288135591,1.0779661016949154,1.0164406779661017,0.98288135593220327,0.94932203389830505,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.921088135593221},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.776767796610171},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.627566101694915},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.283796610169492},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.87980338983051},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.6420661016949136},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3982881355932211}]
[null,67,19.549830508474574,13.489383050847456,19.107457627118642,{"$f":"IF(AN9>E9,E9,AN9)","v":13.279683050847455},18.665084745762712,{"$f":"IF(AO9>G9,G9,AO9)","v":13.065559322033899},{"$f":"U9*$I$13","v":17.72542372881356},{"$f":"IF(AP9>I9,I9,AP9)","v":12.762305084745762},16.715593220338981,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.202383050847455},16.166440677966101,{"$f":"IF(AR9>M9,M9,AR9)","v":12.043998305084745},15.617288135593219,{"$f":"IF(AS9>O9,O9,AS9)","v":11.869138983050846},null,1.0861016949152542,1.0615254237288134,1.0369491525423729,0.98474576271186443,0.92864406779661013,0.89813559322033887,0.86762711864406772,0.69,0.69499999999999995,0.7,0.72,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.489383050847456},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.279683050847455},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.065559322033899},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.762305084745762},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.202383050847455},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.043998305084745},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.869138983050846}]
[null,62,17.884067796610168,15.916820338983049,17.487457627118644,15.738711864406779,17.09084745762712,15.55267118644068,{"$f":"U10*$I$13","v":16.257966101694915},15.119908474576272,15.373220338983051,14.758291525423729,14.914067796610171,14.615786440677967,14.454915254237289,14.454915254237289,null,0.9935593220338983,0.97152542372881356,0.94949152542372883,0.90322033898305087,0.85406779661016952,0.82855932203389837,0.80305084745762711,0.89,0.9,0.91,0.93,0.96,0.98,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.916820338983049,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.738711864406779},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.55267118644068},15.119908474576272,14.758291525423729,14.615786440677967,14.454915254237289]
[null,57,17.319661016949155,17.319661016949155,17.003898305084746,17.003898305084746,16.688135593220341,16.688135593220341,{"$f":"U11*$I$13","v":16.010847457627118},16.010847457627118,15.275593220338983,15.275593220338983,14.868305084745762,14.868305084745762,14.461016949152542,14.461016949152542,null,0.96220338983050857,0.9446610169491525,0.92711864406779665,0.88949152542372878,0.84864406779661017,0.82601694915254231,0.80338983050847457,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.319661016949155,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.003898305084746},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.688135593220341},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.010847457627118},15.275593220338983,14.868305084745762,14.461016949152542]
[2000,72,21.798305084745763,11.553101694915256,21.285762711864407,11.387883050847458,20.773220338983052,11.217538983050849,{"$f":"U12*$I$13","v":19.69322033898305},10.831271186440679,18.536949152542373,10.38069152542373,17.91,10.119149999999999,17.283050847457627,9.8513389830508462,null,1.2110169491525424,1.182542372881356,1.1540677966101696,1.0940677966101695,1.0298305084745762,0.995,0.96016949152542375,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.553101694915256},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.387883050847458},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.217538983050849},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.831271186440679},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.38069152542373},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.119149999999999},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8513389830508462}]
[null,67,19.915932203389833,14.339471186440679,19.449152542372882,14.100635593220339,18.982372881355932,13.857132203389829,18,13.5,16.950508474576271,13.051891525423729,16.381525423728814,12.859497457627119,15.812542372881355,12.650033898305084,null,1.1064406779661018,1.0805084745762712,1.0545762711864406,1,0.94169491525423732,0.91008474576271192,0.87847457627118641,0.72,0.72499999999999998,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.339471186440679},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.100635593220339},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.857132203389829},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.051891525423729},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.859497457627119},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.650033898305084}]
[null,62,18.283728813559321,17.003867796610169,17.876440677966102,16.803854237288135,17.469152542372882,16.595694915254239,{"$f":"U14*$I$13","v":16.630169491525422},16.463867796610167,15.818644067796612,15.818644067796612,15.380847457627118,15.380847457627118,14.943050847457625,14.943050847457625,null,1.0157627118644068,0.99313559322033895,0.97050847457627121,0.92389830508474569,0.87881355932203398,0.85449152542372875,0.83016949152542363,0.93,0.94,0.95,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.003867796610169,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.803854237288135},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.595694915254239},16.463867796610167,15.818644067796612,15.380847457627118,14.943050847457625]
[null,57,18.024406779661017,18.024406779661017,17.68271186440678,17.68271186440678,17.341016949152543,17.341016949152543,16.611864406779663,16.611864406779663,15.818644067796612,15.818644067796612,15.382372881355934,15.382372881355934,14.946101694915255,14.946101694915255,null,1.0013559322033898,0.98237288135593226,0.9633898305084746,0.92288135593220344,0.87881355932203398,0.85457627118644075,0.83033898305084752,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.024406779661017,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.68271186440678},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.341016949152543},16.611864406779663,15.818644067796612,15.382372881355934,14.946101694915255]
[2250,72,22.082033898305081,11.924298305084745,21.551186440677967,11.745396610169493,21.020338983050848,11.561186440677968,19.900677966101696,11.14437966101695,18.707796610169492,10.850522033898304,18.061016949152542,10.565694915254236,17.414237288135592,10.274399999999998,null,1.226779661016949,1.1972881355932203,1.1677966101694917,1.1055932203389831,1.0393220338983051,1.0033898305084745,0.96745762711864403,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.58499999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.924298305084745},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.745396610169493},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.561186440677968},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.14437966101695},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.850522033898304},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.565694915254236},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.274399999999998}]
[null,67,20.178305084745762,15.133728813559323,19.694745762711868,14.86953305084746,19.211186440677963,14.600501694915252,18.198305084745762,14.376661016949152,17.11830508474576,13.865827118644066,16.53406779661017,13.640605932203389,15.949830508474577,13.397857627118643,null,1.1210169491525424,1.0941525423728815,1.0672881355932202,1.0110169491525423,0.95101694915254231,0.91855932203389834,0.88610169491525426,0.75,0.755,0.76,0.79,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.133728813559323},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.86953305084746},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.600501694915252},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.376661016949152},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.865827118644066},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.640605932203389},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.397857627118643}]
[null,62,18.643728813559324,18.084416949152544,18.259322033898307,17.985432203389834,17.87491525423729,17.87491525423729,17.099999999999998,17.099999999999998,16.261016949152541,16.261016949152541,15.79728813559322,15.79728813559322,15.333559322033899,15.333559322033899,null,1.0357627118644068,1.014406779661017,0.99305084745762717,0.95,0.90338983050847455,0.87762711864406784,0.85186440677966102,0.97,0.98499999999999999,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.084416949152544,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":17.985432203389834},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.87491525423729},17.099999999999998,16.261016949152541,15.79728813559322,15.333559322033899]
[null,57,18.60406779661017,18.60406779661017,18.23949152542373,18.23949152542373,17.87491525423729,17.87491525423729,17.099999999999998,17.099999999999998,16.261016949152541,16.261016949152541,15.798813559322033,15.798813559322033,15.336610169491527,15.336610169491527,null,1.0335593220338983,1.0133050847457628,0.99305084745762717,0.95,0.90338983050847455,0.87771186440677962,0.8520338983050848,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.60406779661017,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.23949152542373},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.87491525423729},17.099999999999998,16.261016949152541,15.798813559322033,15.336610169491527]

{"sheet":"NXA6_18","index":42,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.41},{"$f":"IF(AM8>C8,C8,AM8)","v":10.2768},{"$f":"S8*$I$13","v":20.945},{"$f":"IF(AN8>E8,E8,AN8)","v":10.158325},{"$f":"T8*$I$13","v":20.48},{"$f":"IF(AO8>G8,G8,AO8)","v":10.0352},{"$f":"U8*$I$13","v":19.46},{"$f":"IF(AP8>I8,I8,AP8)","v":9.73},{"$f":"V8*$I$13","v":18.329999999999998},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3483000000000001},{"$f":"W8*$I$13","v":17.739999999999998},{"$f":"IF(AR8>M8,M8,AR8)","v":9.136099999999999},{"$f":"X8*$I$13","v":17.149999999999999},{"$f":"IF(AS8>O8,O8,AS8)","v":8.9179999999999993},null,1.1894444444444445,1.1636111111111112,1.1377777777777778,1.0811111111111111,1.0183333333333333,0.98555555555555552,0.95277777777777772,0.48,0.48499999999999999,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.2768},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.158325},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.0352},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.73},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3483000000000001},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.136099999999999},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.9179999999999993}]
[null,67,19.54,12.701000000000001,19.100000000000001,{"$f":"IF(AN9>E9,E9,AN9)","v":12.510500000000002},18.66,{"$f":"IF(AO9>G9,G9,AO9)","v":12.3156},{"$f":"U9*$I$13","v":17.690000000000001},{"$f":"IF(AP9>I9,I9,AP9)","v":11.852300000000001},16.649999999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.488499999999998},16.105,{"$f":"IF(AR9>M9,M9,AR9)","v":11.354025},15.56,{"$f":"IF(AS9>O9,O9,AS9)","v":11.203200000000001},null,1.0855555555555556,1.0611111111111111,1.0366666666666666,0.98277777777777786,0.92499999999999993,0.8947222222222222,0.86444444444444446,0.65,0.65500000000000003,0.66,0.67,0.69,0.70499999999999996,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.701000000000001},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.510500000000002},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.3156},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":11.852300000000001},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.488499999999998},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.354025},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.203200000000001}]
[null,62,17.82,14.9688,17.405000000000001,14.79425,16.989999999999998,14.611399999999998,{"$f":"U10*$I$13","v":16.12},14.185600000000001,15.2,13.831999999999999,14.77,14.105350000000001,14.34,14.34,null,0.99,0.9669444444444445,0.94388888888888878,0.89555555555555566,0.84444444444444444,0.82055555555555548,0.79666666666666663,0.84,0.85,0.86,0.88,0.91,0.95500000000000007,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,14.9688,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":14.79425},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.611399999999998},14.185600000000001,13.831999999999999,14.105350000000001,14.34]
[null,57,17.23,17.23,16.905000000000001,16.905000000000001,16.579999999999998,16.579999999999998,{"$f":"U11*$I$13","v":15.88},15.88,15.13,15.13,14.725000000000001,14.725000000000001,14.32,14.32,null,0.9572222222222222,0.93916666666666671,0.92111111111111099,0.88222222222222224,0.84055555555555561,0.81805555555555565,0.79555555555555557,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.23,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.905000000000001},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.579999999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.88},15.13,14.725000000000001,14.32]
[600,72,21.81,10.904999999999999,21.32,10.7666,20.83,10.623299999999999,{"$f":"U12*$I$13","v":19.78},10.087800000000001,18.61,9.8633000000000006,17.994999999999997,9.627324999999999,17.38,9.3851999999999993,null,1.2116666666666667,1.1844444444444444,1.1572222222222222,1.098888888888889,1.0338888888888889,0.99972222222222207,0.9655555555555555,0.5,0.505,0.51,0.51,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.904999999999999},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.7666},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.623299999999999},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.087800000000001},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8633000000000006},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.627324999999999},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.3851999999999993}]
[null,67,19.920000000000002,13.545600000000002,19.465000000000003,13.333525000000003,19.010000000000002,13.116899999999999,18,12.78,16.93,12.3589,16.36,12.1882,15.79,12.000399999999999,null,1.1066666666666667,1.0813888888888892,1.0561111111111112,1,0.94055555555555559,0.90888888888888886,0.87722222222222213,0.68,0.68500000000000005,0.69,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.545600000000002},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.333525000000003},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.116899999999999},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.78},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.3589},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.1882},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.000399999999999}]
[null,62,18.260000000000002,16.068800000000003,17.835000000000001,15.873150000000001,17.41,15.669,{"$f":"U14*$I$13","v":16.59},16.59,15.78,15.78,15.344999999999999,15.344999999999999,14.91,14.91,null,1.0144444444444445,0.99083333333333334,0.96722222222222221,0.92166666666666663,0.87666666666666659,0.85249999999999992,0.82833333333333337,0.88,0.89,0.9,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.068800000000003,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":15.873150000000001},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.669},16.59,15.78,15.344999999999999,14.91]
[null,57,18.02,18.02,17.664999999999999,17.664999999999999,17.309999999999999,17.309999999999999,16.559999999999999,16.559999999999999,15.75,15.75,15.315000000000001,15.315000000000001,14.879999999999999,14.879999999999999,null,1.0011111111111111,0.98138888888888887,0.96166666666666656,0.91999999999999993,0.875,0.85083333333333344,0.82666666666666666,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.02,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.664999999999999},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.309999999999999},16.559999999999999,15.75,15.315000000000001,14.879999999999999]
[675,72,22.09,11.486800000000001,21.585000000000001,11.224200000000002,21.08,10.961599999999999,20.010000000000002,10.605300000000002,18.8,10.340000000000002,18.164999999999999,10.081575000000001,17.53,9.8168000000000024,null,1.2272222222222222,1.1991666666666667,1.171111111111111,1.1116666666666668,1.0444444444444445,1.0091666666666665,0.97388888888888892,0.52,0.52,0.52,0.53,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.486800000000001},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.224200000000002},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.961599999999999},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.605300000000002},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.340000000000002},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.081575000000001},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.8168000000000024}]
[null,67,20.2,14.341999999999999,19.729999999999997,14.205599999999997,19.260000000000002,14.059800000000001,18.23,13.672499999999999,17.12,13.182400000000001,16.54,12.9839,15.96,12.768000000000001,null,1.1222222222222222,1.096111111111111,1.07,1.0127777777777778,0.95111111111111113,0.91888888888888887,0.88666666666666671,0.71,0.72,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.341999999999999},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.205599999999997},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.059800000000001},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.672499999999999},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.182400000000001},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":12.9839},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.768000000000001}]
[null,62,18.68,18.68,18.314999999999998,18.314999999999998,17.95,17.95,17.149999999999999,17.149999999999999,16.29,16.29,15.824999999999999,15.824999999999999,15.36,15.36,null,1.0377777777777777,1.0174999999999998,0.99722222222222223,0.95277777777777772,0.90499999999999992,0.87916666666666665,0.85333333333333328,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.68,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.314999999999998},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.95},17.149999999999999,16.29,15.824999999999999,15.36]
[null,57,18.66,18.66,18.29,18.29,17.920000000000002,17.920000000000002,17.12,17.12,16.260000000000002,16.260000000000002,15.8,15.8,15.34,15.34,null,1.0366666666666666,1.016111111111111,0.99555555555555564,0.95111111111111113,0.90333333333333343,0.87777777777777777,0.85222222222222221,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.66,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.29},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.920000000000002},17.12,16.260000000000002,15.8,15.34]

{"sheet":"NXA6_24","index":43,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.516101694915253},{"$f":"IF(AM8>C8,C8,AM8)","v":10.327728813559322},{"$f":"S8*$I$13","v":21.024152542372882},{"$f":"IF(AN8>E8,E8,AN8)","v":10.196713983050847},{"$f":"T8*$I$13","v":20.53220338983051},{"$f":"IF(AO8>G8,G8,AO8)","v":10.06077966101695},{"$f":"U8*$I$13","v":19.479661016949152},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7398305084745758},{"$f":"V8*$I$13","v":18.373728813559321},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3706016949152531},{"$f":"W8*$I$13","v":17.790254237288131},{"$f":"IF(AR8>M8,M8,AR8)","v":9.1619809322033881},{"$f":"X8*$I$13","v":17.206779661016949},{"$f":"IF(AS8>O8,O8,AS8)","v":8.9475254237288144},null,1.1953389830508474,1.1680084745762711,1.140677966101695,1.0822033898305083,1.0207627118644067,0.98834745762711851,0.95593220338983043,0.48,0.48499999999999999,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.327728813559322},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.196713983050847},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.06077966101695},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7398305084745758},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3706016949152531},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.1619809322033881},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.9475254237288144}]
[null,67,19.54830508474576,12.706398305084745,19.094491525423727,{"$f":"IF(AN9>E9,E9,AN9)","v":12.60236440677966},18.640677966101695,{"$f":"IF(AO9>G9,G9,AO9)","v":12.489254237288137},{"$f":"U9*$I$13","v":17.687288135593221},{"$f":"IF(AP9>I9,I9,AP9)","v":12.027355932203392},16.680508474576271,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.676355932203389},16.146610169491524,{"$f":"IF(AR9>M9,M9,AR9)","v":11.464093220338981},15.612711864406778,{"$f":"IF(AS9>O9,O9,AS9)","v":11.24115254237288},null,1.0860169491525422,1.0608050847457626,1.035593220338983,0.98262711864406782,0.92669491525423731,0.89703389830508473,0.86737288135593216,0.65,0.66,0.67,0.68,0.7,0.71,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.706398305084745},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.60236440677966},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.489254237288137},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.027355932203392},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.676355932203389},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.464093220338981},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.24115254237288}]
[null,62,17.786440677966102,15.118474576271186,17.378389830508475,14.945415254237288,16.970338983050848,14.764194915254237,{"$f":"U10*$I$13","v":16.123728813559321},14.350118644067797,15.254237288135592,15.254237288135592,14.853813559322033,14.853813559322033,14.453389830508474,14.453389830508474,null,0.98813559322033895,0.9654661016949152,0.94279661016949146,0.8957627118644067,0.84745762711864403,0.82521186440677963,0.80296610169491522,0.85,0.86,0.87,0.89,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.118474576271186,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":14.945415254237288},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.764194915254237},14.350118644067797,15.254237288135592,14.853813559322033,14.453389830508474]
[null,57,17.298305084745763,17.298305084745763,16.977966101694911,16.977966101694911,16.657627118644069,16.657627118644069,{"$f":"U11*$I$13","v":15.963559322033896},15.963559322033896,15.223728813559323,15.223728813559323,14.827118644067797,14.827118644067797,14.430508474576271,14.430508474576271,null,0.96101694915254232,0.94322033898305069,0.92542372881355928,0.88686440677966094,0.84576271186440677,0.82372881355932204,0.80169491525423731,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.298305084745763,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":16.977966101694911},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.657627118644069},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":15.963559322033896},15.223728813559323,14.827118644067797,14.430508474576271]
[800,72,21.905084745762711,10.952542372881355,21.394067796610166,10.804004237288133,20.883050847457625,10.650355932203389,{"$f":"U12*$I$13","v":19.792372881355931},10.292033898305084,18.640677966101695,9.8795593220338986,18.034322033898306,9.6483622881355942,17.427966101694913,9.4111016949152546,null,1.2169491525423728,1.1885593220338981,1.1601694915254237,1.0995762711864405,1.035593220338983,1.001906779661017,0.96822033898305082,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.952542372881355},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.804004237288133},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.650355932203389},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.292033898305084},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8795593220338986},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.6483622881355942},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.4111016949152546}]
[null,67,19.952542372881354,13.767254237288133,19.475847457627115,13.535713983050844,18.99915254237288,13.299406779661014,18,12.959999999999999,16.947457627118641,12.541118644067794,16.390677966101695,12.37496186440678,15.833898305084746,12.192101694915255,null,1.1084745762711863,1.0819915254237287,1.0555084745762711,1,0.94152542372881343,0.91059322033898304,0.87966101694915255,0.69,0.69499999999999995,0.7,0.72,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.767254237288133},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.535713983050844},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.299406779661014},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.959999999999999},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.541118644067794},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.37496186440678},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.192101694915255}]
[null,62,18.236440677966101,16.230432203389832,17.832203389830511,16.851432203389834,17.427966101694913,17.427966101694913,{"$f":"U14*$I$13","v":16.665254237288135},16.665254237288135,15.872033898305084,15.872033898305084,15.444915254237287,15.444915254237287,15.017796610169491,15.017796610169491,null,1.013135593220339,0.99067796610169501,0.96822033898305082,0.92584745762711862,0.88177966101694905,0.85805084745762705,0.83432203389830506,0.89,0.94500000000000006,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.230432203389832,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.851432203389834},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.427966101694913},16.665254237288135,15.872033898305084,15.444915254237287,15.017796610169491]
[null,57,18.076271186440678,18.076271186440678,17.72923728813559,17.72923728813559,17.382203389830508,17.382203389830508,16.642372881355932,16.642372881355932,15.849152542372881,15.849152542372881,15.422033898305083,15.422033898305083,14.994915254237286,14.994915254237286,null,1.0042372881355932,0.98495762711864387,0.96567796610169487,0.92457627118644059,0.88050847457627113,0.85677966101694902,0.83305084745762703,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.076271186440678,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.72923728813559},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.382203389830508},16.642372881355932,15.849152542372881,15.422033898305083,14.994915254237286]
[900,72,22.179661016949147,11.533423728813556,21.66101694915254,11.372033898305084,21.142372881355929,11.205457627118642,20.005932203389829,10.803203389830509,18.82372881355932,10.353050847457627,18.202118644067799,10.193186440677968,17.58050847457627,10.020889830508473,null,1.2322033898305083,1.2033898305084745,1.1745762711864405,1.1114406779661017,1.0457627118644066,1.0112288135593221,0.97669491525423724,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.533423728813556},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.372033898305084},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.205457627118642},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.803203389830509},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.353050847457627},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.193186440677968},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.020889830508473}]
[null,67,20.242372881355934,14.574508474576271,19.750423728813558,14.417809322033897,19.258474576271183,14.251271186440675,18.228813559322035,13.853898305084746,17.145762711864407,13.373694915254237,16.57372881355932,13.176114406779661,16.001694915254237,12.961372881355933,null,1.1245762711864407,1.0972457627118644,1.0699152542372881,1.0127118644067796,0.9525423728813559,0.92076271186440672,0.88898305084745755,0.72,0.73,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.574508474576271},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.417809322033897},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.251271186440675},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.853898305084746},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.373694915254237},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.176114406779661},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.961372881355933}]
[null,62,18.762711864406779,18.762711864406779,18.388983050847457,18.388983050847457,18.015254237288136,18.015254237288136,17.222033898305082,17.222033898305082,16.383050847457625,16.383050847457625,15.929237288135591,15.929237288135591,15.475423728813558,15.475423728813558,null,1.0423728813559321,1.0216101694915254,1.0008474576271187,0.956779661016949,0.9101694915254237,0.8849576271186439,0.85974576271186431,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.762711864406779,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.388983050847457},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.015254237288136},17.222033898305082,16.383050847457625,15.929237288135591,15.475423728813558]
[null,57,18.732203389830506,18.732203389830506,18.362288135593218,18.362288135593218,17.992372881355934,17.992372881355934,17.199152542372882,17.199152542372882,16.360169491525422,16.360169491525422,15.910169491525421,15.910169491525421,15.460169491525424,15.460169491525424,null,1.0406779661016947,1.0201271186440677,0.99957627118644066,0.95550847457627119,0.90889830508474567,0.88389830508474565,0.85889830508474574,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.732203389830506,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.362288135593218},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.992372881355934},17.199152542372882,16.360169491525422,15.910169491525421,15.460169491525424]

{"sheet":"NXA6_30","index":44,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":21.455244755244756},{"$f":"IF(AM8>C8,C8,AM8)","v":10.51306993006993},{"$f":"S8*$I$13","v":20.980069930069931},{"$f":"IF(AN8>E8,E8,AN8)","v":10.385134615384615},{"$f":"T8*$I$13","v":20.504895104895102},{"$f":"IF(AO8>G8,G8,AO8)","v":10.252447552447551},{"$f":"U8*$I$13","v":19.51048951048951},{"$f":"IF(AP8>I8,I8,AP8)","v":9.755244755244755},{"$f":"V8*$I$13","v":18.453146853146855},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.4111048951048968},{"$f":"W8*$I$13","v":17.883566433566433},{"$f":"IF(AR8>M8,M8,AR8)","v":9.2994545454545445},{"$f":"X8*$I$13","v":17.313986013986014},{"$f":"IF(AS8>O8,O8,AS8)","v":9.176412587412587},null,1.191958041958042,1.1655594405594405,1.139160839160839,1.083916083916084,1.0251748251748252,0.99353146853146845,0.96188811188811185,0.49,0.495,0.5,0.5,0.51,0.52,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.51306993006993},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.385134615384615},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.252447552447551},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.755244755244755},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.4111048951048968},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.2994545454545445},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.176412587412587}]
[null,67,19.504195804195803,12.872769230769231,19.06993006993007,{"$f":"IF(AN9>E9,E9,AN9)","v":12.776853146853147},18.635664335664334,{"$f":"IF(AO9>G9,G9,AO9)","v":12.672251748251748},{"$f":"U9*$I$13","v":17.723076923076921},{"$f":"IF(AP9>I9,I9,AP9)","v":12.228923076923074},16.747552447552447,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.890762237762237},16.22202797202797,{"$f":"IF(AR9>M9,M9,AR9)","v":11.679860139860137},15.696503496503496,{"$f":"IF(AS9>O9,O9,AS9)","v":11.458447552447552},null,1.0835664335664335,1.0594405594405594,1.0353146853146853,0.98461538461538456,0.93041958041958039,0.90122377622377614,0.872027972027972,0.66,0.67,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.872769230769231},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.776853146853147},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.672251748251748},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.228923076923074},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.890762237762237},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.679860139860137},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.458447552447552}]
[null,62,17.817482517482517,15.323034965034966,17.430419580419578,15.164465034965033,17.043356643356642,14.998153846153844,{"$f":"U10*$I$13","v":16.237762237762237},14.613986013986013,15.457342657342656,15.457342657342656,15.054545454545455,15.054545454545455,14.651748251748252,14.651748251748252,null,0.98986013986013976,0.96835664335664329,0.9468531468531467,0.90209790209790208,0.85874125874125862,0.83636363636363642,0.813986013986014,0.86,0.87,0.88,0.9,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.323034965034966,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.164465034965033},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.998153846153844},14.613986013986013,15.457342657342656,15.054545454545455,14.651748251748252]
[null,57,17.471328671328671,17.471328671328671,17.156643356643357,17.156643356643357,16.841958041958044,16.841958041958044,{"$f":"U11*$I$13","v":16.168531468531469},16.168531468531469,15.432167832167831,15.432167832167831,15.032517482517481,15.032517482517481,14.632867132867133,14.632867132867133,null,0.9706293706293706,0.9531468531468531,0.93566433566433571,0.89825174825174825,0.85734265734265724,0.83513986013986008,0.81293706293706292,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.471328671328671,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.156643356643357},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.841958041958044},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.168531468531469},15.432167832167831,15.032517482517481,14.632867132867133]
[1000,72,21.820279720279721,11.128342657342658,21.323076923076922,10.87476923076923,20.825874125874126,10.621195804195805,{"$f":"U12*$I$13","v":19.793706293706293},10.292727272727273,18.698601398601397,10.097244755244756,18.106993006993005,9.8683111888111874,17.515384615384612,9.6334615384615372,null,1.2122377622377623,1.1846153846153846,1.156993006993007,1.0996503496503496,1.0388111888111888,1.0059440559440558,0.97307692307692295,0.51,0.51,0.51,0.52,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.128342657342658},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.87476923076923},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.621195804195805},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.292727272727273},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.097244755244756},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8683111888111874},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6334615384615372}]
[null,67,19.856643356643357,13.899650349650349,19.400349650349654,13.677246503496505,18.944055944055947,13.450279720279722,18,13.14,16.993006993006993,12.744755244755245,16.448601398601397,12.583180069930069,15.904195804195803,12.405272727272727,null,1.1031468531468531,1.0777972027972029,1.0524475524475525,1,0.94405594405594406,0.91381118881118872,0.8835664335664335,0.7,0.70499999999999996,0.71,0.73,0.75,0.76500000000000001,0.78,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.899650349650349},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.677246503496505},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.450279720279722},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.744755244755245},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.583180069930069},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.405272727272727}]
[null,62,18.270629370629372,18.087923076923079,17.911888111888111,17.82232867132867,17.553146853146853,17.553146853146853,{"$f":"U14*$I$13","v":16.829370629370629},16.829370629370629,16.048951048951047,16.048951048951047,15.62097902097902,15.62097902097902,15.193006993006993,15.193006993006993,null,1.015034965034965,0.99510489510489508,0.97517482517482512,0.93496503496503491,0.89160839160839156,0.86783216783216777,0.84405594405594409,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.087923076923079,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.82232867132867},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.553146853146853},16.829370629370629,16.048951048951047,15.62097902097902,15.193006993006993]
[null,57,18.207692307692305,18.207692307692305,17.864685314685314,17.864685314685314,17.521678321678319,17.521678321678319,16.804195804195803,16.804195804195803,16.023776223776224,16.023776223776224,15.598951048951047,15.598951048951047,15.174125874125874,15.174125874125874,null,1.0115384615384615,0.99248251748251737,0.97342657342657335,0.93356643356643354,0.89020979020979019,0.86660839160839154,0.843006993006993,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.207692307692305,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.864685314685314},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.521678321678319},16.804195804195803,16.023776223776224,15.598951048951047,15.174125874125874]
[1125,72,22.084615384615386,11.484000000000002,21.568531468531468,11.323479020979022,21.052447552447553,11.157797202797203,19.988811188811191,10.993846153846155,18.862237762237761,10.562853146853147,18.254895104895102,10.314015734265732,17.647552447552446,10.059104895104893,null,1.226923076923077,1.1982517482517483,1.1695804195804196,1.1104895104895105,1.0479020979020979,1.014160839160839,0.98041958041958033,0.52,0.52500000000000002,0.53,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.484000000000002},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.323479020979022},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.157797202797203},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.993846153846155},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.562853146853147},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.314015734265732},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.059104895104893}]
[null,67,20.114685314685314,14.683720279720278,19.645804195804196,14.537895104895105,19.176923076923078,14.382692307692309,18.207692307692305,14.019923076923074,17.175524475524472,13.568664335664334,16.618531468531469,13.377917832167832,16.061538461538461,13.170461538461538,null,1.1174825174825174,1.0914335664335664,1.0653846153846154,1.0115384615384615,0.95419580419580408,0.92325174825174827,0.89230769230769225,0.73,0.74,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.683720279720278},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.537895104895105},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.382692307692309},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.019923076923074},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.568664335664334},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.377917832167832},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.170461538461538}]
[null,62,18.837062937062939,18.837062937062939,18.475174825174822,18.475174825174822,18.113286713286712,18.113286713286712,17.351748251748251,17.351748251748251,16.527272727272727,16.527272727272727,16.077272727272728,16.077272727272728,15.627272727272725,15.627272727272725,null,1.0465034965034965,1.0263986013986013,1.0062937062937063,0.96398601398601391,0.91818181818181821,0.89318181818181819,0.86818181818181805,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.837062937062939,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.475174825174822},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.113286713286712},17.351748251748251,16.527272727272727,16.077272727272728,15.627272727272725]
[null,57,18.811888111888113,18.811888111888113,18.45,18.45,18.088111888111886,18.088111888111886,17.326573426573425,17.326573426573425,16.502097902097901,16.502097902097901,16.055244755244754,16.055244755244754,15.608391608391607,15.608391608391607,null,1.0451048951048951,1.0249999999999999,1.0048951048951047,0.96258741258741254,0.91678321678321673,0.89195804195804185,0.86713286713286708,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.811888111888113,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.45},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.088111888111886},17.326573426573425,16.502097902097901,16.055244755244754,15.608391608391607]

{"sheet":"NXA6_36","index":45,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.484883720930235},{"$f":"IF(AM8>C8,C8,AM8)","v":10.742441860465117},{"$f":"S8*$I$13","v":21.003488372093024},{"$f":"IF(AN8>E8,E8,AN8)","v":10.501744186046512},{"$f":"T8*$I$13","v":20.522093023255813},{"$f":"IF(AO8>G8,G8,AO8)","v":10.261046511627907},{"$f":"U8*$I$13","v":19.501744186046515},{"$f":"IF(AP8>I8,I8,AP8)","v":9.9458895348837224},{"$f":"V8*$I$13","v":18.418604651162791},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.5776744186046514},{"$f":"W8*$I$13","v":17.845639534883723},{"$f":"IF(AR8>M8,M8,AR8)","v":9.4581889534883743},{"$f":"X8*$I$13","v":17.272674418604652},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3272441860465118},null,1.1936046511627909,1.1668604651162791,1.1401162790697674,1.0834302325581397,1.0232558139534884,0.99142441860465136,0.95959302325581397,0.5,0.5,0.5,0.51,0.52,0.53,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.742441860465117},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.501744186046512},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.261046511627907},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.9458895348837224},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.5776744186046514},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.4581889534883743},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3272441860465118}]
[null,67,19.533139534883723,13.087203488372095,19.093604651162789,{"$f":"IF(AN9>E9,E9,AN9)","v":12.983651162790695},18.654069767441861,{"$f":"IF(AO9>G9,G9,AO9)","v":12.871308139534882},{"$f":"U9*$I$13","v":17.722674418604651},{"$f":"IF(AP9>I9,I9,AP9)","v":12.405872093023255},16.723255813953489,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.040744186046512},16.197383720930233,{"$f":"IF(AR9>M9,M9,AR9)","v":11.905077034883721},15.671511627906977,{"$f":"IF(AS9>O9,O9,AS9)","v":11.753633720930232},null,1.0851744186046512,1.0607558139534883,1.0363372093023255,0.98459302325581388,0.92906976744186054,0.89985465116279073,0.87063953488372092,0.67,0.67999999999999994,0.69,0.7,0.72,0.73499999999999999,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.087203488372095},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.983651162790695},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.871308139534882},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.405872093023255},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.040744186046512},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.905077034883721},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.753633720930232}]
[null,62,17.837790697674421,15.697255813953491,17.442732558139536,15.524031976744187,17.04767441860465,15.342906976744185,{"$f":"U10*$I$13","v":16.220930232558139},14.923255813953489,15.420348837209303,15.420348837209303,15.022674418604652,15.022674418604652,14.625,14.625,null,0.99098837209302337,0.96904069767441869,0.9470930232558139,0.90116279069767447,0.85668604651162794,0.83459302325581397,0.8125,0.88,0.89,0.9,0.92,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.697255813953491,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.524031976744187},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.342906976744185},14.923255813953489,15.420348837209303,15.022674418604652,14.625]
[null,57,17.466279069767445,17.466279069767445,17.147093023255813,17.147093023255813,16.827906976744185,16.827906976744185,{"$f":"U11*$I$13","v":16.142441860465116},16.142441860465116,15.399418604651164,15.399418604651164,15.001744186046514,15.001744186046514,14.604069767441862,14.604069767441862,null,0.97034883720930243,0.95261627906976731,0.93488372093023253,0.89680232558139539,0.8555232558139535,0.83343023255813964,0.81133720930232567,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.466279069767445,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.147093023255813},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.827906976744185},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.142441860465116},15.399418604651164,15.001744186046514,14.604069767441862]
[1200,72,21.856395348837214,11.365325581395352,21.351453488372098,11.102755813953491,20.846511627906981,10.840186046511631,{"$f":"U12*$I$13","v":19.789534883720933},10.488453488372095,18.664534883720933,10.265494186046514,18.068023255813955,10.027752906976746,17.471511627906978,9.7840465116279081,null,1.2142441860465119,1.1861918604651165,1.1581395348837211,1.0994186046511629,1.0369186046511629,1.003779069767442,0.97063953488372101,0.52,0.52,0.52,0.53,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.365325581395352},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.102755813953491},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.840186046511631},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.488453488372095},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.265494186046514},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.027752906976746},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7840465116279081}]
[null,67,19.894186046511631,14.124872093023258,19.431104651162794,13.893239825581396,18.968023255813954,13.656976744186046,18,13.32,16.974418604651163,13.070302325581396,16.42761627906977,12.813540697674421,15.880813953488374,12.545843023255816,null,1.105232558139535,1.0795058139534885,1.0537790697674418,1,0.94302325581395341,0.91264534883720938,0.88226744186046524,0.71,0.71499999999999997,0.72,0.74,0.77,0.78,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.124872093023258},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.893239825581396},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.656976744186046},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.070302325581396},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.813540697674421},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.545843023255816}]
[null,62,18.282558139534881,16.819953488372093,17.913662790697675,17.197116279069768,17.544767441860468,17.544767441860468,{"$f":"U14*$I$13","v":16.806976744186045},16.806976744186045,16.011627906976745,16.011627906976745,15.585174418604652,15.585174418604652,15.158720930232558,15.158720930232558,null,1.0156976744186046,0.99520348837209305,0.97470930232558151,0.93372093023255809,0.88953488372093026,0.86584302325581397,0.84215116279069768,0.92,0.96,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.819953488372093,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.197116279069768},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.544767441860468},16.806976744186045,16.011627906976745,15.585174418604652,15.158720930232558]
[null,57,18.209302325581397,18.209302325581397,17.861337209302327,17.861337209302327,17.513372093023257,17.513372093023257,16.780813953488373,16.780813953488373,15.98546511627907,15.98546511627907,15.561627906976746,15.561627906976746,15.137790697674419,15.137790697674419,null,1.0116279069767442,0.992296511627907,0.97296511627906979,0.93226744186046517,0.88808139534883723,0.86453488372093035,0.84098837209302324,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.209302325581397,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.861337209302327},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.513372093023257},16.780813953488373,15.98546511627907,15.561627906976746,15.137790697674419]
[1350,72,22.123255813953488,11.725325581395349,21.602616279069768,11.557399709302326,21.081976744186047,11.384267441860466,19.983139534883719,11.190558139534884,18.826744186046511,10.73124418604651,18.217151162790696,10.565947674418602,17.607558139534884,10.388459302325581,null,1.2290697674418605,1.2001453488372094,1.1712209302325582,1.1101744186046512,1.0459302325581394,1.012063953488372,0.97819767441860461,0.53,0.53500000000000003,0.54,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.725325581395349},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.557399709302326},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.384267441860466},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.190558139534884},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.73124418604651},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.565947674418602},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.388459302325581}]
[null,67,20.150581395348837,14.911430232558139,19.677034883720935,14.757776162790702,19.203488372093027,14.594651162790701,18.209302325581397,14.20325581395349,17.152325581395349,13.893383720930233,16.595058139534885,13.690922965116279,16.037790697674421,13.471744186046513,null,1.1194767441860465,1.0931686046511631,1.0668604651162792,1.0116279069767442,0.95290697674418612,0.9219476744186047,0.89098837209302328,0.74,0.75,0.76,0.78,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.911430232558139},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.757776162790702},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.594651162790701},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.20325581395349},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.893383720930233},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.690922965116279},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.471744186046513}]
[null,62,18.842441860465119,18.842441860465119,18.476162790697675,18.476162790697675,18.109883720930231,18.109883720930231,17.330232558139535,17.330232558139535,16.48779069767442,16.48779069767442,16.040406976744187,16.040406976744187,15.593023255813955,15.593023255813955,null,1.0468023255813954,1.026453488372093,1.0061046511627907,0.96279069767441861,0.91598837209302331,0.89113372093023258,0.86627906976744196,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.842441860465119,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.476162790697675},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.109883720930231},17.330232558139535,16.48779069767442,16.040406976744187,15.593023255813955]
[null,57,18.816279069767447,18.816279069767447,18.450000000000003,18.450000000000003,18.083720930232559,18.083720930232559,17.309302325581395,17.309302325581395,16.46686046511628,16.46686046511628,16.019476744186047,16.019476744186047,15.572093023255816,15.572093023255816,null,1.0453488372093025,1.0250000000000001,1.0046511627906978,0.96162790697674416,0.91482558139534886,0.88997093023255824,0.86511627906976751,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.816279069767447,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.450000000000003},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.083720930232559},17.309302325581395,16.46686046511628,16.019476744186047,15.572093023255816]

{"sheet":"NXA6_42","index":46,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.504578313253013},{"$f":"IF(AM8>C8,C8,AM8)","v":10.537243373493975},{"$f":"S8*$I$13","v":21.012289156626508},{"$f":"IF(AN8>E8,E8,AN8)","v":10.29602168674699},{"$f":"T8*$I$13","v":20.520000000000003},{"$f":"IF(AO8>G8,G8,AO8)","v":10.054800000000002},{"$f":"U8*$I$13","v":19.466024096385542},{"$f":"IF(AP8>I8,I8,AP8)","v":9.7330120481927711},{"$f":"V8*$I$13","v":18.346987951807229},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3569638554216876},{"$f":"W8*$I$13","v":17.757108433734938},{"$f":"IF(AR8>M8,M8,AR8)","v":9.1449108433734931},{"$f":"X8*$I$13","v":17.167228915662651},{"$f":"IF(AS8>O8,O8,AS8)","v":8.926959036144579},null,1.1946987951807229,1.1673493975903615,1.1400000000000001,1.0814457831325301,1.0192771084337349,0.98650602409638544,0.95373493975903612,0.49,0.49,0.49,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.537243373493975},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.29602168674699},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.054800000000002},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.7330120481927711},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3569638554216876},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.1449108433734931},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.926959036144579}]
[null,67,19.591807228915663,12.930592771084338,19.142891566265064,{"$f":"IF(AN9>E9,E9,AN9)","v":12.730022891566268},18.693975903614458,{"$f":"IF(AO9>G9,G9,AO9)","v":12.524963855421687},{"$f":"U9*$I$13","v":17.739759036144576},{"$f":"IF(AP9>I9,I9,AP9)","v":12.240433734939757},16.720481927710843,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.871542168674697},16.182650602409637,{"$f":"IF(AR9>M9,M9,AR9)","v":11.651508433734939},15.644819277108434,{"$f":"IF(AS9>O9,O9,AS9)","v":11.420718072289157},null,1.088433734939759,1.0634939759036146,1.03855421686747,0.98554216867469879,0.92891566265060233,0.89903614457831327,0.8691566265060241,0.66,0.66500000000000004,0.67,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.930592771084338},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.730022891566268},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.524963855421687},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.240433734939757},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.871542168674697},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.651508433734939},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.420718072289157}]
[null,62,17.921927710843374,15.233638554216867,17.525060240963853,15.071551807228914,17.128192771084336,14.901527710843373,{"$f":"U10*$I$13","v":16.2910843373494},14.499065060240966,15.462650602409639,15.462650602409639,15.057108433734941,15.057108433734941,14.651566265060241,14.651566265060241,null,0.99566265060240966,0.97361445783132528,0.951566265060241,0.90506024096385551,0.85903614457831323,0.83650602409638564,0.81397590361445782,0.85,0.86,0.87,0.89,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.233638554216867,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.071551807228914},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.901527710843373},14.499065060240966,15.462650602409639,15.057108433734941,14.651566265060241]
[null,57,17.544578313253012,17.544578313253012,17.22144578313253,17.22144578313253,16.898313253012049,16.898313253012049,{"$f":"U11*$I$13","v":16.195662650602412},16.195662650602412,15.440963855421687,15.440963855421687,15.035421686746988,15.035421686746988,14.629879518072288,14.629879518072288,null,0.974698795180723,0.95674698795180724,0.93879518072289159,0.89975903614457842,0.85783132530120487,0.83530120481927705,0.81277108433734935,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.544578313253012,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.22144578313253},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.898313253012049},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.195662650602412},15.440963855421687,15.035421686746988,14.629879518072288]
[1400,72,21.860240963855421,10.930120481927711,21.344096385542169,10.778768674698796,20.827951807228917,10.622255421686749,{"$f":"U12*$I$13","v":19.726265060240966},10.257657831325302,18.572530120481925,9.8434409638554214,17.958795180722891,9.6977493975903624,17.345060240963857,9.5397831325301219,null,1.2144578313253012,1.1857831325301205,1.1571084337349398,1.0959036144578314,1.0318072289156626,0.99771084337349403,0.96361445783132538,0.5,0.505,0.51,0.52,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.930120481927711},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.778768674698796},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.622255421686749},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.257657831325302},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8434409638554214},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.6977493975903624},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.5397831325301219}]
[null,67,19.930120481927712,13.75178313253012,19.463855421686745,13.62469879518072,18.997590361445781,13.488289156626504,18,12.959999999999999,16.946024096385543,12.709518072289157,16.390843373493976,12.457040963855421,15.835662650602409,12.193460240963855,null,1.1072289156626507,1.0813253012048192,1.0554216867469879,1,0.94144578313253013,0.91060240963855421,0.87975903614457829,0.69,0.7,0.71,0.72,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.75178313253012},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.62469879518072},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.488289156626504},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.959999999999999},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.709518072289157},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.457040963855421},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.193460240963855}]
[null,62,18.351325301204817,16.332679518072286,17.969638554216868,16.981308433734942,17.587951807228915,17.587951807228915,{"$f":"U14*$I$13","v":16.837590361445784},16.837590361445784,16.022168674698793,16.022168674698793,15.586265060240965,15.586265060240965,15.150361445783131,15.150361445783131,null,1.0195180722891566,0.99831325301204821,0.97710843373493972,0.935421686746988,0.89012048192771076,0.86590361445783137,0.84168674698795176,0.89,0.94500000000000006,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.332679518072286,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.981308433734942},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.587951807228915},16.837590361445784,16.022168674698793,15.586265060240965,15.150361445783131]
[null,57,18.260240963855424,18.260240963855424,17.913253012048191,17.913253012048191,17.566265060240966,17.566265060240966,16.81156626506024,16.81156626506024,16.000481927710844,16.000481927710844,15.566746987951808,15.566746987951808,15.133012048192771,15.133012048192771,null,1.0144578313253012,0.99518072289156623,0.97590361445783136,0.93397590361445781,0.8889156626506024,0.86481927710843376,0.84072289156626512,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.260240963855424,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.913253012048191},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.566265060240966},16.81156626506024,16.000481927710844,15.566746987951808,15.133012048192771]
[1575,72,22.111807228915662,11.498139759036144,21.578313253012048,11.328614457831327,21.044819277108438,11.153754216867473,19.912771084337351,10.75289638554217,18.719999999999995,10.483199999999998,18.088915662650603,10.220237349397589,17.457831325301203,9.9509638554216853,null,1.2284337349397589,1.1987951807228916,1.1691566265060243,1.1062650602409638,1.0399999999999998,1.0049397590361446,0.96987951807228912,0.52,0.52500000000000002,0.53,0.54,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.498139759036144},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.328614457831327},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.153754216867473},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.75289638554217},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.483199999999998},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.220237349397589},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.9509638554216853}]
[null,67,20.181686746987953,14.530814457831326,19.700240963855421,14.381175903614457,19.218795180722893,14.22190843373494,18.195180722891568,13.828337349397591,17.110843373493978,13.517566265060243,16.54265060240964,13.31683373493976,15.974457831325299,13.099055421686744,null,1.1212048192771085,1.0944578313253013,1.0677108433734941,1.0108433734939759,0.95060240963855425,0.91903614457831329,0.88746987951807221,0.72,0.73,0.74,0.76,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.530814457831326},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.381175903614457},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.22190843373494},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.828337349397591},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.517566265060243},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.31683373493976},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.099055421686744}]
[null,62,18.876144578313252,18.876144578313252,18.507469879518077,18.507469879518077,18.138795180722894,18.138795180722894,17.332048192771083,17.332048192771083,16.47325301204819,16.47325301204819,16.013493975903614,16.013493975903614,15.553734939759035,15.553734939759035,null,1.0486746987951807,1.0281927710843375,1.007710843373494,0.96289156626506023,0.91518072289156616,0.88963855421686755,0.86409638554216861,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.876144578313252,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.507469879518077},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.138795180722894},17.332048192771083,16.47325301204819,16.013493975903614,15.553734939759035]
[null,57,18.850120481927711,18.850120481927711,18.481445783132529,18.481445783132529,18.112771084337346,18.112771084337346,17.31036144578313,17.31036144578313,16.45156626506024,16.45156626506024,15.991807228915665,15.991807228915665,15.532048192771084,15.532048192771084,null,1.0472289156626506,1.0267469879518072,1.0062650602409637,0.96168674698795176,0.9139759036144578,0.88843373493975919,0.86289156626506025,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.850120481927711,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.481445783132529},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.112771084337346},17.31036144578313,16.45156626506024,15.991807228915665,15.532048192771084]

{"sheet":"NXA6_48","index":47,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.78},{"$f":"IF(AM8>C8,C8,AM8)","v":10.89},{"$f":"S8*$I$13","v":21.23413043478261},{"$f":"IF(AN8>E8,E8,AN8)","v":10.723235869565219},{"$f":"T8*$I$13","v":20.688260869565216},{"$f":"IF(AO8>G8,G8,AO8)","v":10.55101304347826},{"$f":"U8*$I$13","v":19.569130434782611},{"$f":"IF(AP8>I8,I8,AP8)","v":10.175947826086958},{"$f":"V8*$I$13","v":18.399130434782609},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.751539130434784},{"$f":"W8*$I$13","v":17.788695652173914},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5169521739130438},{"$f":"X8*$I$13","v":17.178260869565214},{"$f":"IF(AS8>O8,O8,AS8)","v":9.2762608695652169},null,1.21,1.1796739130434784,1.1493478260869565,1.0871739130434783,1.0221739130434784,0.98826086956521741,0.95434782608695645,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.89},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.723235869565219},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.55101304347826},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.175947826086958},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.751539130434784},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5169521739130438},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.2762608695652169}]
[null,67,19.721739130434781,13.410782608695651,19.232608695652171,{"$f":"IF(AN9>E9,E9,AN9)","v":13.270499999999997},18.743478260869562,{"$f":"IF(AO9>G9,G9,AO9)","v":13.120434782608692},{"$f":"U9*$I$13","v":17.745652173913044},{"$f":"IF(AP9>I9,I9,AP9)","v":12.776869565217391},16.704782608695652,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.361539130434782},16.155000000000001,{"$f":"IF(AR9>M9,M9,AR9)","v":12.116250000000001},15.605217391304349,{"$f":"IF(AS9>O9,O9,AS9)","v":11.859965217391306},null,1.0956521739130434,1.0684782608695651,1.0413043478260868,0.98586956521739133,0.92804347826086953,0.89749999999999996,0.86695652173913051,0.68,0.69,0.7,0.72,0.74,0.75,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.410782608695651},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.270499999999997},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.120434782608692},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.776869565217391},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.361539130434782},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.116250000000001},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.859965217391306}]
[null,62,17.95304347826087,15.978208695652174,17.534347826086957,15.780913043478263,17.115652173913045,15.575243478260871,{"$f":"U10*$I$13","v":16.282173913043479},16.119352173913043,15.487826086956522,15.487826086956522,15.076956521739129,15.076956521739129,14.666086956521738,14.666086956521738,null,0.99739130434782619,0.97413043478260875,0.9508695652173913,0.90456521739130435,0.86043478260869566,0.83760869565217388,0.81478260869565211,0.89,0.9,0.91,0.99,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.978208695652174,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.780913043478263},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.575243478260871},16.119352173913043,15.487826086956522,15.076956521739129,14.666086956521738]
[null,57,17.624347826086954,17.624347826086954,17.283913043478261,17.283913043478261,16.943478260869565,16.943478260869565,{"$f":"U11*$I$13","v":16.231304347826086},16.231304347826086,15.464347826086957,15.464347826086957,15.055434782608698,15.055434782608698,14.646521739130435,14.646521739130435,null,0.97913043478260864,0.96021739130434791,0.94130434782608685,0.90173913043478249,0.85913043478260875,0.83641304347826095,0.81369565217391304,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.624347826086954,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.283913043478261},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.943478260869565},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.231304347826086},15.464347826086957,15.055434782608698,14.646521739130435]
[1600,72,22.15173913043478,11.518904347826087,21.578478260869563,11.328701086956521,21.005217391304349,11.132765217391306,{"$f":"U12*$I$13","v":19.831304347826087},10.708904347826088,18.618260869565219,10.240043478260871,17.982391304347825,10.070139130434782,17.346521739130434,9.8875173913043461,null,1.2306521739130434,1.1988043478260868,1.1669565217391304,1.1017391304347826,1.0343478260869565,0.99902173913043479,0.96369565217391295,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.518904347826087},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.328701086956521},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.132765217391306},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.708904347826088},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.240043478260871},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.070139130434782},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8875173913043461}]
[null,67,20.062173913043477,14.444765217391303,19.553478260869564,14.176271739130433,19.044782608695655,13.902691304347828,18,13.5,16.916086956521738,13.194547826086957,16.348695652173916,12.997213043478263,15.781304347826087,12.782856521739131,null,1.1145652173913043,1.086304347826087,1.0580434782608696,1,0.93978260869565211,0.90826086956521745,0.87673913043478258,0.72,0.72499999999999998,0.73,0.75,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.444765217391303},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.176271739130433},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.902691304347828},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.194547826086957},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.997213043478263},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.782856521739131}]
[null,62,18.422608695652173,18.238382608695652,18.037173913043478,17.94698804347826,17.651739130434784,17.651739130434784,{"$f":"U14*$I$13","v":16.869130434782608},16.869130434782608,16.039565217391306,16.039565217391306,15.595434782608697,15.595434782608697,15.151304347826086,15.151304347826086,null,1.0234782608695652,1.0020652173913043,0.98065217391304349,0.9371739130434783,0.89108695652173919,0.86641304347826098,0.84173913043478255,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.238382608695652,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.94698804347826},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.651739130434784},16.869130434782608,16.039565217391306,15.595434782608697,15.151304347826086]
[null,57,18.363913043478259,18.363913043478259,17.996086956521737,17.996086956521737,17.628260869565217,17.628260869565217,16.845652173913042,16.845652173913042,16.01608695652174,16.01608695652174,15.573913043478258,15.573913043478258,15.131739130434783,15.131739130434783,null,1.0202173913043477,0.99978260869565205,0.97934782608695647,0.93586956521739129,0.88978260869565218,0.86521739130434772,0.84065217391304348,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.363913043478259,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.996086956521737},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.628260869565217},16.845652173913042,16.01608695652174,15.573913043478258,15.131739130434783]
[1800,72,22.41391304347826,12.103513043478261,21.821086956521739,11.89249239130435,21.228260869565219,11.675543478260872,20.015217391304351,11.208521739130438,18.759130434782605,10.88029565217391,18.105652173913043,10.59180652173913,17.452173913043481,10.296782608695652,null,1.2452173913043478,1.2122826086956522,1.1793478260869565,1.1119565217391305,1.0421739130434782,1.0058695652173912,0.96956521739130441,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.58499999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.103513043478261},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.89249239130435},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.675543478260872},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.208521739130438},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.88029565217391},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.59180652173913},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.296782608695652}]
[null,67,20.316521739130437,15.237391304347828,19.790217391304349,15.040565217391306,19.263913043478261,14.833213043478262,18.187826086956523,14.368382608695654,17.072608695652175,13.999539130434782,16.491521739130434,13.770420652173911,15.910434782608695,13.523869565217391,null,1.1286956521739131,1.0994565217391306,1.0702173913043478,1.0104347826086957,0.94847826086956533,0.91619565217391297,0.88391304347826083,0.75,0.76,0.77,0.79,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.237391304347828},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.040565217391306},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.833213043478262},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.368382608695654},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.999539130434782},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.770420652173911},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.523869565217391}]
[null,62,18.989999999999998,18.989999999999998,18.590869565217393,18.590869565217393,18.191739130434787,18.191739130434787,17.358260869565218,17.358260869565218,16.473913043478262,16.473913043478262,16.004347826086956,16.004347826086956,15.534782608695652,15.534782608695652,null,1.0549999999999999,1.0328260869565218,1.0106521739130436,0.96434782608695646,0.91521739130434787,0.88913043478260878,0.86304347826086958,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.989999999999998,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.590869565217393},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.191739130434787},17.358260869565218,16.473913043478262,16.004347826086956,15.534782608695652]
[null,57,18.966521739130432,18.966521739130432,18.567391304347826,18.567391304347826,18.16826086956522,18.16826086956522,17.334782608695651,17.334782608695651,16.458260869565219,16.458260869565219,15.986739130434785,15.986739130434785,15.515217391304347,15.515217391304347,null,1.0536956521739129,1.0315217391304348,1.0093478260869566,0.96304347826086956,0.91434782608695653,0.88815217391304357,0.8619565217391304,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.966521739130432,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.567391304347826},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.16826086956522},17.334782608695651,16.458260869565219,15.986739130434785,15.515217391304347]

{"sheet":"NXA6_49","index":48,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_49"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.494999999999997},{"$f":"IF(AM8>C8,C8,AM8)","v":10.747499999999999},{"$f":"S8*$I$13","v":20.977499999999999},{"$f":"IF(AN8>E8,E8,AN8)","v":10.5936375},{"$f":"T8*$I$13","v":20.46},{"$f":"IF(AO8>G8,G8,AO8)","v":10.434600000000001},{"$f":"U8*$I$13","v":19.4175},{"$f":"IF(AP8>I8,I8,AP8)","v":10.097100000000001},{"$f":"V8*$I$13","v":18.356249999999999},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7288125000000001},{"$f":"W8*$I$13","v":17.799375000000001},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5226656250000019},{"$f":"X8*$I$13","v":17.2425},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3109500000000001},null,1.1941666666666666,1.1654166666666665,1.1366666666666667,1.0787500000000001,1.0197916666666667,0.9888541666666667,0.95791666666666664,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.747499999999999},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.5936375},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.434600000000001},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.097100000000001},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7288125000000001},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5226656250000019},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3109500000000001}]
[null,67,19.612500000000001,13.336500000000001,19.147500000000001,{"$f":"IF(AN9>E9,E9,AN9)","v":13.116037500000001},18.682499999999997,{"$f":"IF(AO9>G9,G9,AO9)","v":12.890924999999998},{"$f":"U9*$I$13","v":17.73},{"$f":"IF(AP9>I9,I9,AP9)","v":12.5883},16.758749999999999,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.066299999999998},16.248750000000001,{"$f":"IF(AR9>M9,M9,AR9)","v":11.942831250000001},15.73875,{"$f":"IF(AS9>O9,O9,AS9)","v":11.804062500000001},null,1.0895833333333333,1.06375,1.0379166666666666,0.98499999999999999,0.93104166666666666,0.90270833333333333,0.87437500000000001,0.68,0.68500000000000005,0.69,0.71,0.72,0.73499999999999999,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.336500000000001},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.116037500000001},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.890924999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.5883},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.066299999999998},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.942831250000001},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.804062500000001}]
[null,62,17.924999999999997,15.594749999999998,17.512500000000003,15.411000000000003,17.100000000000001,15.219000000000001,{"$f":"U10*$I$13","v":16.259999999999998},14.959199999999999,15.404999999999999,14.480699999999999,14.996249999999998,14.546362499999997,14.5875,14.5875,null,0.99583333333333324,0.97291666666666676,0.95000000000000007,0.90333333333333332,0.85583333333333333,0.83312499999999989,0.81041666666666667,0.87,0.88,0.89,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.594749999999998,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.411000000000003},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.219000000000001},14.959199999999999,14.480699999999999,14.546362499999997,14.5875]
[null,57,17.388749999999998,17.388749999999998,17.05875,17.05875,16.728749999999998,16.728749999999998,{"$f":"U11*$I$13","v":16.049999999999997},16.049999999999997,15.33,15.33,14.9475,14.9475,14.565000000000001,14.565000000000001,null,0.96604166666666658,0.94770833333333326,0.92937499999999995,0.89166666666666661,0.85166666666666668,0.83041666666666669,0.8091666666666667,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.388749999999998,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.05875},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.728749999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.049999999999997},15.33,14.9475,14.565000000000001]
[1600,72,21.866250000000001,11.37045,21.326250000000002,11.196281250000002,20.786249999999999,11.016712500000001,{"$f":"U12*$I$13","v":19.69875},10.637325000000001,18.592500000000001,10.225875000000002,18.016874999999999,9.9993656249999994,17.44125,9.767100000000001,null,1.2147916666666667,1.1847916666666667,1.1547916666666667,1.0943750000000001,1.0329166666666667,1.0009375,0.96895833333333325,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.37045},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.196281250000002},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.016712500000001},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.637325000000001},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.225875000000002},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9993656249999994},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.767100000000001}]
[null,67,19.96875,14.1778125,19.477499999999999,13.9264125,18.986250000000002,13.670100000000001,18,13.32,16.987500000000001,12.910500000000001,16.460625,12.756984375,15.93375,12.5876625,null,1.109375,1.0820833333333333,1.0547916666666668,1,0.94374999999999998,0.91447916666666662,0.88520833333333337,0.71,0.71499999999999997,0.72,0.74,0.76,0.77500000000000002,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.1778125},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.9264125},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.670100000000001},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.32},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.910500000000001},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.756984375},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.5876625}]
[null,62,18.333750000000002,16.867050000000003,17.910000000000004,16.656300000000002,17.486250000000002,16.437075,{"$f":"U14*$I$13","v":16.69125},16.69125,15.914999999999999,15.914999999999999,15.504375,15.504375,15.09375,15.09375,null,1.0185416666666667,0.99500000000000011,0.97145833333333342,0.92729166666666663,0.88416666666666666,0.86135416666666664,0.83854166666666663,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.867050000000003,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.656300000000002},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.437075},16.69125,15.914999999999999,15.504375,15.09375]
[null,57,18.116250000000001,18.116250000000001,17.758125000000003,17.758125000000003,17.399999999999999,17.399999999999999,16.668750000000003,16.668750000000003,15.89625,15.89625,15.485625000000001,15.485625000000001,15.075000000000001,15.075000000000001,null,1.0064583333333335,0.98656250000000012,0.96666666666666667,0.92604166666666676,0.88312500000000005,0.86031250000000004,0.83750000000000002,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.116250000000001,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.758125000000003},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.399999999999999},16.668750000000003,15.89625,15.485625000000001,15.075000000000001]
[1800,72,22.143750000000001,11.957625000000002,21.581250000000001,11.761781250000002,21.018750000000001,11.560312500000002,19.897500000000001,11.142600000000002,18.757500000000004,10.691775000000002,18.164999999999999,10.535699999999999,17.572499999999998,10.367774999999998,null,1.2302083333333333,1.1989583333333333,1.1677083333333333,1.1054166666666667,1.0420833333333335,1.0091666666666665,0.97624999999999995,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.957625000000002},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.761781250000002},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.560312500000002},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.142600000000002},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.691775000000002},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.535699999999999},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.367774999999998}]
[null,67,20.227499999999999,14.968349999999999,19.723125,14.792343750000001,19.21875,14.606249999999999,18.191249999999997,14.189174999999997,17.15625,13.725000000000001,16.616250000000001,13.542243749999999,16.076249999999998,13.343287499999997,null,1.12375,1.0957291666666666,1.0677083333333333,1.0106249999999999,0.953125,0.92312500000000008,0.89312499999999995,0.74,0.75,0.76,0.78,0.8,0.81499999999999995,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.968349999999999},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.792343750000001},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.606249999999999},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.189174999999997},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.725000000000001},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.542243749999999},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.343287499999997}]
[null,62,18.727499999999999,18.727499999999999,18.348749999999999,18.348749999999999,17.970000000000002,17.970000000000002,17.186249999999998,17.186249999999998,16.365000000000002,16.365000000000002,15.93375,15.93375,15.502500000000001,15.502500000000001,null,1.0404166666666665,1.0193749999999999,0.99833333333333341,0.95479166666666659,0.90916666666666668,0.88520833333333337,0.86125000000000007,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.727499999999999,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.348749999999999},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.970000000000002},17.186249999999998,16.365000000000002,15.93375,15.502500000000001]
[null,57,18.708749999999998,18.708749999999998,18.328125,18.328125,17.947499999999998,17.947499999999998,17.16375,17.16375,16.346250000000001,16.346250000000001,15.914999999999999,15.914999999999999,15.483750000000001,15.483750000000001,null,1.0393749999999999,1.0182291666666667,0.99708333333333332,0.95354166666666673,0.90812500000000007,0.88416666666666666,0.86020833333333335,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.708749999999998,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.328125},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.947499999999998},17.16375,16.346250000000001,15.914999999999999,15.483750000000001]

{"sheet":"NXA6_60","index":49,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.734999999999999},{"$f":"IF(AM8>C8,C8,AM8)","v":10.8675},{"$f":"S8*$I$13","v":21.180535714285718},{"$f":"IF(AN8>E8,E8,AN8)","v":10.696170535714288},{"$f":"T8*$I$13","v":20.626071428571432},{"$f":"IF(AO8>G8,G8,AO8)","v":10.519296428571431},{"$f":"U8*$I$13","v":19.47214285714286},{"$f":"IF(AP8>I8,I8,AP8)","v":10.125514285714287},{"$f":"V8*$I$13","v":18.25392857142857},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.6745821428571421},{"$f":"W8*$I$13","v":17.609464285714285},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5091107142857147},{"$f":"X8*$I$13","v":16.965},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3307500000000001},null,1.2075,1.1766964285714288,1.1458928571428573,1.0817857142857144,1.0141071428571429,0.97830357142857138,0.9425,0.5,0.505,0.51,0.52,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.8675},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.696170535714288},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.519296428571431},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.125514285714287},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.6745821428571421},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5091107142857147},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3307500000000001}]
[null,67,19.803214285714287,13.466185714285716,19.311428571428568,{"$f":"IF(AN9>E9,E9,AN9)","v":13.324885714285712},18.819642857142856,{"$f":"IF(AO9>G9,G9,AO9)","v":13.173749999999998},{"$f":"U9*$I$13","v":17.78142857142857},{"$f":"IF(AP9>I9,I9,AP9)","v":12.802628571428571},16.682142857142857,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.344785714285713},16.100357142857145,{"$f":"IF(AR9>M9,M9,AR9)","v":12.155769642857145},15.51857142857143,{"$f":"IF(AS9>O9,O9,AS9)","v":11.949300000000001},null,1.1001785714285715,1.0728571428571427,1.0455357142857142,0.98785714285714288,0.92678571428571421,0.89446428571428582,0.86214285714285721,0.68,0.69,0.7,0.72,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.466185714285716},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.324885714285712},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.173749999999998},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.802628571428571},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.344785714285713},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.155769642857145},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.949300000000001}]
[null,62,18.205714285714283,16.203085714285713,17.792678571428574,16.725117857142859,17.379642857142859,17.20584642857143,{"$f":"U10*$I$13","v":16.588928571428571},16.588928571428571,15.746785714285716,15.746785714285716,15.290357142857141,15.290357142857141,14.83392857142857,14.83392857142857,null,1.0114285714285713,0.98848214285714298,0.96553571428571427,0.92160714285714285,0.87482142857142864,0.84946428571428567,0.82410714285714282,0.89,0.94,0.99,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.203085714285713,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.725117857142859},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":17.20584642857143},16.588928571428571,15.746785714285716,15.290357142857141,14.83392857142857]
[null,57,18.061071428571431,18.061071428571431,17.701071428571428,17.701071428571428,17.341071428571428,17.341071428571428,{"$f":"U11*$I$13","v":16.563214285714285},16.563214285714285,15.727500000000001,15.727500000000001,15.271071428571432,15.271071428571432,14.814642857142857,14.814642857142857,null,1.0033928571428572,0.98339285714285718,0.96339285714285716,0.9201785714285714,0.87375000000000003,0.84839285714285728,0.82303571428571431,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.061071428571431,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.701071428571428},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.341071428571428},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.563214285714285},15.727500000000001,15.271071428571432,14.814642857142857]
[2000,72,22.033928571428572,11.457642857142858,21.458571428571425,11.265749999999999,20.883214285714288,11.068103571428573,{"$f":"U12*$I$13","v":19.681071428571428},10.627778571428571,18.42107142857143,10.315800000000001,17.754107142857144,10.031070535714285,17.087142857142855,9.7396714285714268,null,1.2241071428571428,1.1921428571428569,1.1601785714285715,1.0933928571428571,1.0233928571428572,0.98633928571428575,0.94928571428571418,0.52,0.52500000000000002,0.53,0.54,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.457642857142858},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.265749999999999},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.068103571428573},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.627778571428571},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.315800000000001},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.031070535714285},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7396714285714268}]
[null,67,20.102142857142859,14.473542857142858,19.587857142857139,14.299135714285711,19.073571428571427,14.114442857142855,18,13.68,16.865357142857142,13.323632142857143,16.265892857142859,13.094043750000001,15.666428571428574,12.84647142857143,null,1.1167857142857143,1.0882142857142856,1.0596428571428571,1,0.93696428571428569,0.90366071428571437,0.87035714285714294,0.72,0.73,0.74,0.76,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.473542857142858},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.299135714285711},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.114442857142855},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.68},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.323632142857143},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.094043750000001},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.84647142857143}]
[null,62,18.765000000000001,18.765000000000001,18.374464285714286,18.374464285714286,17.983928571428571,17.983928571428571,{"$f":"U14*$I$13","v":17.145},17.145,16.245000000000001,16.245000000000001,15.758035714285713,15.758035714285713,15.271071428571426,15.271071428571426,null,1.0425,1.0208035714285715,0.99910714285714286,0.95250000000000001,0.90249999999999997,0.87544642857142851,0.84839285714285706,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.765000000000001,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":18.374464285714286},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.983928571428571},17.145,16.245000000000001,15.758035714285713,15.271071428571426]
[null,57,18.7425,18.7425,18.351964285714288,18.351964285714288,17.961428571428574,17.961428571428574,17.125714285714285,17.125714285714285,16.225714285714286,16.225714285714286,15.73875,15.73875,15.251785714285717,15.251785714285717,null,1.04125,1.0195535714285715,0.99785714285714289,0.9514285714285714,0.90142857142857136,0.87437500000000001,0.84732142857142867,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.7425,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18.351964285714288},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.961428571428574},17.125714285714285,16.225714285714286,15.73875,15.251785714285717]
[2250,72,22.242857142857144,12.011142857142858,21.648214285714282,11.798276785714284,21.053571428571431,11.579464285714288,19.816071428571426,11.097,18.520714285714284,10.742014285714284,17.840892857142855,10.526126785714284,17.161071428571429,10.296642857142857,null,1.2357142857142858,1.2026785714285713,1.1696428571428572,1.1008928571428571,1.0289285714285714,0.99116071428571417,0.95339285714285715,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.011142857142858},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.798276785714284},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.579464285714288},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.097},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.742014285714284},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.526126785714284},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.296642857142857}]
[null,67,20.317499999999999,15.238125,19.790357142857143,15.139623214285715,19.263214285714284,15.025307142857143,18.157499999999999,14.526,17.000357142857144,14.110296428571429,16.394464285714285,13.853322321428571,15.788571428571428,13.578171428571428,null,1.1287499999999999,1.0994642857142858,1.0701785714285714,1.00875,0.94446428571428576,0.91080357142857138,0.87714285714285711,0.75,0.76500000000000001,0.78,0.8,0.83,0.84499999999999997,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.238125},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.139623214285715},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.025307142857143},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.526},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.110296428571429},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.853322321428571},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.578171428571428}]
[null,62,19.317857142857143,19.317857142857143,18.901607142857141,18.901607142857141,18.485357142857143,18.485357142857143,17.594999999999999,17.594999999999999,16.640357142857145,16.640357142857145,16.126071428571429,16.126071428571429,15.611785714285714,15.611785714285714,null,1.0732142857142857,1.0500892857142856,1.0269642857142858,0.97750000000000004,0.92446428571428574,0.89589285714285716,0.86732142857142858,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,19.317857142857143,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.901607142857141},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.485357142857143},17.594999999999999,16.640357142857145,16.126071428571429,15.611785714285714]
[null,57,19.295357142857142,19.295357142857142,18.879107142857141,18.879107142857141,18.462857142857139,18.462857142857139,17.575714285714284,17.575714285714284,16.62107142857143,16.62107142857143,16.108392857142857,16.108392857142857,15.595714285714285,15.595714285714285,null,1.0719642857142857,1.0488392857142856,1.0257142857142856,0.97642857142857142,0.92339285714285713,0.89491071428571434,0.86642857142857144,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,19.295357142857142,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.879107142857141},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.462857142857139},17.575714285714284,16.62107142857143,16.108392857142857,15.595714285714285]

{"sheet":"NXA6_61","index":50,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["NXA6_61"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.581848739495801},{"$f":"IF(AM8>C8,C8,AM8)","v":10.7909243697479},{"$f":"S8*$I$13","v":21.067563025210085},{"$f":"IF(AN8>E8,E8,AN8)","v":10.639119327731093},{"$f":"T8*$I$13","v":20.553277310924372},{"$f":"IF(AO8>G8,G8,AO8)","v":10.48217142857143},{"$f":"U8*$I$13","v":19.455126050420169},{"$f":"IF(AP8>I8,I8,AP8)","v":10.116665546218488},{"$f":"V8*$I$13","v":18.269243697478991},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.6826991596638656},{"$f":"W8*$I$13","v":17.632436974789915},{"$f":"IF(AR8>M8,M8,AR8)","v":9.4333537815126043},{"$f":"X8*$I$13","v":16.995630252100842},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1776403361344556},null,1.1989915966386555,1.1704201680672268,1.1418487394957983,1.0808403361344538,1.0149579831932773,0.97957983193277309,0.94420168067226895,0.5,0.505,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.7909243697479},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.639119327731093},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.48217142857143},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.116665546218488},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.6826991596638656},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.4333537815126043},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1776403361344556}]
[null,67,19.663865546218485,13.37142857142857,19.201008403361346,{"$f":"IF(AN9>E9,E9,AN9)","v":13.152690756302523},18.7381512605042,{"$f":"IF(AO9>G9,G9,AO9)","v":12.929324369747897},{"$f":"U9*$I$13","v":17.74890756302521},{"$f":"IF(AP9>I9,I9,AP9)","v":12.601724369747899},16.687058823529412,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.18155294117647},16.113781512605044,{"$f":"IF(AR9>M9,M9,AR9)","v":12.004767226890758},15.540504201680672,{"$f":"IF(AS9>O9,O9,AS9)","v":11.810783193277311},null,1.0924369747899159,1.0667226890756303,1.0410084033613445,0.98605042016806721,0.92705882352941171,0.89521008403361346,0.8633613445378151,0.68,0.68500000000000005,0.69,0.71,0.73,0.745,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.37142857142857},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.152690756302523},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.929324369747897},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.601724369747899},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.18155294117647},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.004767226890758},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.810783193277311}]
[null,62,18.015126050420168,15.853310924369747,17.608235294117645,15.671329411764704,17.201344537815125,15.481210084033613,{"$f":"U10*$I$13","v":16.345210084033614},15.037593277310926,15.495126050420168,15.495126050420168,15.061008403361344,15.061008403361344,14.626890756302521,14.626890756302521,null,1.0008403361344538,0.97823529411764698,0.95563025210084029,0.90806722689075636,0.86084033613445377,0.83672268907563019,0.81260504201680672,0.88,0.89,0.9,0.92,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.853310924369747,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.671329411764704},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.481210084033613},15.037593277310926,15.495126050420168,15.061008403361344,14.626890756302521]
[null,57,17.649075630252103,17.649075630252103,17.317815126050423,17.317815126050423,16.98655462184874,16.98655462184874,{"$f":"U11*$I$13","v":16.263529411764704},16.263529411764704,15.473949579831931,15.473949579831931,15.03983193277311,15.03983193277311,14.605714285714287,14.605714285714287,null,0.98050420168067232,0.96210084033613452,0.94369747899159662,0.9035294117647058,0.85966386554621843,0.83554621848739496,0.8114285714285715,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.649075630252103,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.317815126050423},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.98655462184874},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.263529411764704},15.473949579831931,15.03983193277311,14.605714285714287]
[2000,72,21.932773109243694,11.405042016806721,21.394285714285715,11.232000000000001,20.855798319327732,11.053573109243699,{"$f":"U12*$I$13","v":19.703193277310923},10.639724369747899,18.477983193277307,10.16289075630252,17.816974789915967,9.9775058823529434,17.155966386554621,9.7789008403361333,null,1.2184873949579831,1.1885714285714286,1.1586554621848739,1.0946218487394956,1.0265546218487394,0.98983193277310921,0.95310924369747896,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.405042016806721},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.232000000000001},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.053573109243699},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.639724369747899},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.16289075630252},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9775058823529434},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7789008403361333}]
[null,67,19.999663865546218,14.199761344537814,19.517142857142858,14.052342857142857,19.034621848739498,13.895273949579833,18,13.5,16.898823529411764,13.012094117647059,16.305882352941175,12.800117647058823,15.712941176470588,12.570352941176472,null,1.1110924369747899,1.0842857142857143,1.0574789915966387,1,0.93882352941176472,0.90588235294117647,0.87294117647058822,0.71,0.72,0.73,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.199761344537814},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.052342857142857},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.895273949579833},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.012094117647059},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.800117647058823},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.570352941176472}]
[null,62,18.444705882352942,16.969129411764708,18.054453781512603,17.332275630252099,17.664201680672271,17.664201680672271,{"$f":"U14*$I$13","v":16.883697478991596},16.883697478991596,16.030588235294118,16.030588235294118,15.563193277310925,15.563193277310925,15.095798319327731,15.095798319327731,null,1.0247058823529411,1.0030252100840336,0.98134453781512609,0.93798319327731094,0.89058823529411768,0.86462184873949577,0.83865546218487397,0.92,0.96,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.969129411764708,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.332275630252099},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.664201680672271},16.883697478991596,16.030588235294118,15.563193277310925,15.095798319327731]
[null,57,18.356974789915963,18.356974789915963,18,18,17.643025210084033,17.643025210084033,16.856470588235293,16.856470588235293,16.009411764705881,16.009411764705881,15.543529411764705,15.543529411764705,15.077647058823532,15.077647058823532,null,1.0198319327731091,1,0.98016806722689076,0.93647058823529405,0.88941176470588235,0.86352941176470588,0.83764705882352952,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.356974789915963,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.643025210084033},16.856470588235293,16.009411764705881,15.543529411764705,15.077647058823532]
[2250,72,22.180840336134452,11.977653781512604,21.622689075630252,11.784365546218488,21.064537815126052,11.585495798319329,19.881680672268907,11.133741176470588,18.614117647058826,10.796188235294119,17.934957983193275,10.581625210084031,17.255798319327731,10.353478991596639,null,1.2322689075630251,1.2012605042016806,1.1702521008403362,1.1045378151260503,1.0341176470588236,0.99638655462184866,0.95865546218487396,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.59,0.6,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.977653781512604},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.784365546218488},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.585495798319329},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.133741176470588},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.796188235294119},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.581625210084031},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.353478991596639}]
[null,67,20.250756302521005,15.188067226890754,19.750084033613447,15.01006386554622,19.249411764705886,14.822047058823532,18.184537815126053,14.365784873949583,17.053109243697477,13.98354957983193,16.44655462184874,13.732873109243698,15.84,13.464,null,1.1250420168067226,1.0972268907563025,1.0694117647058825,1.0102521008403362,0.94739495798319329,0.91369747899159659,0.88,0.75,0.76,0.77,0.79,0.82,0.83499999999999996,0.85,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.188067226890754},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.01006386554622},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.822047058823532},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.365784873949583},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.98354957983193},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.732873109243698},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.464}]
[null,62,18.968067226890756,18.968067226890756,18.585378151260503,18.585378151260503,18.202689075630254,18.202689075630254,17.36470588235294,17.36470588235294,16.460168067226892,16.460168067226892,15.965546218487393,15.965546218487393,15.4709243697479,15.4709243697479,null,1.053781512605042,1.0325210084033614,1.0112605042016807,0.96470588235294119,0.91445378151260504,0.88697478991596634,0.85949579831932776,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.968067226890756,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.585378151260503},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.202689075630254},17.36470588235294,16.460168067226892,15.965546218487393,15.4709243697479]
[null,57,18.943865546218486,18.943865546218486,18.561176470588236,18.561176470588236,18.178487394957983,18.178487394957983,17.346554621848743,17.346554621848743,16.442016806722688,16.442016806722688,15.947394957983194,15.947394957983194,15.452773109243697,15.452773109243697,null,1.0524369747899158,1.0311764705882354,1.0099159663865547,0.96369747899159675,0.91344537815126048,0.8859663865546219,0.85848739495798321,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.943865546218486,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.561176470588236},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.178487394957983},17.346554621848743,16.442016806722688,15.947394957983194,15.452773109243697]

{"sheet":"R4A3_18","index":51,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_18"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[525,72,{"$f":"R8*$I$13","v":21.29651162790698},{"$f":"IF(AM8>C8,C8,AM8)","v":10.64825581395349},{"$f":"S8*$I$13","v":20.81511627906977},{"$f":"IF(AN8>E8,E8,AN8)","v":10.407558139534885},{"$f":"T8*$I$13","v":20.333720930232559},{"$f":"IF(AO8>G8,G8,AO8)","v":10.166860465116279},{"$f":"U8*$I$13","v":19.318604651162794},{"$f":"IF(AP8>I8,I8,AP8)","v":9.8524883720930241},{"$f":"V8*$I$13","v":18.324418604651168},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.5286976744186074},{"$f":"W8*$I$13","v":17.790697674418606},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3401162790697683},{"$f":"X8*$I$13","v":17.256976744186048},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1461976744186053},null,1.183139534883721,1.1563953488372094,1.1296511627906978,1.0732558139534885,1.0180232558139537,0.9883720930232559,0.95872093023255811,0.5,0.5,0.5,0.51,0.52,0.52500000000000002,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.64825581395349},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.407558139534885},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.166860465116279},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.8524883720930241},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.5286976744186074},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3401162790697683},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1461976744186053}]
[null,67,19.590697674418607,12.929860465116281,19.140697674418604,{"$f":"IF(AN9>E9,E9,AN9)","v":12.824267441860465},18.690697674418605,{"$f":"IF(AO9>G9,G9,AO9)","v":12.709674418604653},{"$f":"U9*$I$13","v":17.738372093023255},{"$f":"IF(AP9>I9,I9,AP9)","v":12.239476744186044},16.786046511627909,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.918093023255814},16.278488372093022,{"$f":"IF(AR9>M9,M9,AR9)","v":11.720511627906976},15.77093023255814,{"$f":"IF(AS9>O9,O9,AS9)","v":11.512779069767442},null,1.0883720930232559,1.0633720930232557,1.0383720930232558,0.98546511627906974,0.93255813953488376,0.9043604651162791,0.87616279069767444,0.66,0.67,0.68,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.929860465116281},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.824267441860465},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.709674418604653},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.239476744186044},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.918093023255814},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.720511627906976},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.512779069767442}]
[null,62,18.010465116279072,15.489000000000001,17.59186046511628,15.304918604651164,17.173255813953489,15.11246511627907,{"$f":"U10*$I$13","v":16.315116279069766},14.68360465116279,15.436046511627909,14.201162790697676,15.001744186046514,14.401674418604653,14.567441860465117,14.567441860465117,null,1.0005813953488374,0.97732558139534897,0.95406976744186056,0.90639534883720929,0.8575581395348838,0.83343023255813964,0.80930232558139537,0.86,0.87,0.88,0.9,0.92,0.96,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.489000000000001,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.304918604651164},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.11246511627907},14.68360465116279,14.201162790697676,14.401674418604653,14.567441860465117]
[null,57,17.47674418604651,17.47674418604651,17.136627906976745,17.136627906976745,16.79651162790698,16.79651162790698,{"$f":"U11*$I$13","v":16.084883720930232},16.084883720930232,15.352325581395348,15.352325581395348,14.959883720930234,14.959883720930234,14.567441860465117,14.567441860465117,null,0.97093023255813948,0.95203488372093026,0.93313953488372103,0.89360465116279064,0.85290697674418603,0.83110465116279075,0.80930232558139537,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.47674418604651,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.136627906976745},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.79651162790698},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.084883720930232},15.352325581395348,14.959883720930234,14.567441860465117]
[600,72,21.694186046511629,11.064034883720931,21.150000000000002,10.892250000000001,20.605813953488372,10.715023255813954,{"$f":"U12*$I$13","v":19.559302325581399},10.366430232558143,18.544186046511626,10.013860465116279,17.994767441860464,9.8071482558139529,17.445348837209306,9.5949418604651182,null,1.2052325581395349,1.175,1.1447674418604652,1.0866279069767444,1.0302325581395348,0.99970930232558142,0.9691860465116281,0.51,0.51500000000000001,0.52,0.53,0.54,0.54500000000000004,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.064034883720931},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.892250000000001},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.715023255813954},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.366430232558143},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.013860465116279},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.8071482558139529},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.5949418604651182}]
[null,67,19.915116279069768,13.741430232558139,19.449418604651164,13.614593023255814,18.983720930232561,13.478441860465118,18,13.14,17.026744186046514,12.770058139534886,16.503488372093024,12.542651162790698,15.980232558139535,12.304779069767443,null,1.1063953488372094,1.0805232558139535,1.0546511627906978,1,0.94593023255813957,0.91686046511627906,0.88779069767441865,0.69,0.7,0.71,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.741430232558139},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.614593023255814},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.478441860465118},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.14},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.770058139534886},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.542651162790698},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.304779069767443}]
[null,62,18.408139534883723,16.567325581395352,17.9843023255814,16.365715116279073,17.560465116279072,16.155627906976747,{"$f":"U14*$I$13","v":16.691860465116278},16.691860465116278,15.938372093023258,15.938372093023258,15.525,15.525,15.111627906976743,15.111627906976743,null,1.0226744186046512,0.99912790697674436,0.97558139534883737,0.92732558139534882,0.88546511627906987,0.86250000000000004,0.83953488372093021,0.9,0.91,0.92,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.567325581395352,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.365715116279073},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.155627906976747},16.691860465116278,15.938372093023258,15.525,15.111627906976743]
[null,57,18.188372093023254,18.188372093023254,17.82732558139535,17.82732558139535,17.466279069767445,17.466279069767445,16.712790697674421,16.712790697674421,15.938372093023258,15.938372093023258,15.525,15.525,15.111627906976743,15.111627906976743,null,1.0104651162790697,0.9904069767441861,0.97034883720930243,0.92848837209302337,0.88546511627906987,0.86250000000000004,0.83953488372093021,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.188372093023254,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.82732558139535},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.466279069767445},16.712790697674421,15.938372093023258,15.525,15.111627906976743]
[675,72,21.987209302325585,11.65322093023256,21.395930232558143,11.446822674418607,20.804651162790698,11.234511627906977,19.726744186046513,10.849709302325584,18.690697674418605,10.466790697674419,18.130813953488371,10.243909883720928,17.57093023255814,10.015430232558138,null,1.2215116279069769,1.1886627906976746,1.155813953488372,1.0959302325581397,1.0383720930232558,1.007267441860465,0.97616279069767442,0.53,0.53500000000000003,0.54,0.55000000000000004,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.65322093023256},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.446822674418607},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.234511627906977},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.849709302325584},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.466790697674419},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.243909883720928},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.015430232558138}]
[null,67,20.145348837209301,14.504651162790696,19.66918604651163,14.358505813953489,19.193023255813952,14.202837209302324,18.188372093023254,13.823162790697673,17.194186046511629,13.411465116279071,16.66046511627907,13.245069767441862,16.126744186046512,13.062662790697676,null,1.1191860465116279,1.0927325581395351,1.0662790697674418,1.0104651162790697,0.95523255813953489,0.92558139534883721,0.89593023255813953,0.72,0.73,0.74,0.76,0.78,0.79500000000000004,0.81,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.504651162790696},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.358505813953489},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.202837209302324},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.823162790697673},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.411465116279071},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.245069767441862},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.062662790697676}]
[null,62,18.774418604651164,18.586674418604652,18.38720930232558,18.295273255813953,18,18,17.2046511627907,17.2046511627907,16.398837209302329,16.398837209302329,15.96453488372093,15.96453488372093,15.530232558139534,15.530232558139534,null,1.0430232558139536,1.0215116279069767,1,0.95581395348837217,0.91104651162790706,0.88691860465116279,0.86279069767441863,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.586674418604652,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.295273255813953},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18},17.2046511627907,16.398837209302329,15.96453488372093,15.530232558139534]
[null,57,18.753488372093027,18.753488372093027,18.376744186046515,18.376744186046515,18,18,17.2046511627907,17.2046511627907,16.398837209302329,16.398837209302329,15.96453488372093,15.96453488372093,15.530232558139534,15.530232558139534,null,1.0418604651162793,1.0209302325581397,1,0.95581395348837217,0.91104651162790706,0.88691860465116279,0.86279069767441863,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.753488372093027,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.376744186046515},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18},17.2046511627907,16.398837209302329,15.96453488372093,15.530232558139534]

{"sheet":"R4A3_24","index":52,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_24"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[700,72,{"$f":"R8*$I$13","v":21.177391304347825},{"$f":"IF(AM8>C8,C8,AM8)","v":10.376921739130434},{"$f":"S8*$I$13","v":20.692173913043476},{"$f":"IF(AN8>E8,E8,AN8)","v":10.24262608695652},{"$f":"T8*$I$13","v":20.20695652173913},{"$f":"IF(AO8>G8,G8,AO8)","v":10.103478260869565},{"$f":"U8*$I$13","v":19.283478260869568},{"$f":"IF(AP8>I8,I8,AP8)","v":9.6417391304347841},{"$f":"V8*$I$13","v":18.344347826086956},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.3556173913043477},{"$f":"W8*$I$13","v":17.82391304347826},{"$f":"IF(AR8>M8,M8,AR8)","v":9.179315217391304},{"$f":"X8*$I$13","v":17.303478260869564},{"$f":"IF(AS8>O8,O8,AS8)","v":8.9978086956521732},null,1.1765217391304348,1.1495652173913042,1.1226086956521739,1.0713043478260871,1.0191304347826087,0.99021739130434772,0.96130434782608698,0.49,0.495,0.5,0.5,0.51,0.51500000000000001,0.52,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.376921739130434},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.24262608695652},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.103478260869565},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.6417391304347841},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.3556173913043477},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.179315217391304},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":8.9978086956521732}]
[null,67,19.463478260869568,12.845895652173915,19.052608695652172,{"$f":"IF(AN9>E9,E9,AN9)","v":12.669984782608696},18.641739130434782,{"$f":"IF(AO9>G9,G9,AO9)","v":12.489965217391305},{"$f":"U9*$I$13","v":17.765217391304347},{"$f":"IF(AP9>I9,I9,AP9)","v":12.257999999999999},16.865217391304348,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.805652173913042},16.372173913043479,{"$f":"IF(AR9>M9,M9,AR9)","v":11.624243478260869},15.879130434782608,{"$f":"IF(AS9>O9,O9,AS9)","v":11.432973913043478},null,1.0813043478260871,1.0584782608695651,1.0356521739130435,0.9869565217391304,0.93695652173913047,0.90956521739130447,0.88217391304347825,0.66,0.66500000000000004,0.67,0.69,0.7,0.71,0.72,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.845895652173915},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.669984782608696},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.489965217391305},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.257999999999999},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.805652173913042},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.624243478260869},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.432973913043478}]
[null,62,17.984347826086957,15.286695652173913,17.600869565217394,15.136747826086959,17.217391304347828,14.97913043478261,{"$f":"U10*$I$13","v":16.411304347826086},14.606060869565216,15.581739130434784,14.179382608695654,15.174782608695653,14.49191739130435,14.767826086956523,14.767826086956523,null,0.99913043478260877,0.97782608695652184,0.95652173913043481,0.91173913043478261,0.8656521739130435,0.84304347826086956,0.82043478260869573,0.85,0.86,0.87,0.89,0.91,0.95500000000000007,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.286695652173913,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.136747826086959},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.97913043478261},14.606060869565216,14.179382608695654,14.49191739130435,14.767826086956523]
[null,57,17.538260869565217,17.538260869565217,17.225217391304348,17.225217391304348,16.912173913043478,16.912173913043478,{"$f":"U11*$I$13","v":16.239130434782609},16.239130434782609,15.534782608695652,15.534782608695652,15.151304347826086,15.151304347826086,14.767826086956523,14.767826086956523,null,0.97434782608695658,0.95695652173913037,0.93956521739130427,0.90217391304347827,0.86304347826086958,0.84173913043478255,0.82043478260869573,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.538260869565217,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.225217391304348},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.912173913043478},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.239130434782609},15.534782608695652,15.151304347826086,14.767826086956523]
[800,72,21.513913043478261,10.972095652173914,20.985652173913042,10.807610869565217,20.457391304347826,10.637843478260869,{"$f":"U12*$I$13","v":19.510434782608698},10.145426086956522,18.54,9.8262,18.007826086956523,9.7242260869565236,17.475652173913041,9.6116086956521727,null,1.1952173913043478,1.1658695652173912,1.1365217391304347,1.0839130434782609,1.03,1.0004347826086957,0.97086956521739121,0.51,0.51500000000000001,0.52,0.52,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":10.972095652173914},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.807610869565217},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.637843478260869},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.145426086956522},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8262},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.7242260869565236},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.6116086956521727}]
[null,67,19.753043478260871,13.6296,19.326521739130438,13.528565217391305,18.900000000000002,13.419,18,12.959999999999999,17.084347826086955,12.642417391304345,16.579565217391306,12.434673913043479,16.074782608695649,12.216834782608693,null,1.0973913043478261,1.0736956521739132,1.05,1,0.94913043478260861,0.92108695652173911,0.89304347826086949,0.69,0.7,0.71,0.72,0.74,0.75,0.76,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.6296},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.528565217391305},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.419},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.959999999999999},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.642417391304345},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.434673913043479},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.216834782608693}]
[null,62,18.344347826086956,16.326469565217391,17.960869565217394,16.164782608695656,17.577391304347827,15.995426086956524,{"$f":"U14*$I$13","v":16.818260869565215},16.818260869565215,16.082608695652176,16.082608695652176,15.679565217391305,15.679565217391305,15.276521739130436,15.276521739130436,null,1.0191304347826087,0.99782608695652186,0.97652173913043483,0.93434782608695643,0.89347826086956528,0.87108695652173918,0.84869565217391307,0.89,0.9,0.91,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.326469565217391,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.164782608695656},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.995426086956524},16.818260869565215,16.082608695652176,15.679565217391305,15.276521739130436]
[null,57,18.195652173913043,18.195652173913043,17.86304347826087,17.86304347826087,17.530434782608694,17.530434782608694,16.818260869565215,16.818260869565215,16.082608695652176,16.082608695652176,15.679565217391305,15.679565217391305,15.276521739130436,15.276521739130436,null,1.0108695652173914,0.99239130434782608,0.9739130434782608,0.93434782608695643,0.89347826086956528,0.87108695652173918,0.84869565217391307,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.195652173913043,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.86304347826087},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.530434782608694},16.818260869565215,16.082608695652176,15.679565217391305,15.276521739130436]
[900,72,21.725217391304348,11.297113043478261,21.185217391304349,11.122239130434783,20.64521739130435,10.941965217391306,19.659130434782607,10.615930434782609,18.673043478260869,10.270173913043479,18.12521739130435,10.150121739130437,17.577391304347827,10.01911304347826,null,1.2069565217391305,1.1769565217391305,1.1469565217391304,1.0921739130434782,1.037391304347826,1.0069565217391305,0.97652173913043483,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.297113043478261},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.122239130434783},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":10.941965217391306},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.615930434782609},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.270173913043479},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.150121739130437},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.01911304347826}]
[null,67,19.956521739130437,14.368695652173914,19.522173913043478,14.251186956521739,19.087826086956522,14.124991304347827,18.164347826086956,13.804904347826087,17.233043478260868,13.441773913043477,16.716521739130435,13.206052173913044,16.2,12.96,null,1.1086956521739131,1.0845652173913043,1.0604347826086957,1.0091304347826087,0.95739130434782604,0.92869565217391303,0.9,0.72,0.73,0.74,0.76,0.78,0.79,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.368695652173914},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.251186956521739},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.124991304347827},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.804904347826087},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.441773913043477},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.206052173913044},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.96}]
[null,62,18.72,18.72,18.371739130434786,18.371739130434786,18.023478260869567,18.023478260869567,17.28,17.28,16.513043478260869,16.513043478260869,16.090434782608696,16.090434782608696,15.667826086956522,15.667826086956522,null,1.04,1.0206521739130436,1.001304347826087,0.96,0.91739130434782612,0.89391304347826095,0.87043478260869567,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.72,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.371739130434786},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.023478260869567},17.28,16.513043478260869,16.090434782608696,15.667826086956522]
[null,57,18.72,18.72,18.375652173913046,18.375652173913046,18.031304347826083,18.031304347826083,17.28,17.28,16.513043478260869,16.513043478260869,16.090434782608696,16.090434782608696,15.667826086956522,15.667826086956522,null,1.04,1.0208695652173914,1.0017391304347825,0.96,0.91739130434782612,0.89391304347826095,0.87043478260869567,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.72,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.375652173913046},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.031304347826083},17.28,16.513043478260869,16.090434782608696,15.667826086956522]

{"sheet":"R4A3_30","index":53,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_30"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[875,72,{"$f":"R8*$I$13","v":21.097058823529412},{"$f":"IF(AM8>C8,C8,AM8)","v":10.970470588235294},{"$f":"S8*$I$13","v":20.65698529411765},{"$f":"IF(AN8>E8,E8,AN8)","v":10.844917279411767},{"$f":"T8*$I$13","v":20.216911764705884},{"$f":"IF(AO8>G8,G8,AO8)","v":10.714963235294119},{"$f":"U8*$I$13","v":19.303676470588236},{"$f":"IF(AP8>I8,I8,AP8)","v":10.230948529411766},{"$f":"V8*$I$13","v":18.350735294117648},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.9093970588235312},{"$f":"W8*$I$13","v":17.82463235294118},{"$f":"IF(AR8>M8,M8,AR8)","v":9.8035477941176499},{"$f":"X8*$I$13","v":17.298529411764708},{"$f":"IF(AS8>O8,O8,AS8)","v":9.6871764705882377},null,1.1720588235294118,1.1476102941176471,1.1231617647058825,1.0724264705882354,1.0194852941176471,0.99025735294117656,0.96102941176470591,0.52,0.52500000000000002,0.53,0.53,0.54,0.55000000000000004,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.970470588235294},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.844917279411767},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.714963235294119},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.230948529411766},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.9093970588235312},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.8035477941176499},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.6871764705882377}]
[null,67,19.488970588235293,13.642279411764704,19.078676470588235,{"$f":"IF(AN9>E9,E9,AN9)","v":13.545860294117645},18.668382352941176,{"$f":"IF(AO9>G9,G9,AO9)","v":13.441235294117647},{"$f":"U9*$I$13","v":17.801470588235293},{"$f":"IF(AP9>I9,I9,AP9)","v":12.995073529411764},16.901470588235295,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.67610294117647},16.40514705882353,{"$f":"IF(AR9>M9,M9,AR9)","v":12.467911764705883},15.908823529411764,{"$f":"IF(AS9>O9,O9,AS9)","v":12.249794117647058},null,1.0827205882352942,1.0599264705882352,1.0371323529411764,0.98897058823529405,0.93897058823529411,0.91139705882352939,0.88382352941176467,0.7,0.71,0.72,0.73,0.75,0.76,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.642279411764704},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.545860294117645},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.441235294117647},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.995073529411764},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.67610294117647},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.467911764705883},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":12.249794117647058}]
[null,62,18.059558823529414,16.434198529411766,17.682352941176468,16.267764705882353,17.305147058823529,16.093786764705882,{"$f":"U10*$I$13","v":16.517647058823531},15.691764705882354,15.76985294117647,15.76985294117647,15.379411764705882,15.379411764705882,14.988970588235293,14.988970588235293,null,1.0033088235294119,0.98235294117647054,0.96139705882352944,0.91764705882352948,0.87610294117647058,0.85441176470588232,0.83272058823529405,0.91,0.92,0.93,0.95,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.434198529411766,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":16.267764705882353},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":16.093786764705882},15.691764705882354,15.76985294117647,15.379411764705882,14.988970588235293]
[null,57,17.801470588235293,17.801470588235293,17.483823529411765,17.483823529411765,17.166176470588237,17.166176470588237,{"$f":"U11*$I$13","v":16.484558823529412},16.484558823529412,15.76985294117647,15.76985294117647,15.379411764705882,15.379411764705882,14.988970588235293,14.988970588235293,null,0.98897058823529405,0.97132352941176481,0.95367647058823535,0.91580882352941184,0.87610294117647058,0.85441176470588232,0.83272058823529405,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.801470588235293,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.483823529411765},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.166176470588237},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.484558823529412},15.76985294117647,15.379411764705882,14.988970588235293]
[1000,72,21.341911764705884,11.524632352941179,20.88529411764706,11.382485294117648,20.428676470588236,11.235772058823532,{"$f":"U12*$I$13","v":19.488970588235293},10.913823529411765,18.516176470588238,10.554220588235294,17.973529411764705,10.334779411764705,17.430882352941175,10.109911764705881,null,1.1856617647058825,1.1602941176470589,1.1349264705882354,1.0827205882352942,1.0286764705882354,0.99852941176470589,0.96838235294117647,0.54,0.54500000000000004,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57499999999999996,0.57999999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.524632352941179},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.382485294117648},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.235772058823532},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.913823529411765},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.554220588235294},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.334779411764705},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":10.109911764705881}]
[null,67,19.733823529411765,14.603029411764705,19.31360294117647,14.38863419117647,18.893382352941181,14.170036764705886,18,13.86,17.080147058823528,13.493316176470588,16.573897058823533,13.341987132352942,16.067647058823532,13.175470588235296,null,1.0963235294117648,1.0729779411764706,1.0496323529411766,1,0.94889705882352937,0.92077205882352953,0.89264705882352946,0.74,0.745,0.75,0.77,0.79,0.80499999999999994,0.82,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.603029411764705},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.38863419117647},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":14.170036764705886},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.86},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.493316176470588},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.341987132352942},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":13.175470588235296}]
[null,62,18.430147058823529,18.245845588235294,18.086029411764702,17.995599264705877,17.741911764705883,17.741911764705883,{"$f":"U14*$I$13","v":17.020588235294117},17.020588235294117,16.272794117647059,16.272794117647059,15.862499999999999,15.862499999999999,15.452205882352942,15.452205882352942,null,1.0238970588235294,1.0047794117647058,0.98566176470588229,0.94558823529411762,0.90404411764705883,0.88124999999999998,0.85845588235294124,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.245845588235294,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.995599264705877},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.741911764705883},17.020588235294117,16.272794117647059,15.862499999999999,15.452205882352942]
[null,57,18.410294117647062,18.410294117647062,18.076102941176469,18.076102941176469,17.741911764705883,17.741911764705883,17.027205882352941,17.027205882352941,16.279411764705884,16.279411764705884,15.865808823529413,15.865808823529413,15.452205882352942,15.452205882352942,null,1.022794117647059,1.0042279411764705,0.98566176470588229,0.94595588235294126,0.90441176470588247,0.8814338235294118,0.85845588235294124,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.410294117647062,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":18.076102941176469},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.741911764705883},17.027205882352941,16.279411764705884,15.865808823529413,15.452205882352942]
[1125,72,21.507352941176471,12.044117647058824,21.037499999999998,11.886187499999998,20.567647058823528,11.723558823529411,19.608088235294119,11.372691176470589,18.61544117647059,10.983110294117647,18.062867647058827,10.837720588235296,17.51029411764706,10.681279411764706,null,1.1948529411764706,1.16875,1.1426470588235293,1.0893382352941177,1.0341911764705882,1.0034926470588237,0.97279411764705892,0.56000000000000005,0.56499999999999995,0.56999999999999995,0.57999999999999996,0.59,0.6,0.61,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":12.044117647058824},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.886187499999998},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.723558823529411},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.372691176470589},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.983110294117647},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.837720588235296},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.681279411764706}]
[null,67,19.905882352941177,15.327529411764706,19.475735294117648,15.191073529411765,19.045588235294119,15.046014705882355,18.138970588235296,14.69256617647059,17.205882352941178,14.452941176470588,16.693014705882355,14.189062500000002,16.180147058823529,13.914926470588235,null,1.1058823529411765,1.0819852941176471,1.0580882352941177,1.0077205882352942,0.95588235294117652,0.92738970588235303,0.89889705882352944,0.77,0.78,0.79,0.81,0.84,0.85,0.86,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.327529411764706},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":15.191073529411765},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":15.046014705882355},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.69256617647059},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":14.452941176470588},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":14.189062500000002},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.914926470588235}]
[null,62,18.893382352941181,18.893382352941181,18.545955882352942,18.545955882352942,18.198529411764707,18.198529411764707,17.444117647058825,17.444117647058825,16.669852941176472,16.669852941176472,16.23970588235294,16.23970588235294,15.809558823529414,15.809558823529414,null,1.0496323529411766,1.0303308823529411,1.0110294117647058,0.96911764705882353,0.92610294117647063,0.90220588235294119,0.87830882352941186,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.893382352941181,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.545955882352942},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.198529411764707},17.444117647058825,16.669852941176472,16.23970588235294,15.809558823529414]
[null,57,18.893382352941181,18.893382352941181,18.545955882352942,18.545955882352942,18.198529411764707,18.198529411764707,17.450735294117649,17.450735294117649,16.669852941176472,16.669852941176472,16.23970588235294,16.23970588235294,15.809558823529414,15.809558823529414,null,1.0496323529411766,1.0303308823529411,1.0110294117647058,0.96948529411764717,0.92610294117647063,0.90220588235294119,0.87830882352941186,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.893382352941181,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.545955882352942},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.198529411764707},17.450735294117649,16.669852941176472,16.23970588235294,15.809558823529414]

{"sheet":"R4A3_36","index":54,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_36"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1050,72,{"$f":"R8*$I$13","v":21.10235294117647},{"$f":"IF(AM8>C8,C8,AM8)","v":10.7622},{"$f":"S8*$I$13","v":20.644411764705882},{"$f":"IF(AN8>E8,E8,AN8)","v":10.63187205882353},{"$f":"T8*$I$13","v":20.186470588235295},{"$f":"IF(AO8>G8,G8,AO8)","v":10.496964705882354},{"$f":"U8*$I$13","v":19.302352941176469},{"$f":"IF(AP8>I8,I8,AP8)","v":10.037223529411765},{"$f":"V8*$I$13","v":18.375882352941179},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7392176470588261},{"$f":"W8*$I$13","v":17.862352941176471},{"$f":"IF(AR8>M8,M8,AR8)","v":9.556358823529413},{"$f":"X8*$I$13","v":17.348823529411767},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3683647058823549},null,1.1723529411764706,1.1469117647058824,1.1214705882352942,1.0723529411764705,1.0208823529411766,0.99235294117647066,0.96382352941176475,0.51,0.51500000000000001,0.52,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":10.7622},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.63187205882353},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.496964705882354},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.037223529411765},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7392176470588261},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.556358823529413},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3683647058823549}]
[null,67,19.408235294117645,13.391682352941174,19.027058823529408,{"$f":"IF(AN9>E9,E9,AN9)","v":13.223805882352938},18.645882352941175,{"$f":"IF(AO9>G9,G9,AO9)","v":13.052117647058822},{"$f":"U9*$I$13","v":17.809411764705882},{"$f":"IF(AP9>I9,I9,AP9)","v":12.644682352941174},16.935882352941174,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.363194117647057},16.454117647058823,{"$f":"IF(AR9>M9,M9,AR9)","v":12.176047058823528},15.972352941176473,{"$f":"IF(AS9>O9,O9,AS9)","v":11.979264705882354},null,1.078235294117647,1.0570588235294116,1.0358823529411765,0.98941176470588232,0.94088235294117639,0.91411764705882348,0.88735294117647068,0.69,0.69499999999999995,0.7,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.391682352941174},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.223805882352938},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.052117647058822},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.644682352941174},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.363194117647057},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.176047058823528},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.979264705882354}]
[null,62,17.984117647058824,16.005864705882352,17.634705882352943,15.87123529411765,17.285294117647059,15.729617647058824,{"$f":"U10*$I$13","v":16.522941176470589},15.366335294117649,15.755294117647059,15.755294117647059,15.382058823529411,15.382058823529411,15.008823529411766,15.008823529411766,null,0.99911764705882344,0.9797058823529412,0.96029411764705874,0.91794117647058826,0.87529411764705889,0.8545588235294117,0.83382352941176474,0.89,0.9,0.91,0.93,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.005864705882352,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.87123529411765},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.729617647058824},15.366335294117649,15.755294117647059,15.382058823529411,15.008823529411766]
[null,57,17.69294117647059,17.69294117647059,17.396470588235292,17.396470588235292,17.099999999999998,17.099999999999998,{"$f":"U11*$I$13","v":16.448823529411765},16.448823529411765,15.765882352941178,15.765882352941178,15.38735294117647,15.38735294117647,15.008823529411766,15.008823529411766,null,0.98294117647058832,0.96647058823529408,0.95,0.9138235294117647,0.87588235294117656,0.85485294117647059,0.83382352941176474,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.69294117647059,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.396470588235292},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":17.099999999999998},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.448823529411765},15.765882352941178,15.38735294117647,15.008823529411766]
[1200,72,21.361764705882354,11.108117647058824,20.869411764705884,10.956441176470589,20.377058823529413,10.79984117647059,{"$f":"U12*$I$13","v":19.48764705882353},10.523329411764706,18.534705882352938,10.194088235294117,18.007941176470588,10.08444705882353,17.481176470588238,9.9642705882352942,null,1.1867647058823529,1.1594117647058824,1.1320588235294118,1.0826470588235295,1.029705882352941,1.0004411764705883,0.97117647058823542,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.108117647058824},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.956441176470589},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.79984117647059},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.523329411764706},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.194088235294117},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.08444705882353},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.9642705882352942}]
[null,67,19.641176470588238,14.141647058823532,19.249411764705883,14.052070588235294,18.857647058823527,13.95465882352941,18,13.5,17.105294117647059,13.171076470588236,16.612941176470589,13.041158823529413,16.120588235294115,12.896470588235292,null,1.0911764705882354,1.0694117647058823,1.0476470588235294,1,0.95029411764705884,0.92294117647058826,0.89558823529411757,0.72,0.73,0.74,0.75,0.77,0.78500000000000003,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.141647058823532},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":14.052070588235294},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.95465882352941},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.171076470588236},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":13.041158823529413},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.896470588235292}]
[null,62,18.397058823529409,16.925294117647056,18.021176470588237,17.300329411764707,17.645294117647058,17.645294117647058,{"$f":"U14*$I$13","v":16.978235294117646},16.978235294117646,16.258235294117647,16.258235294117647,15.858529411764705,15.858529411764705,15.458823529411763,15.458823529411763,null,1.0220588235294117,1.0011764705882353,0.98029411764705876,0.94323529411764706,0.90323529411764714,0.88102941176470584,0.85882352941176465,0.92,0.96,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.925294117647056,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.300329411764707},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.645294117647058},16.978235294117646,16.258235294117647,15.858529411764705,15.458823529411763]
[null,57,18.285882352941176,18.285882352941176,17.976176470588236,17.976176470588236,17.666470588235292,17.666470588235292,16.978235294117646,16.978235294117646,16.258235294117647,16.258235294117647,15.858529411764705,15.858529411764705,15.458823529411763,15.458823529411763,null,1.0158823529411765,0.99867647058823528,0.98147058823529409,0.94323529411764706,0.90323529411764714,0.88102941176470584,0.85882352941176465,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.285882352941176,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.976176470588236},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.666470588235292},16.978235294117646,16.258235294117647,15.858529411764705,15.458823529411763]
[1350,72,21.547058823529415,11.204470588235296,21.030882352941177,11.251522058823531,20.514705882352942,11.28308823529412,19.604117647058825,10.978305882352943,18.63,10.805399999999999,18.095294117647061,10.585747058823531,17.560588235294119,10.360747058823529,null,1.197058823529412,1.1683823529411765,1.1397058823529411,1.0891176470588235,1.0349999999999999,1.0052941176470589,0.97558823529411764,0.52,0.53500000000000003,0.55000000000000004,0.56000000000000005,0.57999999999999996,0.58499999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.204470588235296},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.251522058823531},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.28308823529412},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.978305882352943},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.805399999999999},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.585747058823531},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.360747058823529}]
[null,67,19.847647058823533,14.88573529411765,19.426764705882356,14.764341176470591,19.005882352941178,14.634529411764708,18.132352941176471,14.324558823529413,17.221764705882354,13.949629411764707,16.724117647058822,13.797397058823528,16.226470588235294,13.630235294117647,null,1.1026470588235295,1.079264705882353,1.0558823529411765,1.0073529411764706,0.95676470588235296,0.92911764705882349,0.90147058823529402,0.75,0.76,0.77,0.79,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.88573529411765},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.764341176470591},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.634529411764708},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.324558823529413},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.949629411764707},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.797397058823528},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.630235294117647}]
[null,62,18.757058823529412,18.757058823529412,18.434117647058823,18.434117647058823,18.111176470588234,18.111176470588234,17.391176470588235,17.391176470588235,16.639411764705883,16.639411764705883,16.223823529411767,16.223823529411767,15.808235294117646,15.808235294117646,null,1.0420588235294117,1.0241176470588236,1.0061764705882352,0.9661764705882353,0.92441176470588238,0.90132352941176475,0.878235294117647,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.757058823529412,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.434117647058823},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.111176470588234},17.391176470588235,16.639411764705883,16.223823529411767,15.808235294117646]
[null,57,18.757058823529412,18.757058823529412,18.434117647058823,18.434117647058823,18.111176470588234,18.111176470588234,17.391176470588235,17.391176470588235,16.639411764705883,16.639411764705883,16.223823529411767,16.223823529411767,15.808235294117646,15.808235294117646,null,1.0420588235294117,1.0241176470588236,1.0061764705882352,0.9661764705882353,0.92441176470588238,0.90132352941176475,0.878235294117647,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.757058823529412,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.434117647058823},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.111176470588234},17.391176470588235,16.639411764705883,16.223823529411767,15.808235294117646]

{"sheet":"R4A3_42","index":55,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_42"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1225,72,{"$f":"R8*$I$13","v":21.294683544303794},{"$f":"IF(AM8>C8,C8,AM8)","v":11.073235443037973},{"$f":"S8*$I$13","v":20.832151898734178},{"$f":"IF(AN8>E8,E8,AN8)","v":10.624397468354431},{"$f":"T8*$I$13","v":20.369620253164559},{"$f":"IF(AO8>G8,G8,AO8)","v":10.184810126582279},{"$f":"U8*$I$13","v":19.394430379746836},{"$f":"IF(AP8>I8,I8,AP8)","v":9.8911594936708873},{"$f":"V8*$I$13","v":18.364556962025315},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.5495696202531644},{"$f":"W8*$I$13","v":17.80860759493671},{"$f":"IF(AR8>M8,M8,AR8)","v":9.3495189873417726},{"$f":"X8*$I$13","v":17.252658227848102},{"$f":"IF(AS8>O8,O8,AS8)","v":9.1439088607594936},null,1.1830379746835442,1.1573417721518988,1.1316455696202532,1.0774683544303798,1.0202531645569619,0.98936708860759492,0.95848101265822783,0.52,0.51,0.5,0.51,0.52,0.52500000000000002,0.53,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.073235443037973},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.624397468354431},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.184810126582279},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":9.8911594936708873},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.5495696202531644},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.3495189873417726},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.1439088607594936}]
[null,67,19.526582278481012,12.887544303797469,19.098227848101267,{"$f":"IF(AN9>E9,E9,AN9)","v":12.700321518987343},18.669873417721519,{"$f":"IF(AO9>G9,G9,AO9)","v":12.508815189873419},{"$f":"U9*$I$13","v":17.763037974683545},{"$f":"IF(AP9>I9,I9,AP9)","v":12.256496202531645},16.810632911392403,{"$f":"IF(AQ9>K9,K9,AQ9)","v":11.935549367088607},16.30025316455696,{"$f":"IF(AR9>M9,M9,AR9)","v":11.73618227848101},15.78987341772152,{"$f":"IF(AS9>O9,O9,AS9)","v":11.52660759493671},null,1.0848101265822785,1.0610126582278481,1.0372151898734177,0.98683544303797466,0.9339240506329114,0.90556962025316445,0.87721518987341773,0.66,0.66500000000000004,0.67,0.69,0.71,0.72,0.73,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":12.887544303797469},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":12.700321518987343},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.508815189873419},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.256496202531645},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":11.935549367088607},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":11.73618227848101},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.52660759493671}]
[null,62,17.931645569620255,15.421215189873418,17.544303797468356,15.175822784810128,17.156962025316457,14.926556962025318,{"$f":"U10*$I$13","v":16.345822784810125},14.54778227848101,15.5073417721519,14.266754430379748,15.081265822784809,14.478015189873416,14.655189873417719,14.655189873417719,null,0.99620253164556971,0.97468354430379744,0.95316455696202529,0.90810126582278472,0.86151898734177224,0.83784810126582276,0.81417721518987329,0.86,0.86499999999999999,0.87,0.89,0.92,0.96,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.421215189873418,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.175822784810128},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":14.926556962025318},14.54778227848101,14.266754430379748,14.478015189873416,14.655189873417719]
[null,57,17.453164556962026,17.453164556962026,17.136455696202528,17.136455696202528,16.819746835443038,16.819746835443038,{"$f":"U11*$I$13","v":16.149873417721519},16.149873417721519,15.438987341772153,15.438987341772153,15.051645569620254,15.051645569620254,14.664303797468353,14.664303797468353,null,0.96962025316455691,0.9520253164556961,0.9344303797468354,0.89721518987341764,0.85772151898734184,0.83620253164556968,0.81468354430379741,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.453164556962026,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.136455696202528},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.819746835443038},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.149873417721519},15.438987341772153,15.051645569620254,14.664303797468353]
[1400,72,21.609113924050636,11.236739240506331,21.128354430379744,10.986744303797467,20.64759493670886,10.736749367088608,{"$f":"U12*$I$13","v":19.63594936708861},10.210693670886078,18.569620253164555,9.8418987341772137,17.995443037974681,9.7175392405063281,17.421265822784807,9.5816962025316457,null,1.2005063291139242,1.1737974683544303,1.1470886075949367,1.0908860759493673,1.0316455696202531,0.99974683544303788,0.96784810126582266,0.52,0.52,0.52,0.52,0.53,0.54,0.55000000000000004,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.236739240506331},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":10.986744303797467},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.736749367088608},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.210693670886078},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":9.8418987341772137},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.7175392405063281},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.5816962025316457}]
[null,67,19.831898734177216,13.684010126582278,19.387594936708865,13.474378481012661,18.943291139240507,13.260303797468355,18,12.959999999999999,17.020253164556962,12.594987341772152,16.493924050632909,12.452912658227847,15.96759493670886,12.295048101265822,null,1.1017721518987342,1.0770886075949369,1.0524050632911393,1,0.9455696202531646,0.91632911392405059,0.88708860759493668,0.69,0.69499999999999995,0.7,0.72,0.74,0.755,0.77,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":13.684010126582278},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.474378481012661},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.260303797468355},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":12.959999999999999},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":12.594987341772152},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.452912658227847},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.295048101265822}]
[null,62,18.309873417721519,16.478886075949369,17.917974683544305,16.215767088607596,17.52607594936709,15.948729113924053,{"$f":"U14*$I$13","v":16.701265822784809},16.701265822784809,15.96759493670886,15.96759493670886,15.557468354430378,15.557468354430378,15.147341772151901,15.147341772151901,null,1.0172151898734176,0.99544303797468359,0.97367088607594943,0.92784810126582273,0.88708860759493668,0.8643037974683544,0.84151898734177222,0.9,0.90500000000000003,0.91,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.478886075949369,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.215767088607596},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":15.948729113924053},16.701265822784809,15.96759493670886,15.557468354430378,15.147341772151901]
[null,57,18.123037974683545,18.123037974683545,17.785822784810126,17.785822784810126,17.448607594936707,17.448607594936707,16.728607594936708,16.728607594936708,15.96759493670886,15.96759493670886,15.557468354430378,15.557468354430378,15.147341772151901,15.147341772151901,null,1.0068354430379747,0.98810126582278479,0.96936708860759491,0.92936708860759498,0.88708860759493668,0.8643037974683544,0.84151898734177222,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.123037974683545,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.785822784810126},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.448607594936707},16.728607594936708,15.96759493670886,15.557468354430378,15.147341772151901]
[1575,72,21.846075949367087,11.359959493670885,21.349367088607593,11.208417721518988,20.852658227848103,11.051908860759495,19.813670886075947,10.699382278481012,18.72,10.295999999999999,18.129873417721516,10.15272911392405,17.539746835443037,9.9976556962025303,null,1.2136708860759493,1.1860759493670885,1.1584810126582279,1.100759493670886,1.04,1.0072151898734176,0.97443037974683544,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.359959493670885},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.208417721518988},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.051908860759495},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":10.699382278481012},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.295999999999999},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.15272911392405},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":9.9976556962025303}]
[null,67,20.064303797468355,14.446298734177216,19.606329113924055,14.31262025316456,19.148354430379747,14.169782278481012,18.182278481012659,13.636708860759494,17.179746835443041,13.400202531645572,16.642025316455697,13.147200000000002,16.104303797468358,12.883443037974686,null,1.1146835443037975,1.0892405063291142,1.0637974683544305,1.0101265822784811,0.95443037974683553,0.92455696202531656,0.8946835443037976,0.72,0.73,0.74,0.75,0.78,0.79,0.8,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.446298734177216},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.31262025316456},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.169782278481012},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":13.636708860759494},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.400202531645572},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.147200000000002},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":12.883443037974686}]
[null,62,18.674430379746838,18.48768607594937,18.312151898734175,18.220591139240504,17.94987341772152,17.94987341772152,17.193417721518987,17.193417721518987,16.391392405063289,16.391392405063289,15.958481012658225,15.958481012658225,15.525569620253165,15.525569620253165,null,1.0374683544303798,1.0173417721518987,0.99721518987341773,0.95518987341772144,0.91063291139240499,0.88658227848101256,0.86253164556962025,0.99,0.995,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.48768607594937,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.220591139240504},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.94987341772152},17.193417721518987,16.391392405063289,15.958481012658225,15.525569620253165]
[null,57,18.665316455696203,18.665316455696203,18.309873417721519,18.309873417721519,17.954430379746835,17.954430379746835,17.197974683544302,17.197974683544302,16.395949367088605,16.395949367088605,15.960759493670885,15.960759493670885,15.525569620253165,15.525569620253165,null,1.0369620253164558,1.0172151898734176,0.99746835443037973,0.95544303797468355,0.91088607594936699,0.88670886075949362,0.86253164556962025,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.665316455696203,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.309873417721519},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.954430379746835},17.197974683544302,16.395949367088605,15.960759493670885,15.525569620253165]

{"sheet":"R4A3_48","index":56,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_48"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1400,72,{"$f":"R8*$I$13","v":21.365217391304348},{"$f":"IF(AM8>C8,C8,AM8)","v":11.109913043478262},{"$f":"S8*$I$13","v":20.907391304347829},{"$f":"IF(AN8>E8,E8,AN8)","v":10.767306521739131},{"$f":"T8*$I$13","v":20.449565217391303},{"$f":"IF(AO8>G8,G8,AO8)","v":10.429278260869564},{"$f":"U8*$I$13","v":19.479130434782608},{"$f":"IF(AP8>I8,I8,AP8)","v":10.129147826086957},{"$f":"V8*$I$13","v":18.453913043478263},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7805739130434795},{"$f":"W8*$I$13","v":17.902173913043477},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5776630434782604},{"$f":"X8*$I$13","v":17.350434782608698},{"$f":"IF(AS8>O8,O8,AS8)","v":9.3692347826086966},null,1.1869565217391305,1.1615217391304349,1.1360869565217391,1.0821739130434782,1.0252173913043479,0.99456521739130432,0.9639130434782609,0.52,0.51500000000000001,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.109913043478262},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.767306521739131},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.429278260869564},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.129147826086957},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7805739130434795},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5776630434782604},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.3692347826086966}]
[null,67,19.498695652173911,13.25911304347826,19.07021739130435,{"$f":"IF(AN9>E9,E9,AN9)","v":13.15845},18.641739130434782,{"$f":"IF(AO9>G9,G9,AO9)","v":13.049217391304348},{"$f":"U9*$I$13","v":17.73782608695652},{"$f":"IF(AP9>I9,I9,AP9)","v":12.593856521739129},16.783043478260872,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.251621739130437},16.274347826086959,{"$f":"IF(AR9>M9,M9,AR9)","v":12.04301739130435},15.765652173913042,{"$f":"IF(AS9>O9,O9,AS9)","v":11.824239130434782},null,1.0832608695652173,1.0594565217391305,1.0356521739130435,0.98543478260869566,0.93239130434782613,0.90413043478260879,0.87586956521739123,0.68,0.69,0.7,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.25911304347826},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.15845},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":13.049217391304348},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.593856521739129},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.251621739130437},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.04301739130435},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.824239130434782}]
[null,62,17.82391304347826,15.863282608695652,17.434565217391302,15.691108695652172,17.045217391304348,15.511147826086956,{"$f":"U10*$I$13","v":16.239130434782609},15.102391304347828,15.401739130434782,15.401739130434782,15.018260869565216,15.018260869565216,14.634782608695652,14.634782608695652,null,0.99021739130434772,0.9685869565217391,0.94695652173913047,0.90217391304347827,0.85565217391304349,0.83434782608695646,0.81304347826086953,0.89,0.9,0.91,0.93,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.863282608695652,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.691108695652172},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.511147826086956},15.102391304347828,15.401739130434782,15.018260869565216,14.634782608695652]
[null,57,17.413043478260867,17.413043478260867,17.096086956521738,17.096086956521738,16.779130434782608,16.779130434782608,{"$f":"U11*$I$13","v":16.11},16.11,15.397826086956522,15.397826086956522,15.016304347826086,15.016304347826086,14.634782608695652,14.634782608695652,null,0.96739130434782605,0.94978260869565212,0.9321739130434783,0.89500000000000002,0.85543478260869565,0.83423913043478259,0.81304347826086953,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.413043478260867,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.096086956521738},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.779130434782608},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.11},15.397826086956522,15.016304347826086,14.634782608695652]
[1600,72,21.713478260869568,11.291008695652176,21.24,11.151,20.766521739130432,11.006256521739131,{"$f":"U12*$I$13","v":19.756956521739131},10.668756521739132,18.692608695652176,10.280934782608698,18.123260869565215,10.058409782608695,17.553913043478261,9.8301913043478262,null,1.2063043478260871,1.18,1.153695652173913,1.097608695652174,1.0384782608695653,1.0068478260869564,0.97521739130434781,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.291008695652176},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.151},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":11.006256521739131},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.668756521739132},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.280934782608698},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":10.058409782608695},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.8301913043478262}]
[null,67,19.831304347826087,14.080226086956522,19.385217391304348,13.957356521739131,18.939130434782609,13.825565217391304,18,13.5,17.013913043478261,13.100713043478262,16.491521739130434,12.863386956521738,15.969130434782608,12.615613043478261,null,1.1017391304347826,1.0769565217391304,1.0521739130434782,1,0.94521739130434779,0.91619565217391297,0.88717391304347826,0.71,0.72,0.73,0.75,0.77,0.78,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.080226086956522},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.957356521739131},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.825565217391304},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.100713043478262},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.863386956521738},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.615613043478261}]
[null,62,18.22304347826087,16.947430434782611,17.833695652173915,17.120347826086959,17.444347826086954,17.269904347826085,{"$f":"U14*$I$13","v":16.704782608695652},16.704782608695652,15.949565217391303,15.949565217391303,15.544565217391302,15.544565217391302,15.139565217391302,15.139565217391302,null,1.0123913043478261,0.99076086956521747,0.96913043478260863,0.92804347826086953,0.88608695652173908,0.863586956521739,0.84108695652173904,0.93,0.96,0.99,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.947430434782611,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":17.120347826086959},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":17.269904347826085},16.704782608695652,15.949565217391303,15.544565217391302,15.139565217391302]
[null,57,18.09391304347826,18.09391304347826,17.757391304347827,17.757391304347827,17.420869565217394,17.420869565217394,16.704782608695652,16.704782608695652,15.949565217391303,15.949565217391303,15.544565217391302,15.544565217391302,15.139565217391302,15.139565217391302,null,1.0052173913043478,0.98652173913043484,0.96782608695652184,0.92804347826086953,0.88608695652173908,0.863586956521739,0.84108695652173904,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.09391304347826,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.757391304347827},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.420869565217394},16.704782608695652,15.949565217391303,15.544565217391302,15.139565217391302]
[1800,72,21.967826086956521,11.423269565217391,21.478695652173911,11.491102173913044,20.989565217391302,11.544260869565218,19.952608695652177,11.17346086956522,18.860869565217396,10.750695652173915,18.275869565217391,10.600004347826086,17.69086956521739,10.43761304347826,null,1.2204347826086956,1.1932608695652174,1.1660869565217391,1.1084782608695654,1.0478260869565219,1.0153260869565217,0.98282608695652174,0.52,0.53500000000000003,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.423269565217391},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.491102173913044},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.544260869565218},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.17346086956522},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.750695652173915},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.600004347826086},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.43761304347826}]
[null,67,20.07,15.0525,19.612173913043478,14.807191304347826,19.154347826086958,14.557304347826088,18.191739130434787,14.189556521739133,17.186086956521741,13.920730434782611,16.649999999999999,13.736249999999998,16.113913043478263,13.53568695652174,null,1.115,1.0895652173913044,1.0641304347826088,1.0106521739130436,0.95478260869565224,0.92499999999999993,0.89521739130434785,0.75,0.755,0.76,0.78,0.81,0.82499999999999996,0.84,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":15.0525},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.807191304347826},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.557304347826088},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.189556521739133},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.920730434782611},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.736249999999998},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.53568695652174}]
[null,62,18.645652173913042,18.645652173913042,18.293478260869563,18.293478260869563,17.941304347826087,17.941304347826087,17.189999999999998,17.189999999999998,16.395652173913042,16.395652173913042,15.969130434782608,15.969130434782608,15.542608695652172,15.542608695652172,null,1.0358695652173913,1.0163043478260869,0.99673913043478268,0.95499999999999996,0.91086956521739126,0.88717391304347826,0.86347826086956514,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.645652173913042,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.293478260869563},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":17.941304347826087},17.189999999999998,16.395652173913042,15.969130434782608,15.542608695652172]
[null,57,18.649565217391302,18.649565217391302,18.295434782608694,18.295434782608694,17.941304347826087,17.941304347826087,17.193913043478261,17.193913043478261,16.395652173913042,16.395652173913042,15.969130434782608,15.969130434782608,15.542608695652172,15.542608695652172,null,1.036086956521739,1.0164130434782608,0.99673913043478268,0.9552173913043478,0.91086956521739126,0.88717391304347826,0.86347826086956514,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.649565217391302,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.295434782608694},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":17.941304347826087},17.193913043478261,16.395652173913042,15.969130434782608,15.542608695652172]

{"sheet":"R4A3_60","index":57,"n_rows":19,"n_cols":45,"rows_kept":19,"cut":false,"hidden":true,"merged":[[130,0,133,0],[120,12,121,12],[120,13,121,13],[120,14,121,14],[120,15,121,15],[122,0,125,0],[126,0,129,0],[119,12,119,13],[119,14,119,15],[120,4,121,4],[120,5,121,5],[120,6,121,6],[120,7,121,7],[120,8,121,8],[120,9,121,9],[120,10,121,10],[120,11,121,11],[119,0,121,0],[119,1,121,1],[119,4,119,5],[119,6,119,7],[119,8,119,9],[119,10,119,11],[111,0,114,0],[117,0,118,1],[117,4,117,15],[118,4,118,5],[118,6,118,7],[118,8,118,9],[118,10,118,11],[118,12,118,13],[118,14,118,15],[101,12,102,12],[101,13,102,13],[101,14,102,14],[101,15,102,15],[103,0,106,0],[107,0,110,0],[100,12,100,13],[100,14,100,15],[101,4,102,4],[101,5,102,5],[101,6,102,6],[101,7,102,7],[101,8,102,8],[101,9,102,9],[101,10,102,10],[101,11,102,11],[100,0,102,0],[100,1,102,1],[100,4,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[92,0,95,0],[98,0,99,1],[98,4,98,15],[99,4,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[99,14,99,15],[82,12,83,12],[82,13,83,13],[82,14,83,14],[82,15,83,15],[84,0,87,0],[88,0,91,0],[81,12,81,13],[81,14,81,15],[82,4,83,4],[82,5,83,5],[82,6,83,6],[82,7,83,7],[82,8,83,8],[82,9,83,9],[82,10,83,10],[82,11,83,11],[81,0,83,0],[81,1,83,1],[81,4,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[73,0,76,0],[79,0,80,1],[79,4,79,15],[80,4,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[80,14,80,15],[63,12,64,12],[63,13,64,13],[63,14,64,14],[63,15,64,15],[65,0,68,0],[69,0,72,0],[62,12,62,13],[62,14,62,15],[63,4,64,4],[63,5,64,5],[63,6,64,6],[63,7,64,7],[63,8,64,8],[63,9,64,9],[63,10,64,10],[63,11,64,11],[62,0,64,0],[62,1,64,1],[62,4,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[54,0,57,0],[60,0,61,1],[60,4,60,15],[61,4,61,5],[61,6,61,7],[61,8,61,9],[61,10,61,11],[61,12,61,13],[61,14,61,15],[44,12,45,12],[44,13,45,13],[44,14,45,14],[44,15,45,15],[46,0,49,0],[50,0,53,0],[43,12,43,13],[43,14,43,15],[44,4,45,4],[44,5,45,5],[44,6,45,6],[44,7,45,7],[44,8,45,8],[44,9,45,9],[44,10,45,10],[44,11,45,11],[43,0,45,0],[43,1,45,1],[43,4,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[35,0,38,0],[41,0,42,1],[41,4,41,15],[42,4,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[25,12,26,12],[25,13,26,13],[25,14,26,14],[25,15,26,15],[27,0,30,0],[31,0,34,0],[24,12,24,13],[24,14,24,15],[25,4,26,4],[25,5,26,5],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,9,26,9],[25,10,26,10],[25,11,26,11],[24,0,26,0],[24,1,26,1],[24,4,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[7,0,10,0],[11,0,14,0],[15,0,18,0],[22,4,22,15],[23,4,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[23,14,23,15],[5,10,6,10],[5,11,6,11],[5,12,6,12],[5,13,6,13],[5,14,6,14],[5,15,6,15],[4,10,4,11],[4,12,4,13],[4,14,4,15],[5,2,6,2],[5,3,6,3],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[5,8,6,8],[4,0,6,0],[4,1,6,1],[4,2,4,3],[4,4,4,5],[4,6,4,7],[4,8,4,9],[5,9,6,9],[2,0,2,1],[2,2,2,15],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]]}
[]
["R4A3_60"]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Total Factors",null,null,null,null,null,null,"Sens. %",null,null,null,null,null,null,"IDB Adj",null,null,null,null,null,null,"Sens Calc"]
[1750,72,{"$f":"R8*$I$13","v":21.224210526315787},{"$f":"IF(AM8>C8,C8,AM8)","v":11.036589473684209},{"$f":"S8*$I$13","v":20.769473684210528},{"$f":"IF(AN8>E8,E8,AN8)","v":10.696278947368421},{"$f":"T8*$I$13","v":20.314736842105262},{"$f":"IF(AO8>G8,G8,AO8)","v":10.360515789473684},{"$f":"U8*$I$13","v":19.342105263157894},{"$f":"IF(AP8>I8,I8,AP8)","v":10.057894736842105},{"$f":"V8*$I$13","v":18.312631578947371},{"$f":"IF(AQ8>K8,K8,AQ8)","v":9.7056947368421067},{"$f":"W8*$I$13","v":17.763157894736842},{"$f":"IF(AR8>M8,M8,AR8)","v":9.5032894736842106},{"$f":"X8*$I$13","v":17.213684210526317},{"$f":"IF(AS8>O8,O8,AS8)","v":9.295389473684212},null,1.1791228070175437,1.153859649122807,1.1285964912280702,1.0745614035087718,1.0173684210526317,0.98684210526315785,0.95631578947368423,0.52,0.51500000000000001,0.51,0.52,0.53,0.53500000000000003,0.54,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y8*C8+($A$4-80)*AF8*$A$8/1000","v":11.036589473684209},{"$f":"Z8*E8+($A$4-80)*AG8*$A$8/1000","v":10.696278947368421},{"$f":"AA8*G8+($A$4-80)*AH8*$A$8/1000","v":10.360515789473684},{"$f":"AB8*I8+($A$4-80)*AI8*$A$8/1000","v":10.057894736842105},{"$f":"AC8*K8+($A$4-80)*AJ8*$A$8/1000","v":9.7056947368421067},{"$f":"AD8*M8+($A$4-80)*AK8*$A$8/1000","v":9.5032894736842106},{"$f":"AE8*O8+($A$4-80)*AL8*$A$8/1000","v":9.295389473684212}]
[null,67,19.509473684210526,13.26644210526316,19.087894736842106,{"$f":"IF(AN9>E9,E9,AN9)","v":13.075207894736844},18.666315789473686,{"$f":"IF(AO9>G9,G9,AO9)","v":12.879757894736843},{"$f":"U9*$I$13","v":17.766315789473683},{"$f":"IF(AP9>I9,I9,AP9)","v":12.614084210526315},16.822105263157898,{"$f":"IF(AQ9>K9,K9,AQ9)","v":12.280136842105264},16.321578947368423,{"$f":"IF(AR9>M9,M9,AR9)","v":12.077968421052633},15.821052631578949,{"$f":"IF(AS9>O9,O9,AS9)","v":11.865789473684211},null,1.083859649122807,1.0604385964912282,1.0370175438596492,0.98701754385964913,0.93456140350877204,0.90675438596491231,0.8789473684210527,0.68,0.68500000000000005,0.69,0.71,0.73,0.74,0.75,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y9*C9+($A$4-80)*AF9*$A$8/1000","v":13.26644210526316},{"$f":"Z9*E9+($A$4-80)*AG9*$A$8/1000","v":13.075207894736844},{"$f":"AA9*G9+($A$4-80)*AH9*$A$8/1000","v":12.879757894736843},{"$f":"AB9*I9+($A$4-80)*AI9*$A$8/1000","v":12.614084210526315},{"$f":"AC9*K9+($A$4-80)*AJ9*$A$8/1000","v":12.280136842105264},{"$f":"AD9*M9+($A$4-80)*AK9*$A$8/1000","v":12.077968421052633},{"$f":"AE9*O9+($A$4-80)*AL9*$A$8/1000","v":11.865789473684211}]
[null,62,17.952631578947368,15.798315789473685,17.572105263157894,15.639173684210526,17.19157894736842,15.472421052631578,{"$f":"U10*$I$13","v":16.386315789473684},15.075410526315791,15.562105263157896,14.628378947368422,15.161052631578949,14.70622105263158,14.760000000000002,14.760000000000002,null,0.99736842105263157,0.97622807017543856,0.95508771929824554,0.91035087719298247,0.86456140350877198,0.84228070175438607,0.82000000000000006,0.88,0.89,0.9,0.92,0.94,0.97,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,15.798315789473685,{"$f":"Z10*E10+($A$4-80)*AG10*$A$8/1000","v":15.639173684210526},{"$f":"AA10*G10+($A$4-80)*AH10*$A$8/1000","v":15.472421052631578},15.075410526315791,14.628378947368422,14.70622105263158,14.760000000000002]
[null,57,17.529473684210526,17.529473684210526,17.216842105263158,17.216842105263158,16.90421052631579,16.90421052631579,{"$f":"U11*$I$13","v":16.234736842105264},16.234736842105264,15.527368421052632,15.527368421052632,15.143684210526315,15.143684210526315,14.760000000000002,14.760000000000002,null,0.97385964912280698,0.95649122807017539,0.93912280701754391,0.90192982456140347,0.86263157894736842,0.84131578947368413,0.82000000000000006,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,17.529473684210526,{"$f":"Z11*E11+($A$4-80)*AG11*$A$8/1000","v":17.216842105263158},{"$f":"AA11*G11+($A$4-80)*AH11*$A$8/1000","v":16.90421052631579},{"$f":"AB11*I11+($A$4-80)*AI11*$A$8/1000","v":16.234736842105264},15.527368421052632,15.143684210526315,14.760000000000002]
[2000,72,21.543157894736844,11.20244210526316,21.066315789473688,11.059815789473687,20.589473684210525,10.912421052631579,{"$f":"U12*$I$13","v":19.582105263157896},10.574336842105264,18.51157894736842,10.181368421052632,17.943157894736842,9.9584526315789486,17.374736842105264,9.7298526315789484,null,1.1968421052631579,1.1703508771929827,1.143859649122807,1.0878947368421052,1.0284210526315789,0.99684210526315786,0.96526315789473693,0.52,0.52500000000000002,0.53,0.54,0.55000000000000004,0.55500000000000005,0.56000000000000005,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y12*C12+($A$4-80)*AF12*$A$12/1000","v":11.20244210526316},{"$f":"Z12*E12+($A$4-80)*AG12*$A$12/1000","v":11.059815789473687},{"$f":"AA12*G12+($A$4-80)*AH12*$A$12/1000","v":10.912421052631579},{"$f":"AB12*I12+($A$4-80)*AI12*$A$12/1000","v":10.574336842105264},{"$f":"AC12*K12+($A$4-80)*AJ12*$A$12/1000","v":10.181368421052632},{"$f":"AD12*M12+($A$4-80)*AK12*$A$12/1000","v":9.9584526315789486},{"$f":"AE12*O12+($A$4-80)*AL12*$A$12/1000","v":9.7298526315789484}]
[null,67,19.812631578947368,14.06696842105263,19.373684210526317,13.949052631578947,18.934736842105263,13.822357894736841,18,13.5,17.021052631578947,13.10621052631579,16.503157894736841,12.872463157894737,15.985263157894735,12.628357894736842,null,1.100701754385965,1.0763157894736843,1.0519298245614035,1,0.94561403508771924,0.9168421052631579,0.88807017543859645,0.71,0.72,0.73,0.75,0.77,0.78,0.79,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y13*C13+($A$4-80)*AF13*$A$12/1000","v":14.06696842105263},{"$f":"Z13*E13+($A$4-80)*AG13*$A$12/1000","v":13.949052631578947},{"$f":"AA13*G13+($A$4-80)*AH13*$A$12/1000","v":13.822357894736841},{"$f":"AB13*I13+($A$4-80)*AI13*$A$12/1000","v":13.5},{"$f":"AC13*K13+($A$4-80)*AJ13*$A$12/1000","v":13.10621052631579},{"$f":"AD13*M13+($A$4-80)*AK13*$A$12/1000","v":12.872463157894737},{"$f":"AE13*O13+($A$4-80)*AL13*$A$12/1000","v":12.628357894736842}]
[null,62,18.322105263157898,16.856336842105268,17.936842105263157,16.681263157894733,17.551578947368419,16.498484210526314,{"$f":"U14*$I$13","v":16.796842105263156},16.796842105263156,16.038947368421052,16.038947368421052,15.628421052631577,15.628421052631577,15.217894736842103,15.217894736842103,null,1.0178947368421054,0.99649122807017543,0.97508771929824556,0.93315789473684208,0.89105263157894732,0.8682456140350876,0.84543859649122799,0.92,0.92999999999999994,0.94,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,16.856336842105268,{"$f":"Z14*E14+($A$4-80)*AG14*$A$12/1000","v":16.681263157894733},{"$f":"AA14*G14+($A$4-80)*AH14*$A$12/1000","v":16.498484210526314},16.796842105263156,16.038947368421052,15.628421052631577,15.217894736842103]
[null,57,18.18,18.18,17.846842105263157,17.846842105263157,17.513684210526314,17.513684210526314,16.8,16.8,16.042105263157893,16.042105263157893,15.629999999999999,15.629999999999999,15.217894736842103,15.217894736842103,null,1.01,0.99149122807017542,0.97298245614035084,0.93333333333333335,0.89122807017543859,0.86833333333333329,0.84543859649122799,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.18,{"$f":"Z15*E15+($A$4-80)*AG15*$A$12/1000","v":17.846842105263157},{"$f":"AA15*G15+($A$4-80)*AH15*$A$12/1000","v":17.513684210526314},16.8,16.042105263157893,15.629999999999999,15.217894736842103]
[2250,72,21.767368421052637,11.319031578947373,21.274736842105266,11.381984210526317,20.782105263157895,11.430157894736844,19.746315789473687,11.057936842105265,18.644210526315792,10.6272,18.059999999999999,10.474799999999998,17.475789473684213,10.310715789473685,null,1.2092982456140353,1.1819298245614036,1.1545614035087719,1.0970175438596492,1.0357894736842106,1.0033333333333332,0.97087719298245623,0.52,0.53500000000000003,0.55000000000000004,0.56000000000000005,0.56999999999999995,0.57999999999999996,0.59,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y16*C16+($A$4-80)*AF16*$A$16/1000","v":11.319031578947373},{"$f":"Z16*E16+($A$4-80)*AG16*$A$16/1000","v":11.381984210526317},{"$f":"AA16*G16+($A$4-80)*AH16*$A$16/1000","v":11.430157894736844},{"$f":"AB16*I16+($A$4-80)*AI16*$A$16/1000","v":11.057936842105265},{"$f":"AC16*K16+($A$4-80)*AJ16*$A$16/1000","v":10.6272},{"$f":"AD16*M16+($A$4-80)*AK16*$A$16/1000","v":10.474799999999998},{"$f":"AE16*O16+($A$4-80)*AL16*$A$16/1000","v":10.310715789473685}]
[null,67,20.030526315789473,14.822589473684209,19.577368421052633,14.683026315789474,19.124210526315789,14.5344,18.167368421052632,14.170547368421055,17.16,13.899600000000001,16.63105263157895,13.637463157894739,16.102105263157895,13.364747368421053,null,1.1128070175438596,1.0876315789473685,1.0624561403508772,1.0092982456140351,0.95333333333333337,0.92394736842105274,0.894561403508772,0.74,0.75,0.76,0.78,0.81,0.82000000000000006,0.83,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,{"$f":"Y17*C17+($A$4-80)*AF17*$A$16/1000","v":14.822589473684209},{"$f":"Z17*E17+($A$4-80)*AG17*$A$16/1000","v":14.683026315789474},{"$f":"AA17*G17+($A$4-80)*AH17*$A$16/1000","v":14.5344},{"$f":"AB17*I17+($A$4-80)*AI17*$A$16/1000","v":14.170547368421055},{"$f":"AC17*K17+($A$4-80)*AJ17*$A$16/1000","v":13.899600000000001},{"$f":"AD17*M17+($A$4-80)*AK17*$A$16/1000","v":13.637463157894739},{"$f":"AE17*O17+($A$4-80)*AL17*$A$16/1000","v":13.364747368421053}]
[null,62,18.710526315789473,18.710526315789473,18.356842105263155,18.356842105263155,18.003157894736841,18.003157894736841,17.248421052631578,17.248421052631578,16.455789473684209,16.455789473684209,16.021578947368422,16.021578947368422,15.587368421052631,15.587368421052631,null,1.0394736842105263,1.0198245614035086,1.0001754385964912,0.95824561403508768,0.91421052631578947,0.89008771929824559,0.86596491228070172,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.710526315789473,{"$f":"Z18*E18+($A$4-80)*AG18*$A$16/1000","v":18.356842105263155},{"$f":"AA18*G18+($A$4-80)*AH18*$A$16/1000","v":18.003157894736841},17.248421052631578,16.455789473684209,16.021578947368422,15.587368421052631]
[null,57,18.710526315789473,18.710526315789473,18.356842105263155,18.356842105263155,18.003157894736841,18.003157894736841,17.248421052631578,17.248421052631578,16.45894736842105,16.45894736842105,16.02315789473684,16.02315789473684,15.587368421052631,15.587368421052631,null,1.0394736842105263,1.0198245614035086,1.0001754385964912,0.95824561403508768,0.91438596491228064,0.89017543859649118,0.86596491228070172,1,1,1,1,1,1,1,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,0.83499999999999996,18.710526315789473,{"$f":"Z19*E19+($A$4-80)*AG19*$A$16/1000","v":18.356842105263155},{"$f":"AA19*G19+($A$4-80)*AH19*$A$16/1000","v":18.003157894736841},17.248421052631578,16.45894736842105,16.02315789473684,15.587368421052631]

{"sheet":"Form","index":58,"n_rows":53,"n_cols":16,"rows_kept":53,"cut":false,"hidden":true,"merged":[[28,15,29,15],[27,4,27,5],[34,0,37,0],[28,13,29,13],[28,10,29,10],[27,14,27,15],[28,14,29,14],[38,0,41,0],[27,12,27,13],[28,4,29,4],[28,5,29,5],[28,6,29,6],[28,7,29,7],[30,0,33,0],[27,8,27,9],[27,10,27,11],[28,12,29,12],[27,0,29,0],[28,11,29,11],[52,1,52,4],[28,2,29,2],[28,3,29,3],[28,9,29,9],[28,8,29,8],[27,1,29,1],[27,2,27,3],[27,6,27,7],[1,3,1,8],[2,3,2,8],[13,0,13,15],[26,14,26,15],[26,10,26,11],[18,6,18,11],[26,4,26,5],[26,12,26,13],[26,8,26,9],[25,2,25,15],[25,0,25,1],[26,2,26,3],[17,6,17,11],[26,6,26,7]]}
[]
[null,null,"Select ICP Condenser:  "]
[null,null,"ADP Evaporator:  ",null,null,null,null,null,null,null,null,null,null,24]
[null,null,"Nominal Capacity:  ",null,"(Mbtuh)",null,null,null,null,null,null,"Condenser Entering Air Temperature: ",null,"(°F) Dry Bulb, 75°F to 115°F"]
[null,null,"AHRI Rated Capacity:  ",null,"(Mbtuh) @ 95 ˚F & 80/67 ˚F conditions",null,null,null,null,null,null,"Evaporator Air Flow (CFM): ",null,null,"to"]
[null,null,"Entering Evaporator Air (DB):  ",null,"(°F) Dry Bulb -- 80°F Standard",null,null,null,null,null,null,"Entering Evaporator Air (WB):  ",null,"(°F) Wet Bulb, 57°F to 72°F"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,48]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"CFM"]
[]
[]
[]
[]
[]
["Extended Ratings"]
[]
[]
[]
[null,null,null,null,null,"ICP Condenser :  "]
[null,null,null,null,null,"ADP Evaporator:  "]
[null,null,null,null,null,"Condenser Entering Air Temperature: ",null,"(°F) Dry Bulb, 75°F to 115°F"]
[null,null,null,null,null,"Evaporator Air Flow:",null,"CFM"]
[null,null,null,null,null,"Entering Evaporator Air (DB):  ",null,"(°F) Dry Bulb"]
[null,null,null,null,null,"Entering Evaporator Air (WB):  ",null,"(°F) Wet Bulb, 57°F to 72°F"]
[null,null,null,null,null,"AHRI Rated Capacity:  ",null,"(Mbtuh) @ 95 ˚F & 80/67 ˚F conditions"]
[]
["Evaporator Air \n",null,"Condenser  Entering Air Temperature ˚F"]
[80,"°F DB",75,null,80,null,85,null,95,null,105,null,110,null,115]
["CFM","EWB†\n˚F","Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh",null,"Capacity Mbtuh"]
[null,null,"Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens.","Total","Sens."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,"Condenser Entering Air Temperature: ",null,"(°F) Dry Bulb, 75°F to 115°F",null,null,null,"CAPACITY IN MBTUH UNDER SPECIFIC CONDITIONS LISTED"]
[null,null,null,"Evaporator Air Flow:",null,"CFM",null,null,null,null,"TOTAL"]
[null,null,null,"Entering Evaporator Air (WB):  ",null,"(°F) Wet Bulb, 57°F to 72°F",null,null,null,null,"SENSIBLE"]
[]
["Notes:","† Entering Wet Bulb"]
[null,"Extended ratings are not certified.  They are calculated based upon typical condenser performance curves and are for engineering information only."]
[null,"When the required data fall between the published data, interpolation may be performed. Extrapolation is not an acceptable practice."]
[null,"Displayed sensible capacity has been adjusted based upon indoor DB.  Sensible capacity will increase with higher indoor DB and decrease with lower indoor DB."]
[null,"The magnitude of the adjustment depends partially on evaporator air flow, with greater adjustment at higher CFM."]
["Printed:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"I-19-A"]

{"sheet":"Instructions","index":59,"n_rows":43,"n_cols":5,"rows_kept":43,"cut":false,"hidden":true,"merged":[]}
[]
[]
[]
[]
[]
[]
[null,"This spreadsheet generates capacity information for ADP rated matches at other than nominal conditions."]
[null,"The information is provided is not certified and is provided for engineering use only."]
[]
[null,"The latest version will always be available at:  www.adpnow.com/extratings/"]
[]
[null,"In order to generate an extended rating, you will need the following information:"]
[null,null,"Condenser model number"]
[null,null,"ADP coil model number"]
[null,null,"Nominal capacity"]
[null,null,"Rated capacity (from AHRI database)"]
[null,null,"Condenser entering air dry bulb temperature"]
[null,null,"Indoor entering air dry bulb temperature"]
[null,null,"Indoor entering air wet bulb temperature"]
[null,null,"Indoor airflow"]
[]
[null,"Select the condenser series and nominal tonnage form the drop down lists."]
[null,"Enter the remaining information in the correct cells. Note there are limits on the range of values allowed."]
[null,"Click on \"Calculate\" to calculate the extended ratings."]
[null,"The table will show capacities for various conditions.  The capacities at the specific design point are "]
[null,"at the bottom of the page."]
[null,"From this point you may:"]
[null,null,"Click \"Clear\" to clear the form and start over."]
[null,null,"Click \"Print\" to print a copy of the data."]
[null,null,"Click \"Copy\" to copy the data to a new spreadsheet and save it in the same directory."]
[]
[null,"Notes:","Displayed sensible capacity has been adjusted based upon indoor DB. Sensible capacity will"]
[null,null,"increase with higher indoor DB and decrease with lower indoor DB.  The magnitude of the "]
[null,null,"adjustment depends partially on evaporator air flow, with greater adjustment at higher CFM."]
[]
[null,"Versions:","I-11-A","2011-02-01","Initial public release"]
[null,null,"I-11-B","2011-05-25","Updated sensible calc and check for capacity units"]
[null,null,"I-12-A","2012-01-03","Renewed date key through 2012"]
[null,null,"I-13-A","2012-12-31","Renewed date key through 2013"]
[null,null,"I-14-A","2013-12-31","Renewed date key through 2014"]
[null,null,"I-15-A","2015-01-31","Renewed date key through 2015"]
[null,null,"I-16-A","2016-03-22","Renewed date key through 2016"]
[null,null,"I-19-A","2019-05-20","New Version"]

{"sheet":"Prompt","index":60,"n_rows":17,"n_cols":2,"rows_kept":17,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,"In order to use this spreadsheet, "]
[null,"Please enable Macros in your security settings."]
[]
[null,"Enabling Macros in Excel 2007"]
[null,"1. In Excel, click the Office button in the upper left corner of the screen."]
[null,"2. Click the \"Excel Options\" button in the lower right."]
[null,"3. Click the \"Trust Center\" button on the left. Then, at the bottom right, select \"Trust Center Settings\" as shown below."]
[null,"4. In the next window, select \"Macro Settings,\" then select the radio button for \"Disable all macros with notification.\""]
[null,"5. When openning this spreadsheet, you will see a warning like this in the menu bar:"]
[]
[]
[null,"6. Select \"Enable this content\" and click \"Okay\".  The spreadsheet will now be functional."]