## Front
SUBMITTAL DATA
S SERIES AIR HANDLER
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Optional Accessories
Unit Size
|  | SM3A1805R | SM3A2407R | SM7A3110R | SM6A3710R
Factory Installed Heat (kW) |  | 5kW | 7.5kw | 10kW | 10kW
Refrigerant |  | R-454B | R-454B | R-454B | R-454B
Factory Installed metering device |  | Non-bleed HP-A/C TXV | Non-bleed HP-A/C TXV | Non-bleed HP-A/C TXV | Non-bleed HP-A/C TXV
Blower Data: | Motor Type | 3-speed PSC motor | 3-speed PSC motor | 5-speed high eff. ECM motor | 5-speed high eff. ECM motor
| Motor H.P. | 1/4 | 1/4 | 1/3 | 1/2
| F.L.A. | 1.7 | 1.7 | 2.2 | 2.9
Nominal CFM |  | 600 | 800 | 1000 | 1200
Max Unit Weight (lbs) |  | 73 | 73 | 79 | 79
Available Voltages |  | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph
Maximum Elec. Heat available (kW) |  | 10kW | 10kW | 10kW | 10kW
Transformer Size and Type |  | 40VA, Class 183 | 40VA, Class 192 | 40VA, Class 637 | 40VA, Class 501
Refrigerant Conn. (IDS) Suction |  | 3/4 | 3/4 | 3/4 | 3/4
Refrigerant Conn. (IDS) Liquid |  | 3/8 | 3/8 | 3/8 | 3/8
Pallet Quantity (min order per model) |  | 4 | 4 | 4 | 4
NOTES:
Cooling capacities subject to outdoor unit matchup. See http://www.adpnow.com/extratings/ for individual capacities by OEM
Cooling and Heating capacity data is rated at the following conditions:
Cooling: 80 FDB / 67 FWB Indoor, 95 FDB Outdoor
Heating: 70 FDB / 47 FWB Indoor, 43 FDB Outdoor
| A1 Refrigerants Product Nomenclature |  |  | A2L Refrigerants Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
Low 31" height on models 18 - 37.
A1 model Suitable for use with R-410A.
A2L model Suitable for use with R-32 and R-454B.
A2L model include factory installed Refrigerant Detections System (RDS).
Cabinets constructed of heavy-gauge, corrosion-resistant galvanized steel.
Refrigerant connections located on top left.
5/8" foil-faced insulation for excellent sweat resistance and quiet operation.
(4) Screw removal for easy access to all electrical connections.
Dual condensate drain connections on left side, right side, and bottom of cabinet.
1" duct flanges on all models simplify attachment to plenums such as 1 1/2" ductboard.
Air filter included with every air handler; no tools required for changeout.
Pull disconnect line voltage connection standard on all models.
Wall hanging bracket included for field installation.
Decorative wall panel or closet panel available
10-year limited warranty available.
Product registration required.
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
S SERIES AIR HANDLER
Dimensions
Air Handler Size | [5 empty] | A (in) | B (in) | C (in)
SM3A1805R | [5 empty] | 22 | 18.75 | 31
SM3A2407R | [5 empty] | 22 | 18.75 | 31
SM7A3110R | [5 empty] | 22 | 18.75 | 31
SM6A3710R | [5 empty] | 22 | 18.75 | 31
| Airflow (CFM) vs. External Static Pressure (inches W.C.) | [6 empty] | Electric Data
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
SM3A1805R | * ^ Low - Red | 606 | 591 | 576 | 559 | 529 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| Med - Blue | 802 | 784 | 751 | 722 | 693 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| High -Black | 1046 | 1013 | 987 | 943 | 885 |  | SM3A1805R | 5 | 17060.71 | 1.8 | 1.7 | 19.8556 | 22.5333 | 24.8194 | 28.1667 | 25 | 30
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
SM3A2407R | Low - Red | 606 | 591 | 576 | 559 | 529 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| * ^ Med - Blue | 802 | 784 | 751 | 722 | 693 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| High -Black | 1046 | 1013 | 987 | 943 | 885 |  | SM3A2407R | 7.5 | 25591.065 | 1.8 | 1.7 | 28.8833 | 32.95 | 36.1042 | 41.1875 | 40 | 45
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
SM7A3110R | Tap 1 | 656 | 600 | 567 | 522 | 473 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| Tap 2 | 842 | 800 | 782 | 739 | 716 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| * Tap 3 | 1059 | 1028 | 1004 | 972 | 946 |  | SM7A3110R | 10 | 34121.42 | 2.4 | 2.2 | 38.5111 | 43.8667 | 48.1389 | 54.8333 | 50 | 60
| ^ Tap 4 | 1106 | 1084 | 1053 | 1030 | 1000
| Tap 5 | 1137 | 1108 | 1085 | 1055 | 1031
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
SM6A3710R | Tap 1 | 848 | 800 | 769 | 726 | 692 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| Tap 2 | 1051 | 1028 | 1000 | 956 | 930 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| * Tap 3 | 1247 | 1215 | 1188 | 1161 | 1126 |  | SM6A3710R | 10 | 34121.42 | 3.1 | 2.9 | 39.2111 | 44.5667 | 49.0139 | 55.7083 | 50 | 60
| ^ Tap 4 | 1310 | 1279 | 1254 | 1228 | 1200
| Tap 5 | 1364 | 1334 | 1304 | 1279 | 1250
* Factory setting for cooling. | [7 empty] | [1] For 208 Volts use .751 correction factor for kW & BTUH.
^ Factory setting for heating. | [7 empty] | [2] Breaker supplied with heat kit may need to be changed. Verify breaker sizing based on min, circuit ampacity.
*** All airflow data is with a dry coil, filter, & electric heat.
A
B
C

## Nomenclature (hidden)
S | M2 |  | 1 |  | 24 |  | 05 |  | A |  | S | M2 |  | 1 |  | 24 |  | 05 |  | A
Series | Slab No. |  | Metering Device |  | Unit Size |  | Electric Heat |  | Refrigerant Detection System |  | Series | Slab No. |  | Metering Device |  | Unit Size |  | Electric Heat |  | Revision | Revision
S | K#: | Copper slab | 1: | Piston (R-454B & R-32) | 18, 24, 30, 36: | 3-speed PSC motor | 00: | None | R: | Included (Factory installed) | S | K#: | Copper slab | 1: | Piston (R-410A) | 18, 24, 30, 36: | 3-speed PSC motor | 00: | None
| L#: | Copper slab | A: | Non-bleed HP-A/C TXV (R-454B) | 19, 25, 31, 37, 39: | 5-speed ECM motor | 05: | 5 kW |  |  |  | L#: | Copper slab | 7: | Bleed HP-A/C TXV (R-410A) | 19, 25, 31, 37, 39: | 5-speed ECM motor | 05: | 5 kW
| M#: | Aluminum slab | B: | Non-bleed HP-A/C TXV (R-32) |  |  | 07: | 7.5 kW |  |  |  | M#: | Aluminum slab | 9: | Non-bleed HP-A/C TXV (R-410A) |  |  | 07: | 7.5 kW
|  |  | C: | Bleed HP-A/C TXV (R-454B) |  |  | 10: | 10 kW | [9 empty] | 10: | 10 kW

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model)
SM211800R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 4
SM211805R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3 | 3/4 | 3/8 | 4
SM211807R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 4 | 3/4 | 3/8 | 4
SM211810R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 5 | 3/4 | 3/8 | 4
SM211900R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 6 | 3/4 | 3/8 | 4
SM211905R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 7 | 3/4 | 3/8 | 4
SM211907R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 8 | 3/4 | 3/8 | 4
SM211910R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 9 | 3/4 | 3/8 | 4
SM212400R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 10 | 3/4 | 3/8 | 4
SM212405R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 11 | 3/4 | 3/8 | 4
SM212407R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 12 | 3/4 | 3/8 | 4
SM212410R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 13 | 3/4 | 3/8 | 4
SM212500R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 14 | 3/4 | 3/8 | 4
SM212505R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 15 | 3/4 | 3/8 | 4
SM212507R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 16 | 3/4 | 3/8 | 4
SM212510R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 17 | 3/4 | 3/8 | 4
SM213000R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 18 | 3/4 | 3/8 | 4
SM213005R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 19 | 3/4 | 3/8 | 4
SM213007R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 20 | 3/4 | 3/8 | 4
SM213010R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 21 | 3/4 | 3/8 | 4
SM213100R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 22 | 3/4 | 3/8 | 4
SM213105R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 23 | 3/4 | 3/8 | 4
SM213107R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 24 | 3/4 | 3/8 | 4
SM213110R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 25 | 3/4 | 3/8 | 4
SM213600R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 26 | 3/4 | 3/8 | 4
SM213605R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 27 | 3/4 | 3/8 | 4
SM213607R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 28 | 3/4 | 3/8 | 4
SM213610R | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 29 | 3/4 | 3/8 | 4
SM213700R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 30 | 3/4 | 3/8 | 4
SM213705R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 31 | 3/4 | 3/8 | 4
SM213707R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 32 | 3/4 | 3/8 | 4
SM213710R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 33 | 3/4 | 3/8 | 4
SM2A1800R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 38 | 3/4 | 3/8 | 4
SM2A1805R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 39 | 3/4 | 3/8 | 4
SM2A1807R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 40 | 3/4 | 3/8 | 4
SM2A1810R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 41 | 3/4 | 3/8 | 4
SM2A1900R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 42 | 3/4 | 3/8 | 4
SM2A1905R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 43 | 3/4 | 3/8 | 4
SM2A1907R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 44 | 3/4 | 3/8 | 4
SM2A1910R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 45 | 3/4 | 3/8 | 4
SM2A2400R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 46 | 3/4 | 3/8 | 4
SM2A2405R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 47 | 3/4 | 3/8 | 4
SM2A2407R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 48 | 3/4 | 3/8 | 4
SM2A2410R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 49 | 3/4 | 3/8 | 4
SM2A2500R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 50 | 3/4 | 3/8 | 4
SM2A2505R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 51 | 3/4 | 3/8 | 4
SM2A2507R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 52 | 3/4 | 3/8 | 4
SM2A2510R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 53 | 3/4 | 3/8 | 4
SM2A3000R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 54 | 3/4 | 3/8 | 4
SM2A3005R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 55 | 3/4 | 3/8 | 4
SM2A3007R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 56 | 3/4 | 3/8 | 4
SM2A3010R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 57 | 3/4 | 3/8 | 4
SM2A3100R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 58 | 3/4 | 3/8 | 4
SM2A3105R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 59 | 3/4 | 3/8 | 4
SM2A3107R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 60 | 3/4 | 3/8 | 4
SM2A3110R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 61 | 3/4 | 3/8 | 4
SM2A3600R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 62 | 3/4 | 3/8 | 4
SM2A3605R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 63 | 3/4 | 3/8 | 4
SM2A3607R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 64 | 3/4 | 3/8 | 4
SM2A3610R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 65 | 3/4 | 3/8 | 4
SM2A3700R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 66 | 3/4 | 3/8 | 4
SM2A3705R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 67 | 3/4 | 3/8 | 4
SM2A3707R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 68 | 3/4 | 3/8 | 4
SM2A3710R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 69 | 3/4 | 3/8 | 4
SM2B1800R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 74 | 3/4 | 3/8 | 4
SM2B1805R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 75 | 3/4 | 3/8 | 4
SM2B1807R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 76 | 3/4 | 3/8 | 4
SM2B1810R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 77 | 3/4 | 3/8 | 4
SM2B1900R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 78 | 3/4 | 3/8 | 4
SM2B1905R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 79 | 3/4 | 3/8 | 4
SM2B1907R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 80 | 3/4 | 3/8 | 4
SM2B1910R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 81 | 3/4 | 3/8 | 4
SM2B2400R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 82 | 3/4 | 3/8 | 4
SM2B2405R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 83 | 3/4 | 3/8 | 4
SM2B2407R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 84 | 3/4 | 3/8 | 4
SM2B2410R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 85 | 3/4 | 3/8 | 4
SM2B2500R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 86 | 3/4 | 3/8 | 4
SM2B2505R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 87 | 3/4 | 3/8 | 4
SM2B2507R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 88 | 3/4 | 3/8 | 4
SM2B2510R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 89 | 3/4 | 3/8 | 4
SM2B3000R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 90 | 3/4 | 3/8 | 4
SM2B3005R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 91 | 3/4 | 3/8 | 4
SM2B3007R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 92 | 3/4 | 3/8 | 4
SM2B3010R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 93 | 3/4 | 3/8 | 4
SM2B3100R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 94 | 3/4 | 3/8 | 4
SM2B3105R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 95 | 3/4 | 3/8 | 4
SM2B3107R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 96 | 3/4 | 3/8 | 4
SM2B3110R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 97 | 3/4 | 3/8 | 4
SM2B3600R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 98 | 3/4 | 3/8 | 4
SM2B3605R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 99 | 3/4 | 3/8 | 4
SM2B3607R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 100 | 3/4 | 3/8 | 4
SM2B3610R | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 101 | 3/4 | 3/8 | 4
SM2B3700R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 102 | 3/4 | 3/8 | 4
SM2B3705R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 103 | 3/4 | 3/8 | 4
SM2B3707R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 104 | 3/4 | 3/8 | 4
SM2B3710R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 105 | 3/4 | 3/8 | 4
SM2C1800R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 110 | 3/4 | 3/8 | 4
SM2C1805R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 111 | 3/4 | 3/8 | 4
SM2C1807R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 112 | 3/4 | 3/8 | 4
SM2C1810R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 113 | 3/4 | 3/8 | 4
SM2C1900R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 114 | 3/4 | 3/8 | 4
SM2C1905R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 115 | 3/4 | 3/8 | 4
SM2C1907R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 116 | 3/4 | 3/8 | 4
SM2C1910R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 117 | 3/4 | 3/8 | 4
SM2C2400R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 118 | 3/4 | 3/8 | 4
SM2C2405R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 119 | 3/4 | 3/8 | 4
SM2C2407R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 120 | 3/4 | 3/8 | 4
SM2C2410R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 121 | 3/4 | 3/8 | 4
SM2C2500R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 122 | 3/4 | 3/8 | 4
SM2C2505R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 123 | 3/4 | 3/8 | 4
SM2C2507R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 124 | 3/4 | 3/8 | 4
SM2C2510R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 125 | 3/4 | 3/8 | 4
SM2C3000R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 126 | 3/4 | 3/8 | 4
SM2C3005R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 127 | 3/4 | 3/8 | 4
SM2C3007R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 128 | 3/4 | 3/8 | 4
SM2C3010R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 129 | 3/4 | 3/8 | 4
SM2C3100R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 130 | 3/4 | 3/8 | 4
SM2C3105R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 131 | 3/4 | 3/8 | 4
SM2C3107R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 132 | 3/4 | 3/8 | 4
SM2C3110R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 133 | 3/4 | 3/8 | 4
SM2C3600R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 134 | 3/4 | 3/8 | 4
SM2C3605R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 135 | 3/4 | 3/8 | 4
SM2C3607R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 136 | 3/4 | 3/8 | 4
SM2C3610R | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 137 | 3/4 | 3/8 | 4
SM2C3700R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 138 | 3/4 | 3/8 | 4
SM2C3705R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 139 | 3/4 | 3/8 | 4
SM2C3707R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 140 | 3/4 | 3/8 | 4
SM2C3710R | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 141 | 3/4 | 3/8 | 4
SM311800R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 146 | 3/4 | 3/8 | 4
SM311805R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 147 | 3/4 | 3/8 | 4
SM311807R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 148 | 3/4 | 3/8 | 4
SM311810R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 149 | 3/4 | 3/8 | 4
SM311900R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 150 | 3/4 | 3/8 | 4
SM311905R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 151 | 3/4 | 3/8 | 4
SM311907R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 152 | 3/4 | 3/8 | 4
SM311910R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 153 | 3/4 | 3/8 | 4
SM312400R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 154 | 3/4 | 3/8 | 4
SM312405R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 155 | 3/4 | 3/8 | 4
SM312407R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 156 | 3/4 | 3/8 | 4
SM312410R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 157 | 3/4 | 3/8 | 4
SM312500R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 158 | 3/4 | 3/8 | 4
SM312505R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 159 | 3/4 | 3/8 | 4
SM312507R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 160 | 3/4 | 3/8 | 4
SM312510R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 161 | 3/4 | 3/8 | 4
SM313000R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 162 | 3/4 | 3/8 | 4
SM313005R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 163 | 3/4 | 3/8 | 4
SM313007R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 164 | 3/4 | 3/8 | 4
SM313010R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 165 | 3/4 | 3/8 | 4
SM313100R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 166 | 3/4 | 3/8 | 4
SM313105R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 167 | 3/4 | 3/8 | 4
SM313107R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 168 | 3/4 | 3/8 | 4
SM313110R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 169 | 3/4 | 3/8 | 4
SM313600R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 170 | 3/4 | 3/8 | 4
SM313605R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 171 | 3/4 | 3/8 | 4
SM313607R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 172 | 3/4 | 3/8 | 4
SM313610R | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 173 | 3/4 | 3/8 | 4
SM313700R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 174 | 3/4 | 3/8 | 4
SM313705R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 175 | 3/4 | 3/8 | 4
SM313707R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 176 | 3/4 | 3/8 | 4
SM313710R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 177 | 3/4 | 3/8 | 4
SM3A1800R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 182 | 3/4 | 3/8 | 4
SM3A1805R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 183 | 3/4 | 3/8 | 4
SM3A1807R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 184 | 3/4 | 3/8 | 4
SM3A1810R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 185 | 3/4 | 3/8 | 4
SM3A1900R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 186 | 3/4 | 3/8 | 4
SM3A1905R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 187 | 3/4 | 3/8 | 4
SM3A1907R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 188 | 3/4 | 3/8 | 4
SM3A1910R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 189 | 3/4 | 3/8 | 4
SM3A2400R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 190 | 3/4 | 3/8 | 4
SM3A2405R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 191 | 3/4 | 3/8 | 4
SM3A2407R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 192 | 3/4 | 3/8 | 4
SM3A2410R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 193 | 3/4 | 3/8 | 4
SM3A2500R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 194 | 3/4 | 3/8 | 4
SM3A2505R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 195 | 3/4 | 3/8 | 4
SM3A2507R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 196 | 3/4 | 3/8 | 4
SM3A2510R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 197 | 3/4 | 3/8 | 4
SM3A3000R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 198 | 3/4 | 3/8 | 4
SM3A3005R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 199 | 3/4 | 3/8 | 4
SM3A3007R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 200 | 3/4 | 3/8 | 4
SM3A3010R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 201 | 3/4 | 3/8 | 4
SM3A3100R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 202 | 3/4 | 3/8 | 4
SM3A3105R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 203 | 3/4 | 3/8 | 4
SM3A3107R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 204 | 3/4 | 3/8 | 4
SM3A3110R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 205 | 3/4 | 3/8 | 4
SM3A3600R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 206 | 3/4 | 3/8 | 4
SM3A3605R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 207 | 3/4 | 3/8 | 4
SM3A3607R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 208 | 3/4 | 3/8 | 4
SM3A3610R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 209 | 3/4 | 3/8 | 4
SM3A3700R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 210 | 3/4 | 3/8 | 4
SM3A3705R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 211 | 3/4 | 3/8 | 4
SM3A3707R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 212 | 3/4 | 3/8 | 4
SM3A3710R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 213 | 3/4 | 3/8 | 4
SM3B1800R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 218 | 3/4 | 3/8 | 4
SM3B1805R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 219 | 3/4 | 3/8 | 4
SM3B1807R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 220 | 3/4 | 3/8 | 4
SM3B1810R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 221 | 3/4 | 3/8 | 4
SM3B1900R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 222 | 3/4 | 3/8 | 4
SM3B1905R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 223 | 3/4 | 3/8 | 4
SM3B1907R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 224 | 3/4 | 3/8 | 4
SM3B1910R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 225 | 3/4 | 3/8 | 4
SM3B2400R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 226 | 3/4 | 3/8 | 4
SM3B2405R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 227 | 3/4 | 3/8 | 4
SM3B2407R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 228 | 3/4 | 3/8 | 4
SM3B2410R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 229 | 3/4 | 3/8 | 4
SM3B2500R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 230 | 3/4 | 3/8 | 4
SM3B2505R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 231 | 3/4 | 3/8 | 4
SM3B2507R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 232 | 3/4 | 3/8 | 4
SM3B2510R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 233 | 3/4 | 3/8 | 4
SM3B3000R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 234 | 3/4 | 3/8 | 4
SM3B3005R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 235 | 3/4 | 3/8 | 4
SM3B3007R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 236 | 3/4 | 3/8 | 4
SM3B3010R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 237 | 3/4 | 3/8 | 4
SM3B3100R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 238 | 3/4 | 3/8 | 4
SM3B3105R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 239 | 3/4 | 3/8 | 4
SM3B3107R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 240 | 3/4 | 3/8 | 4
SM3B3110R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 241 | 3/4 | 3/8 | 4
SM3B3600R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 242 | 3/4 | 3/8 | 4
SM3B3605R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 243 | 3/4 | 3/8 | 4
SM3B3607R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 244 | 3/4 | 3/8 | 4
SM3B3610R | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 245 | 3/4 | 3/8 | 4
SM3B3700R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 246 | 3/4 | 3/8 | 4
SM3B3705R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 247 | 3/4 | 3/8 | 4
SM3B3707R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 248 | 3/4 | 3/8 | 4
SM3B3710R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 249 | 3/4 | 3/8 | 4
SM3C1800R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 254 | 3/4 | 3/8 | 4
SM3C1805R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 255 | 3/4 | 3/8 | 4
SM3C1807R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 256 | 3/4 | 3/8 | 4
SM3C1810R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 257 | 3/4 | 3/8 | 4
SM3C1900R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 258 | 3/4 | 3/8 | 4
SM3C1905R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 259 | 3/4 | 3/8 | 4
SM3C1907R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 260 | 3/4 | 3/8 | 4
SM3C1910R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 261 | 3/4 | 3/8 | 4
SM3C2400R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 262 | 3/4 | 3/8 | 4
SM3C2405R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 263 | 3/4 | 3/8 | 4
SM3C2407R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 264 | 3/4 | 3/8 | 4
SM3C2410R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 265 | 3/4 | 3/8 | 4
SM3C2500R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 266 | 3/4 | 3/8 | 4
SM3C2505R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 267 | 3/4 | 3/8 | 4
SM3C2507R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 268 | 3/4 | 3/8 | 4
SM3C2510R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 269 | 3/4 | 3/8 | 4
SM3C3000R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 270 | 3/4 | 3/8 | 4
SM3C3005R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 271 | 3/4 | 3/8 | 4
SM3C3007R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 272 | 3/4 | 3/8 | 4
SM3C3010R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 273 | 3/4 | 3/8 | 4
SM3C3100R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 274 | 3/4 | 3/8 | 4
SM3C3105R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 275 | 3/4 | 3/8 | 4
SM3C3107R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 276 | 3/4 | 3/8 | 4
SM3C3110R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 277 | 3/4 | 3/8 | 4
SM3C3600R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 278 | 3/4 | 3/8 | 4
SM3C3605R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 279 | 3/4 | 3/8 | 4
SM3C3607R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 280 | 3/4 | 3/8 | 4
SM3C3610R | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 281 | 3/4 | 3/8 | 4
SM3C3700R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 282 | 3/4 | 3/8 | 4
SM3C3705R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 283 | 3/4 | 3/8 | 4
SM3C3707R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 284 | 3/4 | 3/8 | 4
SM3C3710R | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 285 | 3/4 | 3/8 | 4
SM511800R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 290 | 3/4 | 3/8 | 4
SM511805R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 291 | 3/4 | 3/8 | 4
SM511807R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 292 | 3/4 | 3/8 | 4
SM511810R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 293 | 3/4 | 3/8 | 4
SM511900R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 294 | 3/4 | 3/8 | 4
SM511905R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 295 | 3/4 | 3/8 | 4
SM511907R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 296 | 3/4 | 3/8 | 4
SM511910R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 297 | 3/4 | 3/8 | 4
SM512400R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 298 | 3/4 | 3/8 | 4
SM512405R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 299 | 3/4 | 3/8 | 4
SM512407R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 300 | 3/4 | 3/8 | 4
SM512410R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 301 | 3/4 | 3/8 | 4
SM512500R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 302 | 3/4 | 3/8 | 4
SM512505R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 303 | 3/4 | 3/8 | 4
SM512507R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 304 | 3/4 | 3/8 | 4
SM512510R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 305 | 3/4 | 3/8 | 4
SM513000R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 306 | 3/4 | 3/8 | 4
SM513005R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 307 | 3/4 | 3/8 | 4
SM513007R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 308 | 3/4 | 3/8 | 4
SM513010R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 309 | 3/4 | 3/8 | 4
SM513100R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 310 | 3/4 | 3/8 | 4
SM513105R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 311 | 3/4 | 3/8 | 4
SM513107R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 312 | 3/4 | 3/8 | 4
SM513110R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 313 | 3/4 | 3/8 | 4
SM513600R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 314 | 3/4 | 3/8 | 4
SM513605R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 315 | 3/4 | 3/8 | 4
SM513607R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 316 | 3/4 | 3/8 | 4
SM513610R | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 317 | 3/4 | 3/8 | 4
SM513700R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 318 | 3/4 | 3/8 | 4
SM513705R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 319 | 3/4 | 3/8 | 4
SM513707R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 320 | 3/4 | 3/8 | 4
SM513710R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 321 | 3/4 | 3/8 | 4
SM5A1800R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 326 | 3/4 | 3/8 | 4
SM5A1805R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 327 | 3/4 | 3/8 | 4
SM5A1807R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 328 | 3/4 | 3/8 | 4
SM5A1810R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 329 | 3/4 | 3/8 | 4
SM5A1900R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 330 | 3/4 | 3/8 | 4
SM5A1905R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 331 | 3/4 | 3/8 | 4
SM5A1907R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 332 | 3/4 | 3/8 | 4
SM5A1910R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 333 | 3/4 | 3/8 | 4
SM5A2400R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 334 | 3/4 | 3/8 | 4
SM5A2405R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 335 | 3/4 | 3/8 | 4
SM5A2407R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 336 | 3/4 | 3/8 | 4
SM5A2410R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 337 | 3/4 | 3/8 | 4
SM5A2500R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 338 | 3/4 | 3/8 | 4
SM5A2505R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 339 | 3/4 | 3/8 | 4
SM5A2507R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 340 | 3/4 | 3/8 | 4
SM5A2510R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 341 | 3/4 | 3/8 | 4
SM5A3000R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 342 | 3/4 | 3/8 | 4
SM5A3005R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 343 | 3/4 | 3/8 | 4
SM5A3007R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 344 | 3/4 | 3/8 | 4
SM5A3010R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 345 | 3/4 | 3/8 | 4
SM5A3100R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 346 | 3/4 | 3/8 | 4
SM5A3105R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 347 | 3/4 | 3/8 | 4
SM5A3107R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 348 | 3/4 | 3/8 | 4
SM5A3110R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 349 | 3/4 | 3/8 | 4
SM5A3600R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 350 | 3/4 | 3/8 | 4
SM5A3605R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 351 | 3/4 | 3/8 | 4
SM5A3607R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 352 | 3/4 | 3/8 | 4
SM5A3610R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 353 | 3/4 | 3/8 | 4
SM5A3700R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 354 | 3/4 | 3/8 | 4
SM5A3705R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 355 | 3/4 | 3/8 | 4
SM5A3707R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 356 | 3/4 | 3/8 | 4
SM5A3710R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 357 | 3/4 | 3/8 | 4
SM5B1800R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 362 | 3/4 | 3/8 | 4
SM5B1805R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 363 | 3/4 | 3/8 | 4
SM5B1807R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 364 | 3/4 | 3/8 | 4
SM5B1810R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 365 | 3/4 | 3/8 | 4
SM5B1900R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 366 | 3/4 | 3/8 | 4
SM5B1905R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 367 | 3/4 | 3/8 | 4
SM5B1907R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 368 | 3/4 | 3/8 | 4
SM5B1910R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 369 | 3/4 | 3/8 | 4
SM5B2400R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 370 | 3/4 | 3/8 | 4
SM5B2405R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 371 | 3/4 | 3/8 | 4
SM5B2407R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 372 | 3/4 | 3/8 | 4
SM5B2410R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 373 | 3/4 | 3/8 | 4
SM5B2500R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 374 | 3/4 | 3/8 | 4
SM5B2505R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 375 | 3/4 | 3/8 | 4
SM5B2507R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 376 | 3/4 | 3/8 | 4
SM5B2510R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 377 | 3/4 | 3/8 | 4
SM5B3000R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 378 | 3/4 | 3/8 | 4
SM5B3005R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 379 | 3/4 | 3/8 | 4
SM5B3007R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 380 | 3/4 | 3/8 | 4
SM5B3010R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 381 | 3/4 | 3/8 | 4
SM5B3100R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 382 | 3/4 | 3/8 | 4
SM5B3105R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 383 | 3/4 | 3/8 | 4
SM5B3107R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 384 | 3/4 | 3/8 | 4
SM5B3110R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 385 | 3/4 | 3/8 | 4
SM5B3600R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 386 | 3/4 | 3/8 | 4
SM5B3605R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 387 | 3/4 | 3/8 | 4
SM5B3607R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 388 | 3/4 | 3/8 | 4
SM5B3610R | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 389 | 3/4 | 3/8 | 4
SM5B3700R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 390 | 3/4 | 3/8 | 4
SM5B3705R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 391 | 3/4 | 3/8 | 4
SM5B3707R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 392 | 3/4 | 3/8 | 4
SM5B3710R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 393 | 3/4 | 3/8 | 4
SM5C1800R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 398 | 3/4 | 3/8 | 4
SM5C1805R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 399 | 3/4 | 3/8 | 4
SM5C1807R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 400 | 3/4 | 3/8 | 4
SM5C1810R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 401 | 3/4 | 3/8 | 4
SM5C1900R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 402 | 3/4 | 3/8 | 4
SM5C1905R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 403 | 3/4 | 3/8 | 4
SM5C1907R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 404 | 3/4 | 3/8 | 4
SM5C1910R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 405 | 3/4 | 3/8 | 4
SM5C2400R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 406 | 3/4 | 3/8 | 4
SM5C2405R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 407 | 3/4 | 3/8 | 4
SM5C2407R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 408 | 3/4 | 3/8 | 4
SM5C2410R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 409 | 3/4 | 3/8 | 4
SM5C2500R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 410 | 3/4 | 3/8 | 4
SM5C2505R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 411 | 3/4 | 3/8 | 4
SM5C2507R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 412 | 3/4 | 3/8 | 4
SM5C2510R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 413 | 3/4 | 3/8 | 4
SM5C3000R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 414 | 3/4 | 3/8 | 4
SM5C3005R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 415 | 3/4 | 3/8 | 4
SM5C3007R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 416 | 3/4 | 3/8 | 4
SM5C3010R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 417 | 3/4 | 3/8 | 4
SM5C3100R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 418 | 3/4 | 3/8 | 4
SM5C3105R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 419 | 3/4 | 3/8 | 4
SM5C3107R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 420 | 3/4 | 3/8 | 4
SM5C3110R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 421 | 3/4 | 3/8 | 4
SM5C3600R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 422 | 3/4 | 3/8 | 4
SM5C3605R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 423 | 3/4 | 3/8 | 4
SM5C3607R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 424 | 3/4 | 3/8 | 4
SM5C3610R | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 425 | 3/4 | 3/8 | 4
SM5C3700R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 426 | 3/4 | 3/8 | 4
SM5C3705R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 427 | 3/4 | 3/8 | 4
SM5C3707R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 428 | 3/4 | 3/8 | 4
SM5C3710R | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 429 | 3/4 | 3/8 | 4
SM611800R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 434 | 3/4 | 3/8 | 4
SM611805R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 435 | 3/4 | 3/8 | 4
SM611807R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 436 | 3/4 | 3/8 | 4
SM611810R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 437 | 3/4 | 3/8 | 4
SM611900R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 438 | 3/4 | 3/8 | 4
SM611905R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 439 | 3/4 | 3/8 | 4
SM611907R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 440 | 3/4 | 3/8 | 4
SM611910R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 441 | 3/4 | 3/8 | 4
SM612400R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 442 | 3/4 | 3/8 | 4
SM612405R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 443 | 3/4 | 3/8 | 4
SM612407R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 444 | 3/4 | 3/8 | 4
SM612410R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 445 | 3/4 | 3/8 | 4
SM612500R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 446 | 3/4 | 3/8 | 4
SM612505R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 447 | 3/4 | 3/8 | 4
SM612507R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 448 | 3/4 | 3/8 | 4
SM612510R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 449 | 3/4 | 3/8 | 4
SM613000R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 450 | 3/4 | 3/8 | 4
SM613005R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 451 | 3/4 | 3/8 | 4
SM613007R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 452 | 3/4 | 3/8 | 4
SM613010R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 453 | 3/4 | 3/8 | 4
SM613100R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 454 | 3/4 | 3/8 | 4
SM613105R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 455 | 3/4 | 3/8 | 4
SM613107R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 456 | 3/4 | 3/8 | 4
SM613110R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 457 | 3/4 | 3/8 | 4
SM613600R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 458 | 3/4 | 3/8 | 4
SM613605R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 459 | 3/4 | 3/8 | 4
SM613607R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 460 | 3/4 | 3/8 | 4
SM613610R | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 461 | 3/4 | 3/8 | 4
SM613700R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 462 | 3/4 | 3/8 | 4
SM613705R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 463 | 3/4 | 3/8 | 4
SM613707R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 464 | 3/4 | 3/8 | 4
SM613710R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 465 | 3/4 | 3/8 | 4
SM6A1800R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 470 | 3/4 | 3/8 | 4
SM6A1805R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 471 | 3/4 | 3/8 | 4
SM6A1807R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 472 | 3/4 | 3/8 | 4
SM6A1810R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 473 | 3/4 | 3/8 | 4
SM6A1900R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 474 | 3/4 | 3/8 | 4
SM6A1905R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 475 | 3/4 | 3/8 | 4
SM6A1907R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 476 | 3/4 | 3/8 | 4
SM6A1910R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 477 | 3/4 | 3/8 | 4
SM6A2400R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 478 | 3/4 | 3/8 | 4
SM6A2405R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 479 | 3/4 | 3/8 | 4
SM6A2407R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 480 | 3/4 | 3/8 | 4
SM6A2410R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 481 | 3/4 | 3/8 | 4
SM6A2500R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 482 | 3/4 | 3/8 | 4
SM6A2505R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 483 | 3/4 | 3/8 | 4
SM6A2507R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 484 | 3/4 | 3/8 | 4
SM6A2510R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 485 | 3/4 | 3/8 | 4
SM6A3000R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 486 | 3/4 | 3/8 | 4
SM6A3005R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 487 | 3/4 | 3/8 | 4
SM6A3007R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 488 | 3/4 | 3/8 | 4
SM6A3010R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 489 | 3/4 | 3/8 | 4
SM6A3100R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 490 | 3/4 | 3/8 | 4
SM6A3105R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 491 | 3/4 | 3/8 | 4
SM6A3107R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 492 | 3/4 | 3/8 | 4
SM6A3110R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 493 | 3/4 | 3/8 | 4
SM6A3600R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 494 | 3/4 | 3/8 | 4
SM6A3605R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 495 | 3/4 | 3/8 | 4
SM6A3607R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 496 | 3/4 | 3/8 | 4
SM6A3610R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 497 | 3/4 | 3/8 | 4
SM6A3700R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 498 | 3/4 | 3/8 | 4
SM6A3705R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 499 | 3/4 | 3/8 | 4
SM6A3707R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 500 | 3/4 | 3/8 | 4
SM6A3710R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 501 | 3/4 | 3/8 | 4
SM6B1800R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 506 | 3/4 | 3/8 | 4
SM6B1805R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 507 | 3/4 | 3/8 | 4
SM6B1807R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 508 | 3/4 | 3/8 | 4
SM6B1810R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 509 | 3/4 | 3/8 | 4
SM6B1900R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 510 | 3/4 | 3/8 | 4
SM6B1905R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 511 | 3/4 | 3/8 | 4
SM6B1907R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 512 | 3/4 | 3/8 | 4
SM6B1910R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 513 | 3/4 | 3/8 | 4
SM6B2400R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 514 | 3/4 | 3/8 | 4
SM6B2405R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 515 | 3/4 | 3/8 | 4
SM6B2407R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 516 | 3/4 | 3/8 | 4
SM6B2410R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 517 | 3/4 | 3/8 | 4
SM6B2500R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 518 | 3/4 | 3/8 | 4
SM6B2505R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 519 | 3/4 | 3/8 | 4
SM6B2507R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 520 | 3/4 | 3/8 | 4
SM6B2510R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 521 | 3/4 | 3/8 | 4
SM6B3000R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 522 | 3/4 | 3/8 | 4
SM6B3005R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 523 | 3/4 | 3/8 | 4
SM6B3007R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 524 | 3/4 | 3/8 | 4
SM6B3010R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 525 | 3/4 | 3/8 | 4
SM6B3100R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 526 | 3/4 | 3/8 | 4
SM6B3105R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 527 | 3/4 | 3/8 | 4
SM6B3107R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 528 | 3/4 | 3/8 | 4
SM6B3110R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 529 | 3/4 | 3/8 | 4
SM6B3600R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 530 | 3/4 | 3/8 | 4
SM6B3605R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 531 | 3/4 | 3/8 | 4
SM6B3607R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 532 | 3/4 | 3/8 | 4
SM6B3610R | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 533 | 3/4 | 3/8 | 4
SM6B3700R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 534 | 3/4 | 3/8 | 4
SM6B3705R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 535 | 3/4 | 3/8 | 4
SM6B3707R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 536 | 3/4 | 3/8 | 4
SM6B3710R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 537 | 3/4 | 3/8 | 4
SM6C1800R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 542 | 3/4 | 3/8 | 4
SM6C1805R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 543 | 3/4 | 3/8 | 4
SM6C1807R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 544 | 3/4 | 3/8 | 4
SM6C1810R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 545 | 3/4 | 3/8 | 4
SM6C1900R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 546 | 3/4 | 3/8 | 4
SM6C1905R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 547 | 3/4 | 3/8 | 4
SM6C1907R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 548 | 3/4 | 3/8 | 4
SM6C1910R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 549 | 3/4 | 3/8 | 4
SM6C2400R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 550 | 3/4 | 3/8 | 4
SM6C2405R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 551 | 3/4 | 3/8 | 4
SM6C2407R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 552 | 3/4 | 3/8 | 4
SM6C2410R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 553 | 3/4 | 3/8 | 4
SM6C2500R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 554 | 3/4 | 3/8 | 4
SM6C2505R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 555 | 3/4 | 3/8 | 4
SM6C2507R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 556 | 3/4 | 3/8 | 4
SM6C2510R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 557 | 3/4 | 3/8 | 4
SM6C3000R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 558 | 3/4 | 3/8 | 4
SM6C3005R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 559 | 3/4 | 3/8 | 4
SM6C3007R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 560 | 3/4 | 3/8 | 4
SM6C3010R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 561 | 3/4 | 3/8 | 4
SM6C3100R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 562 | 3/4 | 3/8 | 4
SM6C3105R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 563 | 3/4 | 3/8 | 4
SM6C3107R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 564 | 3/4 | 3/8 | 4
SM6C3110R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 565 | 3/4 | 3/8 | 4
SM6C3600R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 566 | 3/4 | 3/8 | 4
SM6C3605R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 567 | 3/4 | 3/8 | 4
SM6C3607R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 568 | 3/4 | 3/8 | 4
SM6C3610R | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 569 | 3/4 | 3/8 | 4
SM6C3700R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 570 | 3/4 | 3/8 | 4
SM6C3705R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 571 | 3/4 | 3/8 | 4
SM6C3707R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 572 | 3/4 | 3/8 | 4
SM6C3710R | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 573 | 3/4 | 3/8 | 4
SM711800R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 578 | 3/4 | 3/8 | 4
SM711805R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 579 | 3/4 | 3/8 | 4
SM711807R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 580 | 3/4 | 3/8 | 4
SM711810R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 581 | 3/4 | 3/8 | 4
SM711900R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 582 | 3/4 | 3/8 | 4
SM711905R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 583 | 3/4 | 3/8 | 4
SM711907R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 584 | 3/4 | 3/8 | 4
SM711910R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 585 | 3/4 | 3/8 | 4
SM712400R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 586 | 3/4 | 3/8 | 4
SM712405R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 587 | 3/4 | 3/8 | 4
SM712407R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 588 | 3/4 | 3/8 | 4
SM712410R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 589 | 3/4 | 3/8 | 4
SM712500R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 590 | 3/4 | 3/8 | 4
SM712505R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 591 | 3/4 | 3/8 | 4
SM712507R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 592 | 3/4 | 3/8 | 4
SM712510R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 593 | 3/4 | 3/8 | 4
SM713000R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 594 | 3/4 | 3/8 | 4
SM713005R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 595 | 3/4 | 3/8 | 4
SM713007R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 596 | 3/4 | 3/8 | 4
SM713010R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 597 | 3/4 | 3/8 | 4
SM713100R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 598 | 3/4 | 3/8 | 4
SM713105R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 599 | 3/4 | 3/8 | 4
SM713107R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 600 | 3/4 | 3/8 | 4
SM713110R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 601 | 3/4 | 3/8 | 4
SM713600R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 602 | 3/4 | 3/8 | 4
SM713605R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 603 | 3/4 | 3/8 | 4
SM713607R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 604 | 3/4 | 3/8 | 4
SM713610R | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 605 | 3/4 | 3/8 | 4
SM713700R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 606 | 3/4 | 3/8 | 4
SM713705R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 607 | 3/4 | 3/8 | 4
SM713707R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 608 | 3/4 | 3/8 | 4
SM713710R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 609 | 3/4 | 3/8 | 4
SM7A1800R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 614 | 3/4 | 3/8 | 4
SM7A1805R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 615 | 3/4 | 3/8 | 4
SM7A1807R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 616 | 3/4 | 3/8 | 4
SM7A1810R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 617 | 3/4 | 3/8 | 4
SM7A1900R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 618 | 3/4 | 3/8 | 4
SM7A1905R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 619 | 3/4 | 3/8 | 4
SM7A1907R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 620 | 3/4 | 3/8 | 4
SM7A1910R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 621 | 3/4 | 3/8 | 4
SM7A2400R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 622 | 3/4 | 3/8 | 4
SM7A2405R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 623 | 3/4 | 3/8 | 4
SM7A2407R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 624 | 3/4 | 3/8 | 4
SM7A2410R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 625 | 3/4 | 3/8 | 4
SM7A2500R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 626 | 3/4 | 3/8 | 4
SM7A2505R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 627 | 3/4 | 3/8 | 4
SM7A2507R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 628 | 3/4 | 3/8 | 4
SM7A2510R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 629 | 3/4 | 3/8 | 4
SM7A3000R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 630 | 3/4 | 3/8 | 4
SM7A3005R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 631 | 3/4 | 3/8 | 4
SM7A3007R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 632 | 3/4 | 3/8 | 4
SM7A3010R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 633 | 3/4 | 3/8 | 4
SM7A3100R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 634 | 3/4 | 3/8 | 4
SM7A3105R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 635 | 3/4 | 3/8 | 4
SM7A3107R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 636 | 3/4 | 3/8 | 4
SM7A3110R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 637 | 3/4 | 3/8 | 4
SM7A3600R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 638 | 3/4 | 3/8 | 4
SM7A3605R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 639 | 3/4 | 3/8 | 4
SM7A3607R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 640 | 3/4 | 3/8 | 4
SM7A3610R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 641 | 3/4 | 3/8 | 4
SM7A3700R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 642 | 3/4 | 3/8 | 4
SM7A3705R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 643 | 3/4 | 3/8 | 4
SM7A3707R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 644 | 3/4 | 3/8 | 4
SM7A3710R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 645 | 3/4 | 3/8 | 4
SM7B1800R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 650 | 3/4 | 3/8 | 4
SM7B1805R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 651 | 3/4 | 3/8 | 4
SM7B1807R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 652 | 3/4 | 3/8 | 4
SM7B1810R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 653 | 3/4 | 3/8 | 4
SM7B1900R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 654 | 3/4 | 3/8 | 4
SM7B1905R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 655 | 3/4 | 3/8 | 4
SM7B1907R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 656 | 3/4 | 3/8 | 4
SM7B1910R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 657 | 3/4 | 3/8 | 4
SM7B2400R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 658 | 3/4 | 3/8 | 4
SM7B2405R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 659 | 3/4 | 3/8 | 4
SM7B2407R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 660 | 3/4 | 3/8 | 4
SM7B2410R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 661 | 3/4 | 3/8 | 4
SM7B2500R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 662 | 3/4 | 3/8 | 4
SM7B2505R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 663 | 3/4 | 3/8 | 4
SM7B2507R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 664 | 3/4 | 3/8 | 4
SM7B2510R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 665 | 3/4 | 3/8 | 4
SM7B3000R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 666 | 3/4 | 3/8 | 4
SM7B3005R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 667 | 3/4 | 3/8 | 4
SM7B3007R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 668 | 3/4 | 3/8 | 4
SM7B3010R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 669 | 3/4 | 3/8 | 4
SM7B3100R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 670 | 3/4 | 3/8 | 4
SM7B3105R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 671 | 3/4 | 3/8 | 4
SM7B3107R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 672 | 3/4 | 3/8 | 4
SM7B3110R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 673 | 3/4 | 3/8 | 4
SM7B3600R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 674 | 3/4 | 3/8 | 4
SM7B3605R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 675 | 3/4 | 3/8 | 4
SM7B3607R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 676 | 3/4 | 3/8 | 4
SM7B3610R | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 677 | 3/4 | 3/8 | 4
SM7B3700R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 678 | 3/4 | 3/8 | 4
SM7B3705R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 679 | 3/4 | 3/8 | 4
SM7B3707R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 680 | 3/4 | 3/8 | 4
SM7B3710R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 681 | 3/4 | 3/8 | 4
SM7C1800R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 686 | 3/4 | 3/8 | 4
SM7C1805R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 687 | 3/4 | 3/8 | 4
SM7C1807R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 688 | 3/4 | 3/8 | 4
SM7C1810R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 689 | 3/4 | 3/8 | 4
SM7C1900R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 690 | 3/4 | 3/8 | 4
SM7C1905R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 691 | 3/4 | 3/8 | 4
SM7C1907R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 692 | 3/4 | 3/8 | 4
SM7C1910R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 693 | 3/4 | 3/8 | 4
SM7C2400R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 694 | 3/4 | 3/8 | 4
SM7C2405R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 695 | 3/4 | 3/8 | 4
SM7C2407R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 696 | 3/4 | 3/8 | 4
SM7C2410R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 697 | 3/4 | 3/8 | 4
SM7C2500R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 698 | 3/4 | 3/8 | 4
SM7C2505R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 699 | 3/4 | 3/8 | 4
SM7C2507R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 700 | 3/4 | 3/8 | 4
SM7C2510R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 701 | 3/4 | 3/8 | 4
SM7C3000R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 702 | 3/4 | 3/8 | 4
SM7C3005R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 703 | 3/4 | 3/8 | 4
SM7C3007R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 704 | 3/4 | 3/8 | 4
SM7C3010R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 705 | 3/4 | 3/8 | 4
SM7C3100R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 706 | 3/4 | 3/8 | 4
SM7C3105R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 707 | 3/4 | 3/8 | 4
SM7C3107R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 708 | 3/4 | 3/8 | 4
SM7C3110R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 709 | 3/4 | 3/8 | 4
SM7C3600R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 710 | 3/4 | 3/8 | 4
SM7C3605R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 711 | 3/4 | 3/8 | 4
SM7C3607R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 712 | 3/4 | 3/8 | 4
SM7C3610R | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 713 | 3/4 | 3/8 | 4
SM7C3700R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 714 | 3/4 | 3/8 | 4
SM7C3705R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 715 | 3/4 | 3/8 | 4
SM7C3707R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 716 | 3/4 | 3/8 | 4
SM7C3710R | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 717 | 3/4 | 3/8 | 4
SK111800R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 866 | 3/4 | 3/8 | 4
SK111805R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 867 | 3/4 | 3/8 | 4
SK111807R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 868 | 3/4 | 3/8 | 4
SK111810R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 869 | 3/4 | 3/8 | 4
SK111900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 870 | 3/4 | 3/8 | 4
SK111905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 871 | 3/4 | 3/8 | 4
SK111907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 872 | 3/4 | 3/8 | 4
SK111910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 873 | 3/4 | 3/8 | 4
SK112400R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 874 | 3/4 | 3/8 | 4
SK112405R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 875 | 3/4 | 3/8 | 4
SK112407R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 876 | 3/4 | 3/8 | 4
SK112410R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 877 | 3/4 | 3/8 | 4
SK112500R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 878 | 3/4 | 3/8 | 4
SK112505R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 879 | 3/4 | 3/8 | 4
SK112507R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 880 | 3/4 | 3/8 | 4
SK112510R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 881 | 3/4 | 3/8 | 4
SK113000R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 882 | 3/4 | 3/8 | 4
SK113005R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 883 | 3/4 | 3/8 | 4
SK113007R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 884 | 3/4 | 3/8 | 4
SK113010R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 885 | 3/4 | 3/8 | 4
SK113100R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 886 | 3/4 | 3/8 | 4
SK113105R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 887 | 3/4 | 3/8 | 4
SK113107R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 888 | 3/4 | 3/8 | 4
SK113110R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 889 | 3/4 | 3/8 | 4
SK113600R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 890 | 3/4 | 3/8 | 4
SK113605R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 891 | 3/4 | 3/8 | 4
SK113607R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 892 | 3/4 | 3/8 | 4
SK113610R | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 893 | 3/4 | 3/8 | 4
SK113700R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 894 | 3/4 | 3/8 | 4
SK113705R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 895 | 3/4 | 3/8 | 4
SK113707R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 896 | 3/4 | 3/8 | 4
SK113710R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 897 | 3/4 | 3/8 | 4
SK113900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 898 | 3/4 | 3/8 | 4
SK113905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 899 | 3/4 | 3/8 | 4
SK113907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 900 | 3/4 | 3/8 | 4
SK113910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 901 | 3/4 | 3/8 | 4
SK1A1800R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 902 | 3/4 | 3/8 | 4
SK1A1805R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 903 | 3/4 | 3/8 | 4
SK1A1807R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 904 | 3/4 | 3/8 | 4
SK1A1810R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 905 | 3/4 | 3/8 | 4
SK1A1900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 906 | 3/4 | 3/8 | 4
SK1A1905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 907 | 3/4 | 3/8 | 4
SK1A1907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 908 | 3/4 | 3/8 | 4
SK1A1910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 909 | 3/4 | 3/8 | 4
SK1A2400R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 910 | 3/4 | 3/8 | 4
SK1A2405R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 911 | 3/4 | 3/8 | 4
SK1A2407R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 912 | 3/4 | 3/8 | 4
SK1A2410R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 913 | 3/4 | 3/8 | 4
SK1A2500R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 914 | 3/4 | 3/8 | 4
SK1A2505R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 915 | 3/4 | 3/8 | 4
SK1A2507R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 916 | 3/4 | 3/8 | 4
SK1A2510R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 917 | 3/4 | 3/8 | 4
SK1A3000R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 918 | 3/4 | 3/8 | 4
SK1A3005R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 919 | 3/4 | 3/8 | 4
SK1A3007R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 920 | 3/4 | 3/8 | 4
SK1A3010R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 921 | 3/4 | 3/8 | 4
SK1A3100R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 922 | 3/4 | 3/8 | 4
SK1A3105R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 923 | 3/4 | 3/8 | 4
SK1A3107R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 924 | 3/4 | 3/8 | 4
SK1A3110R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 925 | 3/4 | 3/8 | 4
SK1A3600R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 926 | 3/4 | 3/8 | 4
SK1A3605R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 927 | 3/4 | 3/8 | 4
SK1A3607R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 928 | 3/4 | 3/8 | 4
SK1A3610R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 929 | 3/4 | 3/8 | 4
SK1A3700R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 930 | 3/4 | 3/8 | 4
SK1A3705R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 931 | 3/4 | 3/8 | 4
SK1A3707R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 932 | 3/4 | 3/8 | 4
SK1A3710R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 933 | 3/4 | 3/8 | 4
SK1A3900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 934 | 3/4 | 3/8 | 4
SK1A3905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 935 | 3/4 | 3/8 | 4
SK1A3907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 936 | 3/4 | 3/8 | 4
SK1A3910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 937 | 3/4 | 3/8 | 4
SK1B1800R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 938 | 3/4 | 3/8 | 4
SK1B1805R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 939 | 3/4 | 3/8 | 4
SK1B1807R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 940 | 3/4 | 3/8 | 4
SK1B1810R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 941 | 3/4 | 3/8 | 4
SK1B1900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 942 | 3/4 | 3/8 | 4
SK1B1905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 943 | 3/4 | 3/8 | 4
SK1B1907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 944 | 3/4 | 3/8 | 4
SK1B1910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 945 | 3/4 | 3/8 | 4
SK1B2400R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 946 | 3/4 | 3/8 | 4
SK1B2405R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 947 | 3/4 | 3/8 | 4
SK1B2407R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 948 | 3/4 | 3/8 | 4
SK1B2410R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 949 | 3/4 | 3/8 | 4
SK1B2500R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 950 | 3/4 | 3/8 | 4
SK1B2505R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 951 | 3/4 | 3/8 | 4
SK1B2507R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 952 | 3/4 | 3/8 | 4
SK1B2510R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 953 | 3/4 | 3/8 | 4
SK1B3000R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 954 | 3/4 | 3/8 | 4
SK1B3005R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 955 | 3/4 | 3/8 | 4
SK1B3007R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 956 | 3/4 | 3/8 | 4
SK1B3010R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 957 | 3/4 | 3/8 | 4
SK1B3100R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 958 | 3/4 | 3/8 | 4
SK1B3105R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 959 | 3/4 | 3/8 | 4
SK1B3107R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 960 | 3/4 | 3/8 | 4
SK1B3110R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 961 | 3/4 | 3/8 | 4
SK1B3600R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 962 | 3/4 | 3/8 | 4
SK1B3605R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 963 | 3/4 | 3/8 | 4
SK1B3607R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 964 | 3/4 | 3/8 | 4
SK1B3610R | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 965 | 3/4 | 3/8 | 4
SK1B3700R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 966 | 3/4 | 3/8 | 4
SK1B3705R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 967 | 3/4 | 3/8 | 4
SK1B3707R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 968 | 3/4 | 3/8 | 4
SK1B3710R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 969 | 3/4 | 3/8 | 4
SK1B3900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 970 | 3/4 | 3/8 | 4
SK1B3905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 971 | 3/4 | 3/8 | 4
SK1B3907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 972 | 3/4 | 3/8 | 4
SK1B3910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 973 | 3/4 | 3/8 | 4
SK1C1800R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 974 | 3/4 | 3/8 | 4
SK1C1805R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 975 | 3/4 | 3/8 | 4
SK1C1807R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 976 | 3/4 | 3/8 | 4
SK1C1810R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 977 | 3/4 | 3/8 | 4
SK1C1900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 978 | 3/4 | 3/8 | 4
SK1C1905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 979 | 3/4 | 3/8 | 4
SK1C1907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 980 | 3/4 | 3/8 | 4
SK1C1910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 981 | 3/4 | 3/8 | 4
SK1C2400R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 982 | 3/4 | 3/8 | 4
SK1C2405R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 983 | 3/4 | 3/8 | 4
SK1C2407R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 984 | 3/4 | 3/8 | 4
SK1C2410R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 985 | 3/4 | 3/8 | 4
SK1C2500R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 986 | 3/4 | 3/8 | 4
SK1C2505R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 987 | 3/4 | 3/8 | 4
SK1C2507R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 988 | 3/4 | 3/8 | 4
SK1C2510R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 989 | 3/4 | 3/8 | 4
SK1C3000R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 990 | 3/4 | 3/8 | 4
SK1C3005R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 991 | 3/4 | 3/8 | 4
SK1C3007R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 992 | 3/4 | 3/8 | 4
SK1C3010R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 993 | 3/4 | 3/8 | 4
SK1C3100R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 994 | 3/4 | 3/8 | 4
SK1C3105R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 995 | 3/4 | 3/8 | 4
SK1C3107R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 996 | 3/4 | 3/8 | 4
SK1C3110R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 997 | 3/4 | 3/8 | 4
SK1C3600R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 998 | 3/4 | 3/8 | 4
SK1C3605R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 999 | 3/4 | 3/8 | 4
SK1C3607R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1000 | 3/4 | 3/8 | 4
SK1C3610R | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1001 | 3/4 | 3/8 | 4
SK1C3700R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1002 | 3/4 | 3/8 | 4
SK1C3705R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1003 | 3/4 | 3/8 | 4
SK1C3707R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1004 | 3/4 | 3/8 | 4
SK1C3710R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1005 | 3/4 | 3/8 | 4
SK1C3900R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1006 | 3/4 | 3/8 | 4
SK1C3905R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1007 | 3/4 | 3/8 | 4
SK1C3907R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1008 | 3/4 | 3/8 | 4
SK1C3910R | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1009 | 3/4 | 3/8 | 4
SK211800R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1010 | 3/4 | 3/8 | 4
SK211805R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1011 | 3/4 | 3/8 | 4
SK211807R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1012 | 3/4 | 3/8 | 4
SK211810R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1013 | 3/4 | 3/8 | 4
SK211900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1014 | 3/4 | 3/8 | 4
SK211905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1015 | 3/4 | 3/8 | 4
SK211907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1016 | 3/4 | 3/8 | 4
SK211910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1017 | 3/4 | 3/8 | 4
SK212400R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1018 | 3/4 | 3/8 | 4
SK212405R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1019 | 3/4 | 3/8 | 4
SK212407R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1020 | 3/4 | 3/8 | 4
SK212410R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1021 | 3/4 | 3/8 | 4
SK212500R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1022 | 3/4 | 3/8 | 4
SK212505R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1023 | 3/4 | 3/8 | 4
SK212507R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1024 | 3/4 | 3/8 | 4
SK212510R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1025 | 3/4 | 3/8 | 4
SK213000R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1026 | 3/4 | 3/8 | 4
SK213005R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1027 | 3/4 | 3/8 | 4
SK213007R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1028 | 3/4 | 3/8 | 4
SK213010R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1029 | 3/4 | 3/8 | 4
SK213100R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1030 | 3/4 | 3/8 | 4
SK213105R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1031 | 3/4 | 3/8 | 4
SK213107R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1032 | 3/4 | 3/8 | 4
SK213110R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1033 | 3/4 | 3/8 | 4
SK213600R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1034 | 3/4 | 3/8 | 4
SK213605R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1035 | 3/4 | 3/8 | 4
SK213607R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1036 | 3/4 | 3/8 | 4
SK213610R | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1037 | 3/4 | 3/8 | 4
SK213700R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1038 | 3/4 | 3/8 | 4
SK213705R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1039 | 3/4 | 3/8 | 4
SK213707R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1040 | 3/4 | 3/8 | 4
SK213710R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1041 | 3/4 | 3/8 | 4
SK213900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1042 | 3/4 | 3/8 | 4
SK213905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1043 | 3/4 | 3/8 | 4
SK213907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1044 | 3/4 | 3/8 | 4
SK213910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1045 | 3/4 | 3/8 | 4
SK2A1800R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1046 | 3/4 | 3/8 | 4
SK2A1805R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1047 | 3/4 | 3/8 | 4
SK2A1807R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1048 | 3/4 | 3/8 | 4
SK2A1810R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1049 | 3/4 | 3/8 | 4
SK2A1900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1050 | 3/4 | 3/8 | 4
SK2A1905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1051 | 3/4 | 3/8 | 4
SK2A1907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1052 | 3/4 | 3/8 | 4
SK2A1910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1053 | 3/4 | 3/8 | 4
SK2A2400R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1054 | 3/4 | 3/8 | 4
SK2A2405R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1055 | 3/4 | 3/8 | 4
SK2A2407R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1056 | 3/4 | 3/8 | 4
SK2A2410R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1057 | 3/4 | 3/8 | 4
SK2A2500R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1058 | 3/4 | 3/8 | 4
SK2A2505R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1059 | 3/4 | 3/8 | 4
SK2A2507R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1060 | 3/4 | 3/8 | 4
SK2A2510R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1061 | 3/4 | 3/8 | 4
SK2A3000R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1062 | 3/4 | 3/8 | 4
SK2A3005R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1063 | 3/4 | 3/8 | 4
SK2A3007R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1064 | 3/4 | 3/8 | 4
SK2A3010R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1065 | 3/4 | 3/8 | 4
SK2A3100R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1066 | 3/4 | 3/8 | 4
SK2A3105R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1067 | 3/4 | 3/8 | 4
SK2A3107R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1068 | 3/4 | 3/8 | 4
SK2A3110R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1069 | 3/4 | 3/8 | 4
SK2A3600R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1070 | 3/4 | 3/8 | 4
SK2A3605R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1071 | 3/4 | 3/8 | 4
SK2A3607R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1072 | 3/4 | 3/8 | 4
SK2A3610R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1073 | 3/4 | 3/8 | 4
SK2A3700R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1074 | 3/4 | 3/8 | 4
SK2A3705R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1075 | 3/4 | 3/8 | 4
SK2A3707R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1076 | 3/4 | 3/8 | 4
SK2A3710R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1077 | 3/4 | 3/8 | 4
SK2A3900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1078 | 3/4 | 3/8 | 4
SK2A3905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1079 | 3/4 | 3/8 | 4
SK2A3907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1080 | 3/4 | 3/8 | 4
SK2A3910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1081 | 3/4 | 3/8 | 4
SK2B1800R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1082 | 3/4 | 3/8 | 4
SK2B1805R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1083 | 3/4 | 3/8 | 4
SK2B1807R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1084 | 3/4 | 3/8 | 4
SK2B1810R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1085 | 3/4 | 3/8 | 4
SK2B1900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1086 | 3/4 | 3/8 | 4
SK2B1905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1087 | 3/4 | 3/8 | 4
SK2B1907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1088 | 3/4 | 3/8 | 4
SK2B1910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1089 | 3/4 | 3/8 | 4
SK2B2400R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1090 | 3/4 | 3/8 | 4
SK2B2405R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1091 | 3/4 | 3/8 | 4
SK2B2407R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1092 | 3/4 | 3/8 | 4
SK2B2410R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1093 | 3/4 | 3/8 | 4
SK2B2500R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1094 | 3/4 | 3/8 | 4
SK2B2505R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1095 | 3/4 | 3/8 | 4
SK2B2507R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1096 | 3/4 | 3/8 | 4
SK2B2510R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1097 | 3/4 | 3/8 | 4
SK2B3000R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1098 | 3/4 | 3/8 | 4
SK2B3005R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1099 | 3/4 | 3/8 | 4
SK2B3007R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1100 | 3/4 | 3/8 | 4
SK2B3010R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1101 | 3/4 | 3/8 | 4
SK2B3100R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1102 | 3/4 | 3/8 | 4
SK2B3105R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1103 | 3/4 | 3/8 | 4
SK2B3107R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1104 | 3/4 | 3/8 | 4
SK2B3110R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1105 | 3/4 | 3/8 | 4
SK2B3600R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1106 | 3/4 | 3/8 | 4
SK2B3605R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1107 | 3/4 | 3/8 | 4
SK2B3607R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1108 | 3/4 | 3/8 | 4
SK2B3610R | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1109 | 3/4 | 3/8 | 4
SK2B3700R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1110 | 3/4 | 3/8 | 4
SK2B3705R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1111 | 3/4 | 3/8 | 4
SK2B3707R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1112 | 3/4 | 3/8 | 4
SK2B3710R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1113 | 3/4 | 3/8 | 4
SK2B3900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1114 | 3/4 | 3/8 | 4
SK2B3905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1115 | 3/4 | 3/8 | 4
SK2B3907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1116 | 3/4 | 3/8 | 4
SK2B3910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1117 | 3/4 | 3/8 | 4
SK2C1800R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1118 | 3/4 | 3/8 | 4
SK2C1805R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1119 | 3/4 | 3/8 | 4
SK2C1807R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1120 | 3/4 | 3/8 | 4
SK2C1810R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1121 | 3/4 | 3/8 | 4
SK2C1900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1122 | 3/4 | 3/8 | 4
SK2C1905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1123 | 3/4 | 3/8 | 4
SK2C1907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1124 | 3/4 | 3/8 | 4
SK2C1910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1125 | 3/4 | 3/8 | 4
SK2C2400R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1126 | 3/4 | 3/8 | 4
SK2C2405R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1127 | 3/4 | 3/8 | 4
SK2C2407R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1128 | 3/4 | 3/8 | 4
SK2C2410R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1129 | 3/4 | 3/8 | 4
SK2C2500R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1130 | 3/4 | 3/8 | 4
SK2C2505R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1131 | 3/4 | 3/8 | 4
SK2C2507R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1132 | 3/4 | 3/8 | 4
SK2C2510R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1133 | 3/4 | 3/8 | 4
SK2C3000R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1134 | 3/4 | 3/8 | 4
SK2C3005R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1135 | 3/4 | 3/8 | 4
SK2C3007R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1136 | 3/4 | 3/8 | 4
SK2C3010R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1137 | 3/4 | 3/8 | 4
SK2C3100R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1138 | 3/4 | 3/8 | 4
SK2C3105R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1139 | 3/4 | 3/8 | 4
SK2C3107R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1140 | 3/4 | 3/8 | 4
SK2C3110R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1141 | 3/4 | 3/8 | 4
SK2C3600R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1142 | 3/4 | 3/8 | 4
SK2C3605R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1143 | 3/4 | 3/8 | 4
SK2C3607R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1144 | 3/4 | 3/8 | 4
SK2C3610R | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1145 | 3/4 | 3/8 | 4
SK2C3700R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1146 | 3/4 | 3/8 | 4
SK2C3705R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1147 | 3/4 | 3/8 | 4
SK2C3707R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1148 | 3/4 | 3/8 | 4
SK2C3710R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1149 | 3/4 | 3/8 | 4
SK2C3900R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1150 | 3/4 | 3/8 | 4
SK2C3905R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1151 | 3/4 | 3/8 | 4
SK2C3907R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1152 | 3/4 | 3/8 | 4
SK2C3910R | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1153 | 3/4 | 3/8 | 4
SK311800R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1154 | 3/4 | 3/8 | 4
SK311805R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1155 | 3/4 | 3/8 | 4
SK311807R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1156 | 3/4 | 3/8 | 4
SK311810R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1157 | 3/4 | 3/8 | 4
SK311900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1158 | 3/4 | 3/8 | 4
SK311905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1159 | 3/4 | 3/8 | 4
SK311907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1160 | 3/4 | 3/8 | 4
SK311910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1161 | 3/4 | 3/8 | 4
SK312400R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1162 | 3/4 | 3/8 | 4
SK312405R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1163 | 3/4 | 3/8 | 4
SK312407R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1164 | 3/4 | 3/8 | 4
SK312410R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1165 | 3/4 | 3/8 | 4
SK312500R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1166 | 3/4 | 3/8 | 4
SK312505R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1167 | 3/4 | 3/8 | 4
SK312507R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1168 | 3/4 | 3/8 | 4
SK312510R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1169 | 3/4 | 3/8 | 4
SK313000R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1170 | 3/4 | 3/8 | 4
SK313005R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1171 | 3/4 | 3/8 | 4
SK313007R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1172 | 3/4 | 3/8 | 4
SK313010R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1173 | 3/4 | 3/8 | 4
SK313100R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1174 | 3/4 | 3/8 | 4
SK313105R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1175 | 3/4 | 3/8 | 4
SK313107R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1176 | 3/4 | 3/8 | 4
SK313110R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1177 | 3/4 | 3/8 | 4
SK313600R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1178 | 3/4 | 3/8 | 4
SK313605R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1179 | 3/4 | 3/8 | 4
SK313607R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1180 | 3/4 | 3/8 | 4
SK313610R | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1181 | 3/4 | 3/8 | 4
SK313700R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1182 | 3/4 | 3/8 | 4
SK313705R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1183 | 3/4 | 3/8 | 4
SK313707R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1184 | 3/4 | 3/8 | 4
SK313710R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1185 | 3/4 | 3/8 | 4
SK313900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1186 | 3/4 | 3/8 | 4
SK313905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1187 | 3/4 | 3/8 | 4
SK313907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1188 | 3/4 | 3/8 | 4
SK313910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1189 | 3/4 | 3/8 | 4
SK3A1800R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1190 | 3/4 | 3/8 | 4
SK3A1805R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1191 | 3/4 | 3/8 | 4
SK3A1807R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1192 | 3/4 | 3/8 | 4
SK3A1810R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1193 | 3/4 | 3/8 | 4
SK3A1900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1194 | 3/4 | 3/8 | 4
SK3A1905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1195 | 3/4 | 3/8 | 4
SK3A1907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1196 | 3/4 | 3/8 | 4
SK3A1910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1197 | 3/4 | 3/8 | 4
SK3A2400R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1198 | 3/4 | 3/8 | 4
SK3A2405R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1199 | 3/4 | 3/8 | 4
SK3A2407R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1200 | 3/4 | 3/8 | 4
SK3A2410R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1201 | 3/4 | 3/8 | 4
SK3A2500R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1202 | 3/4 | 3/8 | 4
SK3A2505R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1203 | 3/4 | 3/8 | 4
SK3A2507R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1204 | 3/4 | 3/8 | 4
SK3A2510R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1205 | 3/4 | 3/8 | 4
SK3A3000R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1206 | 3/4 | 3/8 | 4
SK3A3005R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1207 | 3/4 | 3/8 | 4
SK3A3007R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1208 | 3/4 | 3/8 | 4
SK3A3010R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1209 | 3/4 | 3/8 | 4
SK3A3100R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1210 | 3/4 | 3/8 | 4
SK3A3105R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1211 | 3/4 | 3/8 | 4
SK3A3107R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1212 | 3/4 | 3/8 | 4
SK3A3110R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1213 | 3/4 | 3/8 | 4
SK3A3600R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1214 | 3/4 | 3/8 | 4
SK3A3605R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1215 | 3/4 | 3/8 | 4
SK3A3607R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1216 | 3/4 | 3/8 | 4
SK3A3610R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1217 | 3/4 | 3/8 | 4
SK3A3700R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1218 | 3/4 | 3/8 | 4
SK3A3705R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1219 | 3/4 | 3/8 | 4
SK3A3707R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1220 | 3/4 | 3/8 | 4
SK3A3710R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1221 | 3/4 | 3/8 | 4
SK3A3900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1222 | 3/4 | 3/8 | 4
SK3A3905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1223 | 3/4 | 3/8 | 4
SK3A3907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1224 | 3/4 | 3/8 | 4
SK3A3910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1225 | 3/4 | 3/8 | 4
SK3B1800R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1226 | 3/4 | 3/8 | 4
SK3B1805R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1227 | 3/4 | 3/8 | 4
SK3B1807R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1228 | 3/4 | 3/8 | 4
SK3B1810R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1229 | 3/4 | 3/8 | 4
SK3B1900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1230 | 3/4 | 3/8 | 4
SK3B1905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1231 | 3/4 | 3/8 | 4
SK3B1907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1232 | 3/4 | 3/8 | 4
SK3B1910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1233 | 3/4 | 3/8 | 4
SK3B2400R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1234 | 3/4 | 3/8 | 4
SK3B2405R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1235 | 3/4 | 3/8 | 4
SK3B2407R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1236 | 3/4 | 3/8 | 4
SK3B2410R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1237 | 3/4 | 3/8 | 4
SK3B2500R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1238 | 3/4 | 3/8 | 4
SK3B2505R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1239 | 3/4 | 3/8 | 4
SK3B2507R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1240 | 3/4 | 3/8 | 4
SK3B2510R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1241 | 3/4 | 3/8 | 4
SK3B3000R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1242 | 3/4 | 3/8 | 4
SK3B3005R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1243 | 3/4 | 3/8 | 4
SK3B3007R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1244 | 3/4 | 3/8 | 4
SK3B3010R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1245 | 3/4 | 3/8 | 4
SK3B3100R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1246 | 3/4 | 3/8 | 4
SK3B3105R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1247 | 3/4 | 3/8 | 4
SK3B3107R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1248 | 3/4 | 3/8 | 4
SK3B3110R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1249 | 3/4 | 3/8 | 4
SK3B3600R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1250 | 3/4 | 3/8 | 4
SK3B3605R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1251 | 3/4 | 3/8 | 4
SK3B3607R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1252 | 3/4 | 3/8 | 4
SK3B3610R | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1253 | 3/4 | 3/8 | 4
SK3B3700R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1254 | 3/4 | 3/8 | 4
SK3B3705R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1255 | 3/4 | 3/8 | 4
SK3B3707R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1256 | 3/4 | 3/8 | 4
SK3B3710R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1257 | 3/4 | 3/8 | 4
SK3B3900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1258 | 3/4 | 3/8 | 4
SK3B3905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1259 | 3/4 | 3/8 | 4
SK3B3907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1260 | 3/4 | 3/8 | 4
SK3B3910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1261 | 3/4 | 3/8 | 4
SK3C1800R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1262 | 3/4 | 3/8 | 4
SK3C1805R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1263 | 3/4 | 3/8 | 4
SK3C1807R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1264 | 3/4 | 3/8 | 4
SK3C1810R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1265 | 3/4 | 3/8 | 4
SK3C1900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1266 | 3/4 | 3/8 | 4
SK3C1905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1267 | 3/4 | 3/8 | 4
SK3C1907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1268 | 3/4 | 3/8 | 4
SK3C1910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1269 | 3/4 | 3/8 | 4
SK3C2400R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1270 | 3/4 | 3/8 | 4
SK3C2405R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1271 | 3/4 | 3/8 | 4
SK3C2407R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1272 | 3/4 | 3/8 | 4
SK3C2410R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1273 | 3/4 | 3/8 | 4
SK3C2500R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1274 | 3/4 | 3/8 | 4
SK3C2505R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1275 | 3/4 | 3/8 | 4
SK3C2507R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1276 | 3/4 | 3/8 | 4
SK3C2510R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1277 | 3/4 | 3/8 | 4
SK3C3000R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1278 | 3/4 | 3/8 | 4
SK3C3005R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1279 | 3/4 | 3/8 | 4
SK3C3007R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1280 | 3/4 | 3/8 | 4
SK3C3010R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1281 | 3/4 | 3/8 | 4
SK3C3100R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1282 | 3/4 | 3/8 | 4
SK3C3105R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1283 | 3/4 | 3/8 | 4
SK3C3107R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1284 | 3/4 | 3/8 | 4
SK3C3110R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1285 | 3/4 | 3/8 | 4
SK3C3600R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1286 | 3/4 | 3/8 | 4
SK3C3605R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1287 | 3/4 | 3/8 | 4
SK3C3607R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1288 | 3/4 | 3/8 | 4
SK3C3610R | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1289 | 3/4 | 3/8 | 4
SK3C3700R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1290 | 3/4 | 3/8 | 4
SK3C3705R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1291 | 3/4 | 3/8 | 4
SK3C3707R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1292 | 3/4 | 3/8 | 4
SK3C3710R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1293 | 3/4 | 3/8 | 4
SK3C3900R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1294 | 3/4 | 3/8 | 4
SK3C3905R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1295 | 3/4 | 3/8 | 4
SK3C3907R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1296 | 3/4 | 3/8 | 4
SK3C3910R | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1297 | 3/4 | 3/8 | 4
SK611800R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1442 | 3/4 | 3/8 | 4
SK611805R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1443 | 3/4 | 3/8 | 4
SK611807R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1444 | 3/4 | 3/8 | 4
SK611810R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1445 | 3/4 | 3/8 | 4
SK611900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1446 | 3/4 | 3/8 | 4
SK611905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1447 | 3/4 | 3/8 | 4
SK611907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1448 | 3/4 | 3/8 | 4
SK611910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1449 | 3/4 | 3/8 | 4
SK612400R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1450 | 3/4 | 3/8 | 4
SK612405R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1451 | 3/4 | 3/8 | 4
SK612407R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1452 | 3/4 | 3/8 | 4
SK612410R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1453 | 3/4 | 3/8 | 4
SK612500R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1454 | 3/4 | 3/8 | 4
SK612505R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1455 | 3/4 | 3/8 | 4
SK612507R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1456 | 3/4 | 3/8 | 4
SK612510R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1457 | 3/4 | 3/8 | 4
SK613000R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1458 | 3/4 | 3/8 | 4
SK613005R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1459 | 3/4 | 3/8 | 4
SK613007R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1460 | 3/4 | 3/8 | 4
SK613010R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1461 | 3/4 | 3/8 | 4
SK613100R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1462 | 3/4 | 3/8 | 4
SK613105R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1463 | 3/4 | 3/8 | 4
SK613107R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1464 | 3/4 | 3/8 | 4
SK613110R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1465 | 3/4 | 3/8 | 4
SK613600R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1466 | 3/4 | 3/8 | 4
SK613605R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1467 | 3/4 | 3/8 | 4
SK613607R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1468 | 3/4 | 3/8 | 4
SK613610R | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1469 | 3/4 | 3/8 | 4
SK613700R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1470 | 3/4 | 3/8 | 4
SK613705R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1471 | 3/4 | 3/8 | 4
SK613707R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1472 | 3/4 | 3/8 | 4
SK613710R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1473 | 3/4 | 3/8 | 4
SK613900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1474 | 3/4 | 3/8 | 4
SK613905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1475 | 3/4 | 3/8 | 4
SK613907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1476 | 3/4 | 3/8 | 4
SK613910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1477 | 3/4 | 3/8 | 4
SK6A1800R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1478 | 3/4 | 3/8 | 4
SK6A1805R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1479 | 3/4 | 3/8 | 4
SK6A1807R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1480 | 3/4 | 3/8 | 4
SK6A1810R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1481 | 3/4 | 3/8 | 4
SK6A1900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1482 | 3/4 | 3/8 | 4
SK6A1905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1483 | 3/4 | 3/8 | 4
SK6A1907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1484 | 3/4 | 3/8 | 4
SK6A1910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1485 | 3/4 | 3/8 | 4
SK6A2400R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1486 | 3/4 | 3/8 | 4
SK6A2405R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1487 | 3/4 | 3/8 | 4
SK6A2407R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1488 | 3/4 | 3/8 | 4
SK6A2410R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1489 | 3/4 | 3/8 | 4
SK6A2500R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1490 | 3/4 | 3/8 | 4
SK6A2505R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1491 | 3/4 | 3/8 | 4
SK6A2507R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1492 | 3/4 | 3/8 | 4
SK6A2510R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1493 | 3/4 | 3/8 | 4
SK6A3000R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1494 | 3/4 | 3/8 | 4
SK6A3005R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1495 | 3/4 | 3/8 | 4
SK6A3007R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1496 | 3/4 | 3/8 | 4
SK6A3010R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1497 | 3/4 | 3/8 | 4
SK6A3100R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1498 | 3/4 | 3/8 | 4
SK6A3105R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1499 | 3/4 | 3/8 | 4
SK6A3107R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1500 | 3/4 | 3/8 | 4
SK6A3110R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1501 | 3/4 | 3/8 | 4
SK6A3600R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1502 | 3/4 | 3/8 | 4
SK6A3605R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1503 | 3/4 | 3/8 | 4
SK6A3607R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1504 | 3/4 | 3/8 | 4
SK6A3610R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1505 | 3/4 | 3/8 | 4
SK6A3700R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1506 | 3/4 | 3/8 | 4
SK6A3705R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1507 | 3/4 | 3/8 | 4
SK6A3707R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1508 | 3/4 | 3/8 | 4
SK6A3710R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1509 | 3/4 | 3/8 | 4
SK6A3900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1510 | 3/4 | 3/8 | 4
SK6A3905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1511 | 3/4 | 3/8 | 4
SK6A3907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1512 | 3/4 | 3/8 | 4
SK6A3910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1513 | 3/4 | 3/8 | 4
SK6B1800R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1514 | 3/4 | 3/8 | 4
SK6B1805R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1515 | 3/4 | 3/8 | 4
SK6B1807R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1516 | 3/4 | 3/8 | 4
SK6B1810R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1517 | 3/4 | 3/8 | 4
SK6B1900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1518 | 3/4 | 3/8 | 4
SK6B1905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1519 | 3/4 | 3/8 | 4
SK6B1907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1520 | 3/4 | 3/8 | 4
SK6B1910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1521 | 3/4 | 3/8 | 4
SK6B2400R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1522 | 3/4 | 3/8 | 4
SK6B2405R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1523 | 3/4 | 3/8 | 4
SK6B2407R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1524 | 3/4 | 3/8 | 4
SK6B2410R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1525 | 3/4 | 3/8 | 4
SK6B2500R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1526 | 3/4 | 3/8 | 4
SK6B2505R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1527 | 3/4 | 3/8 | 4
SK6B2507R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1528 | 3/4 | 3/8 | 4
SK6B2510R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1529 | 3/4 | 3/8 | 4
SK6B3000R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1530 | 3/4 | 3/8 | 4
SK6B3005R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1531 | 3/4 | 3/8 | 4
SK6B3007R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1532 | 3/4 | 3/8 | 4
SK6B3010R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1533 | 3/4 | 3/8 | 4
SK6B3100R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1534 | 3/4 | 3/8 | 4
SK6B3105R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1535 | 3/4 | 3/8 | 4
SK6B3107R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1536 | 3/4 | 3/8 | 4
SK6B3110R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1537 | 3/4 | 3/8 | 4
SK6B3600R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1538 | 3/4 | 3/8 | 4
SK6B3605R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1539 | 3/4 | 3/8 | 4
SK6B3607R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1540 | 3/4 | 3/8 | 4
SK6B3610R | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1541 | 3/4 | 3/8 | 4
SK6B3700R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1542 | 3/4 | 3/8 | 4
SK6B3705R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1543 | 3/4 | 3/8 | 4
SK6B3707R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1544 | 3/4 | 3/8 | 4
SK6B3710R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1545 | 3/4 | 3/8 | 4
SK6B3900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1546 | 3/4 | 3/8 | 4
SK6B3905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1547 | 3/4 | 3/8 | 4
SK6B3907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1548 | 3/4 | 3/8 | 4
SK6B3910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1549 | 3/4 | 3/8 | 4
SK6C1800R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1550 | 3/4 | 3/8 | 4
SK6C1805R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1551 | 3/4 | 3/8 | 4
SK6C1807R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1552 | 3/4 | 3/8 | 4
SK6C1810R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1553 | 3/4 | 3/8 | 4
SK6C1900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1554 | 3/4 | 3/8 | 4
SK6C1905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1555 | 3/4 | 3/8 | 4
SK6C1907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1556 | 3/4 | 3/8 | 4
SK6C1910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1557 | 3/4 | 3/8 | 4
SK6C2400R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1558 | 3/4 | 3/8 | 4
SK6C2405R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1559 | 3/4 | 3/8 | 4
SK6C2407R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1560 | 3/4 | 3/8 | 4
SK6C2410R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1561 | 3/4 | 3/8 | 4
SK6C2500R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1562 | 3/4 | 3/8 | 4
SK6C2505R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1563 | 3/4 | 3/8 | 4
SK6C2507R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1564 | 3/4 | 3/8 | 4
SK6C2510R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1565 | 3/4 | 3/8 | 4
SK6C3000R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1566 | 3/4 | 3/8 | 4
SK6C3005R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1567 | 3/4 | 3/8 | 4
SK6C3007R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1568 | 3/4 | 3/8 | 4
SK6C3010R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1569 | 3/4 | 3/8 | 4
SK6C3100R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1570 | 3/4 | 3/8 | 4
SK6C3105R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1571 | 3/4 | 3/8 | 4
SK6C3107R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1572 | 3/4 | 3/8 | 4
SK6C3110R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1573 | 3/4 | 3/8 | 4
SK6C3600R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1574 | 3/4 | 3/8 | 4
SK6C3605R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1575 | 3/4 | 3/8 | 4
SK6C3607R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1576 | 3/4 | 3/8 | 4
SK6C3610R | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1577 | 3/4 | 3/8 | 4
SK6C3700R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1578 | 3/4 | 3/8 | 4
SK6C3705R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1579 | 3/4 | 3/8 | 4
SK6C3707R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1580 | 3/4 | 3/8 | 4
SK6C3710R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1581 | 3/4 | 3/8 | 4
SK6C3900R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1582 | 3/4 | 3/8 | 4
SK6C3905R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1583 | 3/4 | 3/8 | 4
SK6C3907R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1584 | 3/4 | 3/8 | 4
SK6C3910R | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1585 | 3/4 | 3/8 | 4
SK711800R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1586 | 3/4 | 3/8 | 4
SK711805R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1587 | 3/4 | 3/8 | 4
SK711807R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1588 | 3/4 | 3/8 | 4
SK711810R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1589 | 3/4 | 3/8 | 4
SK711900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1590 | 3/4 | 3/8 | 4
SK711905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1591 | 3/4 | 3/8 | 4
SK711907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1592 | 3/4 | 3/8 | 4
SK711910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1593 | 3/4 | 3/8 | 4
SK712400R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1594 | 3/4 | 3/8 | 4
SK712405R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1595 | 3/4 | 3/8 | 4
SK712407R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1596 | 3/4 | 3/8 | 4
SK712410R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1597 | 3/4 | 3/8 | 4
SK712500R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1598 | 3/4 | 3/8 | 4
SK712505R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1599 | 3/4 | 3/8 | 4
SK712507R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1600 | 3/4 | 3/8 | 4
SK712510R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1601 | 3/4 | 3/8 | 4
SK713000R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1602 | 3/4 | 3/8 | 4
SK713005R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1603 | 3/4 | 3/8 | 4
SK713007R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1604 | 3/4 | 3/8 | 4
SK713010R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1605 | 3/4 | 3/8 | 4
SK713100R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1606 | 3/4 | 3/8 | 4
SK713105R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1607 | 3/4 | 3/8 | 4
SK713107R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1608 | 3/4 | 3/8 | 4
SK713110R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1609 | 3/4 | 3/8 | 4
SK713600R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1610 | 3/4 | 3/8 | 4
SK713605R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1611 | 3/4 | 3/8 | 4
SK713607R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1612 | 3/4 | 3/8 | 4
SK713610R | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1613 | 3/4 | 3/8 | 4
SK713700R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1614 | 3/4 | 3/8 | 4
SK713705R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1615 | 3/4 | 3/8 | 4
SK713707R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1616 | 3/4 | 3/8 | 4
SK713710R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1617 | 3/4 | 3/8 | 4
SK713900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1618 | 3/4 | 3/8 | 4
SK713905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1619 | 3/4 | 3/8 | 4
SK713907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1620 | 3/4 | 3/8 | 4
SK713910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1621 | 3/4 | 3/8 | 4
SK7A1800R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1622 | 3/4 | 3/8 | 4
SK7A1805R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1623 | 3/4 | 3/8 | 4
SK7A1807R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1624 | 3/4 | 3/8 | 4
SK7A1810R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1625 | 3/4 | 3/8 | 4
SK7A1900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1626 | 3/4 | 3/8 | 4
SK7A1905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1627 | 3/4 | 3/8 | 4
SK7A1907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1628 | 3/4 | 3/8 | 4
SK7A1910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1629 | 3/4 | 3/8 | 4
SK7A2400R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1630 | 3/4 | 3/8 | 4
SK7A2405R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1631 | 3/4 | 3/8 | 4
SK7A2407R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1632 | 3/4 | 3/8 | 4
SK7A2410R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1633 | 3/4 | 3/8 | 4
SK7A2500R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1634 | 3/4 | 3/8 | 4
SK7A2505R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1635 | 3/4 | 3/8 | 4
SK7A2507R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1636 | 3/4 | 3/8 | 4
SK7A2510R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1637 | 3/4 | 3/8 | 4
SK7A3000R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1638 | 3/4 | 3/8 | 4
SK7A3005R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1639 | 3/4 | 3/8 | 4
SK7A3007R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1640 | 3/4 | 3/8 | 4
SK7A3010R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1641 | 3/4 | 3/8 | 4
SK7A3100R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1642 | 3/4 | 3/8 | 4
SK7A3105R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1643 | 3/4 | 3/8 | 4
SK7A3107R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1644 | 3/4 | 3/8 | 4
SK7A3110R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1645 | 3/4 | 3/8 | 4
SK7A3600R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1646 | 3/4 | 3/8 | 4
SK7A3605R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1647 | 3/4 | 3/8 | 4
SK7A3607R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1648 | 3/4 | 3/8 | 4
SK7A3610R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1649 | 3/4 | 3/8 | 4
SK7A3700R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1650 | 3/4 | 3/8 | 4
SK7A3705R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1651 | 3/4 | 3/8 | 4
SK7A3707R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1652 | 3/4 | 3/8 | 4
SK7A3710R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1653 | 3/4 | 3/8 | 4
SK7A3900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1654 | 3/4 | 3/8 | 4
SK7A3905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1655 | 3/4 | 3/8 | 4
SK7A3907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1656 | 3/4 | 3/8 | 4
SK7A3910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1657 | 3/4 | 3/8 | 4
SK7B1800R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1658 | 3/4 | 3/8 | 4
SK7B1805R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1659 | 3/4 | 3/8 | 4
SK7B1807R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1660 | 3/4 | 3/8 | 4
SK7B1810R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1661 | 3/4 | 3/8 | 4
SK7B1900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1662 | 3/4 | 3/8 | 4
SK7B1905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1663 | 3/4 | 3/8 | 4
SK7B1907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1664 | 3/4 | 3/8 | 4
SK7B1910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1665 | 3/4 | 3/8 | 4
SK7B2400R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1666 | 3/4 | 3/8 | 4
SK7B2405R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1667 | 3/4 | 3/8 | 4
SK7B2407R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1668 | 3/4 | 3/8 | 4
SK7B2410R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1669 | 3/4 | 3/8 | 4
SK7B2500R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1670 | 3/4 | 3/8 | 4
SK7B2505R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1671 | 3/4 | 3/8 | 4
SK7B2507R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1672 | 3/4 | 3/8 | 4
SK7B2510R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1673 | 3/4 | 3/8 | 4
SK7B3000R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1674 | 3/4 | 3/8 | 4
SK7B3005R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1675 | 3/4 | 3/8 | 4
SK7B3007R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1676 | 3/4 | 3/8 | 4
SK7B3010R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1677 | 3/4 | 3/8 | 4
SK7B3100R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1678 | 3/4 | 3/8 | 4
SK7B3105R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1679 | 3/4 | 3/8 | 4
SK7B3107R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1680 | 3/4 | 3/8 | 4
SK7B3110R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1681 | 3/4 | 3/8 | 4
SK7B3600R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1682 | 3/4 | 3/8 | 4
SK7B3605R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1683 | 3/4 | 3/8 | 4
SK7B3607R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1684 | 3/4 | 3/8 | 4
SK7B3610R | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1685 | 3/4 | 3/8 | 4
SK7B3700R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1686 | 3/4 | 3/8 | 4
SK7B3705R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1687 | 3/4 | 3/8 | 4
SK7B3707R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1688 | 3/4 | 3/8 | 4
SK7B3710R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1689 | 3/4 | 3/8 | 4
SK7B3900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1690 | 3/4 | 3/8 | 4
SK7B3905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1691 | 3/4 | 3/8 | 4
SK7B3907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1692 | 3/4 | 3/8 | 4
SK7B3910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1693 | 3/4 | 3/8 | 4
SK7C1800R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1694 | 3/4 | 3/8 | 4
SK7C1805R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1695 | 3/4 | 3/8 | 4
SK7C1807R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1696 | 3/4 | 3/8 | 4
SK7C1810R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1697 | 3/4 | 3/8 | 4
SK7C1900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1698 | 3/4 | 3/8 | 4
SK7C1905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1699 | 3/4 | 3/8 | 4
SK7C1907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1700 | 3/4 | 3/8 | 4
SK7C1910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1701 | 3/4 | 3/8 | 4
SK7C2400R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1702 | 3/4 | 3/8 | 4
SK7C2405R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1703 | 3/4 | 3/8 | 4
SK7C2407R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1704 | 3/4 | 3/8 | 4
SK7C2410R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1705 | 3/4 | 3/8 | 4
SK7C2500R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1706 | 3/4 | 3/8 | 4
SK7C2505R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1707 | 3/4 | 3/8 | 4
SK7C2507R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1708 | 3/4 | 3/8 | 4
SK7C2510R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1709 | 3/4 | 3/8 | 4
SK7C3000R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1710 | 3/4 | 3/8 | 4
SK7C3005R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1711 | 3/4 | 3/8 | 4
SK7C3007R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1712 | 3/4 | 3/8 | 4
SK7C3010R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1713 | 3/4 | 3/8 | 4
SK7C3100R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1714 | 3/4 | 3/8 | 4
SK7C3105R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1715 | 3/4 | 3/8 | 4
SK7C3107R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1716 | 3/4 | 3/8 | 4
SK7C3110R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1717 | 3/4 | 3/8 | 4
SK7C3600R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1718 | 3/4 | 3/8 | 4
SK7C3605R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1719 | 3/4 | 3/8 | 4
SK7C3607R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1720 | 3/4 | 3/8 | 4
SK7C3610R | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1721 | 3/4 | 3/8 | 4
SK7C3700R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1722 | 3/4 | 3/8 | 4
SK7C3705R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1723 | 3/4 | 3/8 | 4
SK7C3707R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1724 | 3/4 | 3/8 | 4
SK7C3710R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1725 | 3/4 | 3/8 | 4
SK7C3900R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1726 | 3/4 | 3/8 | 4
SK7C3905R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1727 | 3/4 | 3/8 | 4
SK7C3907R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1728 | 3/4 | 3/8 | 4
SK7C3910R | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1729 | 3/4 | 3/8 | 4
SL111800R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1874 | 3/4 | 3/8 | 4
SL111805R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1875 | 3/4 | 3/8 | 4
SL111807R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1876 | 3/4 | 3/8 | 4
SL111810R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1877 | 3/4 | 3/8 | 4
SL111900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1878 | 3/4 | 3/8 | 4
SL111905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1879 | 3/4 | 3/8 | 4
SL111907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1880 | 3/4 | 3/8 | 4
SL111910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1881 | 3/4 | 3/8 | 4
SL112400R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1882 | 3/4 | 3/8 | 4
SL112405R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1883 | 3/4 | 3/8 | 4
SL112407R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1884 | 3/4 | 3/8 | 4
SL112410R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1885 | 3/4 | 3/8 | 4
SL112500R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1886 | 3/4 | 3/8 | 4
SL112505R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1887 | 3/4 | 3/8 | 4
SL112507R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1888 | 3/4 | 3/8 | 4
SL112510R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1889 | 3/4 | 3/8 | 4
SL113000R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1890 | 3/4 | 3/8 | 4
SL113005R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1891 | 3/4 | 3/8 | 4
SL113007R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1892 | 3/4 | 3/8 | 4
SL113010R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1893 | 3/4 | 3/8 | 4
SL113100R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1894 | 3/4 | 3/8 | 4
SL113105R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1895 | 3/4 | 3/8 | 4
SL113107R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1896 | 3/4 | 3/8 | 4
SL113110R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1897 | 3/4 | 3/8 | 4
SL113600R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1898 | 3/4 | 3/8 | 4
SL113605R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1899 | 3/4 | 3/8 | 4
SL113607R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1900 | 3/4 | 3/8 | 4
SL113610R | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1901 | 3/4 | 3/8 | 4
SL113700R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1902 | 3/4 | 3/8 | 4
SL113705R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1903 | 3/4 | 3/8 | 4
SL113707R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1904 | 3/4 | 3/8 | 4
SL113710R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1905 | 3/4 | 3/8 | 4
SL113900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1906 | 3/4 | 3/8 | 4
SL113905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1907 | 3/4 | 3/8 | 4
SL113907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1908 | 3/4 | 3/8 | 4
SL113910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1909 | 3/4 | 3/8 | 4
SL1A1800R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1910 | 3/4 | 3/8 | 4
SL1A1805R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1911 | 3/4 | 3/8 | 4
SL1A1807R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1912 | 3/4 | 3/8 | 4
SL1A1810R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1913 | 3/4 | 3/8 | 4
SL1A1900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1914 | 3/4 | 3/8 | 4
SL1A1905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1915 | 3/4 | 3/8 | 4
SL1A1907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1916 | 3/4 | 3/8 | 4
SL1A1910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1917 | 3/4 | 3/8 | 4
SL1A2400R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1918 | 3/4 | 3/8 | 4
SL1A2405R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1919 | 3/4 | 3/8 | 4
SL1A2407R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1920 | 3/4 | 3/8 | 4
SL1A2410R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1921 | 3/4 | 3/8 | 4
SL1A2500R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1922 | 3/4 | 3/8 | 4
SL1A2505R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1923 | 3/4 | 3/8 | 4
SL1A2507R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1924 | 3/4 | 3/8 | 4
SL1A2510R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1925 | 3/4 | 3/8 | 4
SL1A3000R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1926 | 3/4 | 3/8 | 4
SL1A3005R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1927 | 3/4 | 3/8 | 4
SL1A3007R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1928 | 3/4 | 3/8 | 4
SL1A3010R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1929 | 3/4 | 3/8 | 4
SL1A3100R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1930 | 3/4 | 3/8 | 4
SL1A3105R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1931 | 3/4 | 3/8 | 4
SL1A3107R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1932 | 3/4 | 3/8 | 4
SL1A3110R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1933 | 3/4 | 3/8 | 4
SL1A3600R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1934 | 3/4 | 3/8 | 4
SL1A3605R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1935 | 3/4 | 3/8 | 4
SL1A3607R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1936 | 3/4 | 3/8 | 4
SL1A3610R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1937 | 3/4 | 3/8 | 4
SL1A3700R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1938 | 3/4 | 3/8 | 4
SL1A3705R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1939 | 3/4 | 3/8 | 4
SL1A3707R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1940 | 3/4 | 3/8 | 4
SL1A3710R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1941 | 3/4 | 3/8 | 4
SL1A3900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1942 | 3/4 | 3/8 | 4
SL1A3905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1943 | 3/4 | 3/8 | 4
SL1A3907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1944 | 3/4 | 3/8 | 4
SL1A3910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1945 | 3/4 | 3/8 | 4
SL1B1800R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1946 | 3/4 | 3/8 | 4
SL1B1805R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1947 | 3/4 | 3/8 | 4
SL1B1807R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1948 | 3/4 | 3/8 | 4
SL1B1810R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1949 | 3/4 | 3/8 | 4
SL1B1900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1950 | 3/4 | 3/8 | 4
SL1B1905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1951 | 3/4 | 3/8 | 4
SL1B1907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1952 | 3/4 | 3/8 | 4
SL1B1910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1953 | 3/4 | 3/8 | 4
SL1B2400R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1954 | 3/4 | 3/8 | 4
SL1B2405R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1955 | 3/4 | 3/8 | 4
SL1B2407R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1956 | 3/4 | 3/8 | 4
SL1B2410R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1957 | 3/4 | 3/8 | 4
SL1B2500R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1958 | 3/4 | 3/8 | 4
SL1B2505R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1959 | 3/4 | 3/8 | 4
SL1B2507R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1960 | 3/4 | 3/8 | 4
SL1B2510R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1961 | 3/4 | 3/8 | 4
SL1B3000R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1962 | 3/4 | 3/8 | 4
SL1B3005R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1963 | 3/4 | 3/8 | 4
SL1B3007R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1964 | 3/4 | 3/8 | 4
SL1B3010R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1965 | 3/4 | 3/8 | 4
SL1B3100R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1966 | 3/4 | 3/8 | 4
SL1B3105R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1967 | 3/4 | 3/8 | 4
SL1B3107R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1968 | 3/4 | 3/8 | 4
SL1B3110R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1969 | 3/4 | 3/8 | 4
SL1B3600R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1970 | 3/4 | 3/8 | 4
SL1B3605R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1971 | 3/4 | 3/8 | 4
SL1B3607R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1972 | 3/4 | 3/8 | 4
SL1B3610R | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1973 | 3/4 | 3/8 | 4
SL1B3700R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1974 | 3/4 | 3/8 | 4
SL1B3705R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1975 | 3/4 | 3/8 | 4
SL1B3707R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1976 | 3/4 | 3/8 | 4
SL1B3710R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1977 | 3/4 | 3/8 | 4
SL1B3900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1978 | 3/4 | 3/8 | 4
SL1B3905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1979 | 3/4 | 3/8 | 4
SL1B3907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1980 | 3/4 | 3/8 | 4
SL1B3910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1981 | 3/4 | 3/8 | 4
SL1C1800R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1982 | 3/4 | 3/8 | 4
SL1C1805R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1983 | 3/4 | 3/8 | 4
SL1C1807R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1984 | 3/4 | 3/8 | 4
SL1C1810R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1985 | 3/4 | 3/8 | 4
SL1C1900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1986 | 3/4 | 3/8 | 4
SL1C1905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1987 | 3/4 | 3/8 | 4
SL1C1907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1988 | 3/4 | 3/8 | 4
SL1C1910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1989 | 3/4 | 3/8 | 4
SL1C2400R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1990 | 3/4 | 3/8 | 4
SL1C2405R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1991 | 3/4 | 3/8 | 4
SL1C2407R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1992 | 3/4 | 3/8 | 4
SL1C2410R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1993 | 3/4 | 3/8 | 4
SL1C2500R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1994 | 3/4 | 3/8 | 4
SL1C2505R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1995 | 3/4 | 3/8 | 4
SL1C2507R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1996 | 3/4 | 3/8 | 4
SL1C2510R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1997 | 3/4 | 3/8 | 4
SL1C3000R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1998 | 3/4 | 3/8 | 4
SL1C3005R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1999 | 3/4 | 3/8 | 4
SL1C3007R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2000 | 3/4 | 3/8 | 4
SL1C3010R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2001 | 3/4 | 3/8 | 4
SL1C3100R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2002 | 3/4 | 3/8 | 4
SL1C3105R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2003 | 3/4 | 3/8 | 4
SL1C3107R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2004 | 3/4 | 3/8 | 4
SL1C3110R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2005 | 3/4 | 3/8 | 4
SL1C3600R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2006 | 3/4 | 3/8 | 4
SL1C3605R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2007 | 3/4 | 3/8 | 4
SL1C3607R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2008 | 3/4 | 3/8 | 4
SL1C3610R | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2009 | 3/4 | 3/8 | 4
SL1C3700R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2010 | 3/4 | 3/8 | 4
SL1C3705R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2011 | 3/4 | 3/8 | 4
SL1C3707R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2012 | 3/4 | 3/8 | 4
SL1C3710R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2013 | 3/4 | 3/8 | 4
SL1C3900R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2014 | 3/4 | 3/8 | 4
SL1C3905R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2015 | 3/4 | 3/8 | 4
SL1C3907R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2016 | 3/4 | 3/8 | 4
SL1C3910R | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2017 | 3/4 | 3/8 | 4
SL511800R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2306 | 3/4 | 3/8 | 4
SL511805R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2307 | 3/4 | 3/8 | 4
SL511807R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2308 | 3/4 | 3/8 | 4
SL511810R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2309 | 3/4 | 3/8 | 4
SL511900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2310 | 3/4 | 3/8 | 4
SL511905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2311 | 3/4 | 3/8 | 4
SL511907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2312 | 3/4 | 3/8 | 4
SL511910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2313 | 3/4 | 3/8 | 4
SL512400R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2314 | 3/4 | 3/8 | 4
SL512405R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2315 | 3/4 | 3/8 | 4
SL512407R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2316 | 3/4 | 3/8 | 4
SL512410R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2317 | 3/4 | 3/8 | 4
SL512500R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2318 | 3/4 | 3/8 | 4
SL512505R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2319 | 3/4 | 3/8 | 4
SL512507R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2320 | 3/4 | 3/8 | 4
SL512510R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2321 | 3/4 | 3/8 | 4
SL513000R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2322 | 3/4 | 3/8 | 4
SL513005R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2323 | 3/4 | 3/8 | 4
SL513007R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2324 | 3/4 | 3/8 | 4
SL513010R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2325 | 3/4 | 3/8 | 4
SL513100R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2326 | 3/4 | 3/8 | 4
SL513105R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2327 | 3/4 | 3/8 | 4
SL513107R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2328 | 3/4 | 3/8 | 4
SL513110R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2329 | 3/4 | 3/8 | 4
SL513600R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2330 | 3/4 | 3/8 | 4
SL513605R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2331 | 3/4 | 3/8 | 4
SL513607R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2332 | 3/4 | 3/8 | 4
SL513610R | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2333 | 3/4 | 3/8 | 4
SL513700R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2334 | 3/4 | 3/8 | 4
SL513705R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2335 | 3/4 | 3/8 | 4
SL513707R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2336 | 3/4 | 3/8 | 4
SL513710R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2337 | 3/4 | 3/8 | 4
SL513900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2338 | 3/4 | 3/8 | 4
SL513905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2339 | 3/4 | 3/8 | 4
SL513907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2340 | 3/4 | 3/8 | 4
SL513910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2341 | 3/4 | 3/8 | 4
SL5A1800R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2342 | 3/4 | 3/8 | 4
SL5A1805R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2343 | 3/4 | 3/8 | 4
SL5A1807R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2344 | 3/4 | 3/8 | 4
SL5A1810R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2345 | 3/4 | 3/8 | 4
SL5A1900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2346 | 3/4 | 3/8 | 4
SL5A1905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2347 | 3/4 | 3/8 | 4
SL5A1907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2348 | 3/4 | 3/8 | 4
SL5A1910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2349 | 3/4 | 3/8 | 4
SL5A2400R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2350 | 3/4 | 3/8 | 4
SL5A2405R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2351 | 3/4 | 3/8 | 4
SL5A2407R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2352 | 3/4 | 3/8 | 4
SL5A2410R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2353 | 3/4 | 3/8 | 4
SL5A2500R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2354 | 3/4 | 3/8 | 4
SL5A2505R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2355 | 3/4 | 3/8 | 4
SL5A2507R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2356 | 3/4 | 3/8 | 4
SL5A2510R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2357 | 3/4 | 3/8 | 4
SL5A3000R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2358 | 3/4 | 3/8 | 4
SL5A3005R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2359 | 3/4 | 3/8 | 4
SL5A3007R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2360 | 3/4 | 3/8 | 4
SL5A3010R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2361 | 3/4 | 3/8 | 4
SL5A3100R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2362 | 3/4 | 3/8 | 4
SL5A3105R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2363 | 3/4 | 3/8 | 4
SL5A3107R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2364 | 3/4 | 3/8 | 4
SL5A3110R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2365 | 3/4 | 3/8 | 4
SL5A3600R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2366 | 3/4 | 3/8 | 4
SL5A3605R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2367 | 3/4 | 3/8 | 4
SL5A3607R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2368 | 3/4 | 3/8 | 4
SL5A3610R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2369 | 3/4 | 3/8 | 4
SL5A3700R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2370 | 3/4 | 3/8 | 4
SL5A3705R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2371 | 3/4 | 3/8 | 4
SL5A3707R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2372 | 3/4 | 3/8 | 4
SL5A3710R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2373 | 3/4 | 3/8 | 4
SL5A3900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2374 | 3/4 | 3/8 | 4
SL5A3905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2375 | 3/4 | 3/8 | 4
SL5A3907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2376 | 3/4 | 3/8 | 4
SL5A3910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2377 | 3/4 | 3/8 | 4
SL5B1800R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2378 | 3/4 | 3/8 | 4
SL5B1805R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2379 | 3/4 | 3/8 | 4
SL5B1807R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2380 | 3/4 | 3/8 | 4
SL5B1810R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2381 | 3/4 | 3/8 | 4
SL5B1900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2382 | 3/4 | 3/8 | 4
SL5B1905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2383 | 3/4 | 3/8 | 4
SL5B1907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2384 | 3/4 | 3/8 | 4
SL5B1910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2385 | 3/4 | 3/8 | 4
SL5B2400R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2386 | 3/4 | 3/8 | 4
SL5B2405R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2387 | 3/4 | 3/8 | 4
SL5B2407R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2388 | 3/4 | 3/8 | 4
SL5B2410R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2389 | 3/4 | 3/8 | 4
SL5B2500R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2390 | 3/4 | 3/8 | 4
SL5B2505R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2391 | 3/4 | 3/8 | 4
SL5B2507R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2392 | 3/4 | 3/8 | 4
SL5B2510R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2393 | 3/4 | 3/8 | 4
SL5B3000R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2394 | 3/4 | 3/8 | 4
SL5B3005R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2395 | 3/4 | 3/8 | 4
SL5B3007R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2396 | 3/4 | 3/8 | 4
SL5B3010R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2397 | 3/4 | 3/8 | 4
SL5B3100R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2398 | 3/4 | 3/8 | 4
SL5B3105R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2399 | 3/4 | 3/8 | 4
SL5B3107R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2400 | 3/4 | 3/8 | 4
SL5B3110R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2401 | 3/4 | 3/8 | 4
SL5B3600R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2402 | 3/4 | 3/8 | 4
SL5B3605R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2403 | 3/4 | 3/8 | 4
SL5B3607R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2404 | 3/4 | 3/8 | 4
SL5B3610R | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2405 | 3/4 | 3/8 | 4
SL5B3700R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2406 | 3/4 | 3/8 | 4
SL5B3705R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2407 | 3/4 | 3/8 | 4
SL5B3707R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2408 | 3/4 | 3/8 | 4
SL5B3710R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2409 | 3/4 | 3/8 | 4
SL5B3900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2410 | 3/4 | 3/8 | 4
SL5B3905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2411 | 3/4 | 3/8 | 4
SL5B3907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2412 | 3/4 | 3/8 | 4
SL5B3910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2413 | 3/4 | 3/8 | 4
SL5C1800R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2414 | 3/4 | 3/8 | 4
SL5C1805R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2415 | 3/4 | 3/8 | 4
SL5C1807R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2416 | 3/4 | 3/8 | 4
SL5C1810R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2417 | 3/4 | 3/8 | 4
SL5C1900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2418 | 3/4 | 3/8 | 4
SL5C1905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2419 | 3/4 | 3/8 | 4
SL5C1907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2420 | 3/4 | 3/8 | 4
SL5C1910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2421 | 3/4 | 3/8 | 4
SL5C2400R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2422 | 3/4 | 3/8 | 4
SL5C2405R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2423 | 3/4 | 3/8 | 4
SL5C2407R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2424 | 3/4 | 3/8 | 4
SL5C2410R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2425 | 3/4 | 3/8 | 4
SL5C2500R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2426 | 3/4 | 3/8 | 4
SL5C2505R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2427 | 3/4 | 3/8 | 4
SL5C2507R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2428 | 3/4 | 3/8 | 4
SL5C2510R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2429 | 3/4 | 3/8 | 4
SL5C3000R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2430 | 3/4 | 3/8 | 4
SL5C3005R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2431 | 3/4 | 3/8 | 4
SL5C3007R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2432 | 3/4 | 3/8 | 4
SL5C3010R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2433 | 3/4 | 3/8 | 4
SL5C3100R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2434 | 3/4 | 3/8 | 4
SL5C3105R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2435 | 3/4 | 3/8 | 4
SL5C3107R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2436 | 3/4 | 3/8 | 4
SL5C3110R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2437 | 3/4 | 3/8 | 4
SL5C3600R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2438 | 3/4 | 3/8 | 4
SL5C3605R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2439 | 3/4 | 3/8 | 4
SL5C3607R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2440 | 3/4 | 3/8 | 4
SL5C3610R | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2441 | 3/4 | 3/8 | 4
SL5C3700R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2442 | 3/4 | 3/8 | 4
SL5C3705R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2443 | 3/4 | 3/8 | 4
SL5C3707R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2444 | 3/4 | 3/8 | 4
SL5C3710R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2445 | 3/4 | 3/8 | 4
SL5C3900R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2446 | 3/4 | 3/8 | 4
SL5C3905R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2447 | 3/4 | 3/8 | 4
SL5C3907R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2448 | 3/4 | 3/8 | 4
SL5C3910R | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2449 | 3/4 | 3/8 | 4
SL611800R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2450 | 3/4 | 3/8 | 4
SL611805R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2451 | 3/4 | 3/8 | 4
SL611807R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2452 | 3/4 | 3/8 | 4
SL611810R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2453 | 3/4 | 3/8 | 4
SL611900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2454 | 3/4 | 3/8 | 4
SL611905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2455 | 3/4 | 3/8 | 4
SL611907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2456 | 3/4 | 3/8 | 4
SL611910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2457 | 3/4 | 3/8 | 4
SL612400R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2458 | 3/4 | 3/8 | 4
SL612405R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2459 | 3/4 | 3/8 | 4
SL612407R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2460 | 3/4 | 3/8 | 4
SL612410R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2461 | 3/4 | 3/8 | 4
SL612500R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2462 | 3/4 | 3/8 | 4
SL612505R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2463 | 3/4 | 3/8 | 4
SL612507R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2464 | 3/4 | 3/8 | 4
SL612510R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2465 | 3/4 | 3/8 | 4
SL613000R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2466 | 3/4 | 3/8 | 4
SL613005R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2467 | 3/4 | 3/8 | 4
SL613007R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2468 | 3/4 | 3/8 | 4
SL613010R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2469 | 3/4 | 3/8 | 4
SL613100R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2470 | 3/4 | 3/8 | 4
SL613105R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2471 | 3/4 | 3/8 | 4
SL613107R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2472 | 3/4 | 3/8 | 4
SL613110R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2473 | 3/4 | 3/8 | 4
SL613600R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2474 | 3/4 | 3/8 | 4
SL613605R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2475 | 3/4 | 3/8 | 4
SL613607R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2476 | 3/4 | 3/8 | 4
SL613610R | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2477 | 3/4 | 3/8 | 4
SL613700R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2478 | 3/4 | 3/8 | 4
SL613705R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2479 | 3/4 | 3/8 | 4
SL613707R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2480 | 3/4 | 3/8 | 4
SL613710R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2481 | 3/4 | 3/8 | 4
SL613900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2482 | 3/4 | 3/8 | 4
SL613905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2483 | 3/4 | 3/8 | 4
SL613907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2484 | 3/4 | 3/8 | 4
SL613910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2485 | 3/4 | 3/8 | 4
SL6A1800R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2486 | 3/4 | 3/8 | 4
SL6A1805R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2487 | 3/4 | 3/8 | 4
SL6A1807R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2488 | 3/4 | 3/8 | 4
SL6A1810R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2489 | 3/4 | 3/8 | 4
SL6A1900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2490 | 3/4 | 3/8 | 4
SL6A1905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2491 | 3/4 | 3/8 | 4
SL6A1907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2492 | 3/4 | 3/8 | 4
SL6A1910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2493 | 3/4 | 3/8 | 4
SL6A2400R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2494 | 3/4 | 3/8 | 4
SL6A2405R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2495 | 3/4 | 3/8 | 4
SL6A2407R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2496 | 3/4 | 3/8 | 4
SL6A2410R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2497 | 3/4 | 3/8 | 4
SL6A2500R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2498 | 3/4 | 3/8 | 4
SL6A2505R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2499 | 3/4 | 3/8 | 4
SL6A2507R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2500 | 3/4 | 3/8 | 4
SL6A2510R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2501 | 3/4 | 3/8 | 4
SL6A3000R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2502 | 3/4 | 3/8 | 4
SL6A3005R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2503 | 3/4 | 3/8 | 4
SL6A3007R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2504 | 3/4 | 3/8 | 4
SL6A3010R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2505 | 3/4 | 3/8 | 4
SL6A3100R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2506 | 3/4 | 3/8 | 4
SL6A3105R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2507 | 3/4 | 3/8 | 4
SL6A3107R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2508 | 3/4 | 3/8 | 4
SL6A3110R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2509 | 3/4 | 3/8 | 4
SL6A3600R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2510 | 3/4 | 3/8 | 4
SL6A3605R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2511 | 3/4 | 3/8 | 4
SL6A3607R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2512 | 3/4 | 3/8 | 4
SL6A3610R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2513 | 3/4 | 3/8 | 4
SL6A3700R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2514 | 3/4 | 3/8 | 4
SL6A3705R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2515 | 3/4 | 3/8 | 4
SL6A3707R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2516 | 3/4 | 3/8 | 4
SL6A3710R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2517 | 3/4 | 3/8 | 4
SL6A3900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2518 | 3/4 | 3/8 | 4
SL6A3905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2519 | 3/4 | 3/8 | 4
SL6A3907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2520 | 3/4 | 3/8 | 4
SL6A3910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2521 | 3/4 | 3/8 | 4
SL6B1800R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2522 | 3/4 | 3/8 | 4
SL6B1805R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2523 | 3/4 | 3/8 | 4
SL6B1807R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2524 | 3/4 | 3/8 | 4
SL6B1810R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2525 | 3/4 | 3/8 | 4
SL6B1900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2526 | 3/4 | 3/8 | 4
SL6B1905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2527 | 3/4 | 3/8 | 4
SL6B1907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2528 | 3/4 | 3/8 | 4
SL6B1910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2529 | 3/4 | 3/8 | 4
SL6B2400R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2530 | 3/4 | 3/8 | 4
SL6B2405R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2531 | 3/4 | 3/8 | 4
SL6B2407R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2532 | 3/4 | 3/8 | 4
SL6B2410R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2533 | 3/4 | 3/8 | 4
SL6B2500R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2534 | 3/4 | 3/8 | 4
SL6B2505R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2535 | 3/4 | 3/8 | 4
SL6B2507R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2536 | 3/4 | 3/8 | 4
SL6B2510R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2537 | 3/4 | 3/8 | 4
SL6B3000R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2538 | 3/4 | 3/8 | 4
SL6B3005R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2539 | 3/4 | 3/8 | 4
SL6B3007R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2540 | 3/4 | 3/8 | 4
SL6B3010R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2541 | 3/4 | 3/8 | 4
SL6B3100R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2542 | 3/4 | 3/8 | 4
SL6B3105R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2543 | 3/4 | 3/8 | 4
SL6B3107R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2544 | 3/4 | 3/8 | 4
SL6B3110R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2545 | 3/4 | 3/8 | 4
SL6B3600R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2546 | 3/4 | 3/8 | 4
SL6B3605R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2547 | 3/4 | 3/8 | 4
SL6B3607R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2548 | 3/4 | 3/8 | 4
SL6B3610R | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2549 | 3/4 | 3/8 | 4
SL6B3700R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2550 | 3/4 | 3/8 | 4
SL6B3705R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2551 | 3/4 | 3/8 | 4
SL6B3707R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2552 | 3/4 | 3/8 | 4
SL6B3710R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2553 | 3/4 | 3/8 | 4
SL6B3900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2554 | 3/4 | 3/8 | 4
SL6B3905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2555 | 3/4 | 3/8 | 4
SL6B3907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2556 | 3/4 | 3/8 | 4
SL6B3910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2557 | 3/4 | 3/8 | 4
SL6C1800R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2558 | 3/4 | 3/8 | 4
SL6C1805R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2559 | 3/4 | 3/8 | 4
SL6C1807R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2560 | 3/4 | 3/8 | 4
SL6C1810R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2561 | 3/4 | 3/8 | 4
SL6C1900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2562 | 3/4 | 3/8 | 4
SL6C1905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2563 | 3/4 | 3/8 | 4
SL6C1907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2564 | 3/4 | 3/8 | 4
SL6C1910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2565 | 3/4 | 3/8 | 4
SL6C2400R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2566 | 3/4 | 3/8 | 4
SL6C2405R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2567 | 3/4 | 3/8 | 4
SL6C2407R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2568 | 3/4 | 3/8 | 4
SL6C2410R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2569 | 3/4 | 3/8 | 4
SL6C2500R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2570 | 3/4 | 3/8 | 4
SL6C2505R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2571 | 3/4 | 3/8 | 4
SL6C2507R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2572 | 3/4 | 3/8 | 4
SL6C2510R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2573 | 3/4 | 3/8 | 4
SL6C3000R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2574 | 3/4 | 3/8 | 4
SL6C3005R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2575 | 3/4 | 3/8 | 4
SL6C3007R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2576 | 3/4 | 3/8 | 4
SL6C3010R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2577 | 3/4 | 3/8 | 4
SL6C3100R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2578 | 3/4 | 3/8 | 4
SL6C3105R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2579 | 3/4 | 3/8 | 4
SL6C3107R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2580 | 3/4 | 3/8 | 4
SL6C3110R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2581 | 3/4 | 3/8 | 4
SL6C3600R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2582 | 3/4 | 3/8 | 4
SL6C3605R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2583 | 3/4 | 3/8 | 4
SL6C3607R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2584 | 3/4 | 3/8 | 4
SL6C3610R | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2585 | 3/4 | 3/8 | 4
SL6C3700R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2586 | 3/4 | 3/8 | 4
SL6C3705R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2587 | 3/4 | 3/8 | 4
SL6C3707R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2588 | 3/4 | 3/8 | 4
SL6C3710R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2589 | 3/4 | 3/8 | 4
SL6C3900R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2590 | 3/4 | 3/8 | 4
SL6C3905R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2591 | 3/4 | 3/8 | 4
SL6C3907R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2592 | 3/4 | 3/8 | 4
SL6C3910R | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2593 | 3/4 | 3/8 | 4
SL911800R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2882 | 3/4 | 3/8 | 4
SL911805R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2883 | 3/4 | 3/8 | 4
SL911807R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2884 | 3/4 | 3/8 | 4
SL911810R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2885 | 3/4 | 3/8 | 4
SL911900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2886 | 3/4 | 3/8 | 4
SL911905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2887 | 3/4 | 3/8 | 4
SL911907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2888 | 3/4 | 3/8 | 4
SL911910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2889 | 3/4 | 3/8 | 4
SL912400R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2890 | 3/4 | 3/8 | 4
SL912405R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2891 | 3/4 | 3/8 | 4
SL912407R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2892 | 3/4 | 3/8 | 4
SL912410R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2893 | 3/4 | 3/8 | 4
SL912500R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2894 | 3/4 | 3/8 | 4
SL912505R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2895 | 3/4 | 3/8 | 4
SL912507R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2896 | 3/4 | 3/8 | 4
SL912510R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2897 | 3/4 | 3/8 | 4
SL913000R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2898 | 3/4 | 3/8 | 4
SL913005R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2899 | 3/4 | 3/8 | 4
SL913007R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2900 | 3/4 | 3/8 | 4
SL913010R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2901 | 3/4 | 3/8 | 4
SL913100R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2902 | 3/4 | 3/8 | 4
SL913105R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2903 | 3/4 | 3/8 | 4
SL913107R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2904 | 3/4 | 3/8 | 4
SL913110R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2905 | 3/4 | 3/8 | 4
SL913600R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2906 | 3/4 | 3/8 | 4
SL913605R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2907 | 3/4 | 3/8 | 4
SL913607R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2908 | 3/4 | 3/8 | 4
SL913610R | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-454B & R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2909 | 3/4 | 3/8 | 4
SL913700R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2910 | 3/4 | 3/8 | 4
SL913705R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2911 | 3/4 | 3/8 | 4
SL913707R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2912 | 3/4 | 3/8 | 4
SL913710R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2913 | 3/4 | 3/8 | 4
SL913900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2914 | 3/4 | 3/8 | 4
SL913905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2915 | 3/4 | 3/8 | 4
SL913907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2916 | 3/4 | 3/8 | 4
SL913910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-454B & R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2917 | 3/4 | 3/8 | 4
SL9A1800R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2918 | 3/4 | 3/8 | 4
SL9A1805R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2919 | 3/4 | 3/8 | 4
SL9A1807R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2920 | 3/4 | 3/8 | 4
SL9A1810R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2921 | 3/4 | 3/8 | 4
SL9A1900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2922 | 3/4 | 3/8 | 4
SL9A1905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2923 | 3/4 | 3/8 | 4
SL9A1907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2924 | 3/4 | 3/8 | 4
SL9A1910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2925 | 3/4 | 3/8 | 4
SL9A2400R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2926 | 3/4 | 3/8 | 4
SL9A2405R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2927 | 3/4 | 3/8 | 4
SL9A2407R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2928 | 3/4 | 3/8 | 4
SL9A2410R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2929 | 3/4 | 3/8 | 4
SL9A2500R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2930 | 3/4 | 3/8 | 4
SL9A2505R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2931 | 3/4 | 3/8 | 4
SL9A2507R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2932 | 3/4 | 3/8 | 4
SL9A2510R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2933 | 3/4 | 3/8 | 4
SL9A3000R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2934 | 3/4 | 3/8 | 4
SL9A3005R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2935 | 3/4 | 3/8 | 4
SL9A3007R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2936 | 3/4 | 3/8 | 4
SL9A3010R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2937 | 3/4 | 3/8 | 4
SL9A3100R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2938 | 3/4 | 3/8 | 4
SL9A3105R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2939 | 3/4 | 3/8 | 4
SL9A3107R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2940 | 3/4 | 3/8 | 4
SL9A3110R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2941 | 3/4 | 3/8 | 4
SL9A3600R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2942 | 3/4 | 3/8 | 4
SL9A3605R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2943 | 3/4 | 3/8 | 4
SL9A3607R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2944 | 3/4 | 3/8 | 4
SL9A3610R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2945 | 3/4 | 3/8 | 4
SL9A3700R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2946 | 3/4 | 3/8 | 4
SL9A3705R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2947 | 3/4 | 3/8 | 4
SL9A3707R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2948 | 3/4 | 3/8 | 4
SL9A3710R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2949 | 3/4 | 3/8 | 4
SL9A3900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2950 | 3/4 | 3/8 | 4
SL9A3905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2951 | 3/4 | 3/8 | 4
SL9A3907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2952 | 3/4 | 3/8 | 4
SL9A3910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2953 | 3/4 | 3/8 | 4
SL9B1800R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2954 | 3/4 | 3/8 | 4
SL9B1805R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2955 | 3/4 | 3/8 | 4
SL9B1807R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2956 | 3/4 | 3/8 | 4
SL9B1810R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2957 | 3/4 | 3/8 | 4
SL9B1900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2958 | 3/4 | 3/8 | 4
SL9B1905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2959 | 3/4 | 3/8 | 4
SL9B1907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2960 | 3/4 | 3/8 | 4
SL9B1910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2961 | 3/4 | 3/8 | 4
SL9B2400R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2962 | 3/4 | 3/8 | 4
SL9B2405R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2963 | 3/4 | 3/8 | 4
SL9B2407R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2964 | 3/4 | 3/8 | 4
SL9B2410R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2965 | 3/4 | 3/8 | 4
SL9B2500R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2966 | 3/4 | 3/8 | 4
SL9B2505R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2967 | 3/4 | 3/8 | 4
SL9B2507R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2968 | 3/4 | 3/8 | 4
SL9B2510R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2969 | 3/4 | 3/8 | 4
SL9B3000R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2970 | 3/4 | 3/8 | 4
SL9B3005R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2971 | 3/4 | 3/8 | 4
SL9B3007R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2972 | 3/4 | 3/8 | 4
SL9B3010R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2973 | 3/4 | 3/8 | 4
SL9B3100R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2974 | 3/4 | 3/8 | 4
SL9B3105R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2975 | 3/4 | 3/8 | 4
SL9B3107R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2976 | 3/4 | 3/8 | 4
SL9B3110R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2977 | 3/4 | 3/8 | 4
SL9B3600R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2978 | 3/4 | 3/8 | 4
SL9B3605R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2979 | 3/4 | 3/8 | 4
SL9B3607R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2980 | 3/4 | 3/8 | 4
SL9B3610R | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2981 | 3/4 | 3/8 | 4
SL9B3700R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2982 | 3/4 | 3/8 | 4
SL9B3705R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2983 | 3/4 | 3/8 | 4
SL9B3707R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2984 | 3/4 | 3/8 | 4
SL9B3710R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2985 | 3/4 | 3/8 | 4
SL9B3900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2986 | 3/4 | 3/8 | 4
SL9B3905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2987 | 3/4 | 3/8 | 4
SL9B3907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2988 | 3/4 | 3/8 | 4
SL9B3910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-32) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2989 | 3/4 | 3/8 | 4
SL9C1800R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2990 | 3/4 | 3/8 | 4
SL9C1805R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2991 | 3/4 | 3/8 | 4
SL9C1807R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2992 | 3/4 | 3/8 | 4
SL9C1810R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2993 | 3/4 | 3/8 | 4
SL9C1900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2994 | 3/4 | 3/8 | 4
SL9C1905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2995 | 3/4 | 3/8 | 4
SL9C1907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2996 | 3/4 | 3/8 | 4
SL9C1910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2997 | 3/4 | 3/8 | 4
SL9C2400R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2998 | 3/4 | 3/8 | 4
SL9C2405R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2999 | 3/4 | 3/8 | 4
SL9C2407R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3000 | 3/4 | 3/8 | 4
SL9C2410R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3001 | 3/4 | 3/8 | 4
SL9C2500R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3002 | 3/4 | 3/8 | 4
SL9C2505R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3003 | 3/4 | 3/8 | 4
SL9C2507R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3004 | 3/4 | 3/8 | 4
SL9C2510R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3005 | 3/4 | 3/8 | 4
SL9C3000R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3006 | 3/4 | 3/8 | 4
SL9C3005R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3007 | 3/4 | 3/8 | 4
SL9C3007R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3008 | 3/4 | 3/8 | 4
SL9C3010R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3009 | 3/4 | 3/8 | 4
SL9C3100R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3010 | 3/4 | 3/8 | 4
SL9C3105R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3011 | 3/4 | 3/8 | 4
SL9C3107R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3012 | 3/4 | 3/8 | 4
SL9C3110R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3013 | 3/4 | 3/8 | 4
SL9C3600R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3014 | 3/4 | 3/8 | 4
SL9C3605R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3015 | 3/4 | 3/8 | 4
SL9C3607R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3016 | 3/4 | 3/8 | 4
SL9C3610R | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3017 | 3/4 | 3/8 | 4
SL9C3700R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3018 | 3/4 | 3/8 | 4
SL9C3705R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3019 | 3/4 | 3/8 | 4
SL9C3707R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3020 | 3/4 | 3/8 | 4
SL9C3710R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3021 | 3/4 | 3/8 | 4
SL9C3900R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3022 | 3/4 | 3/8 | 4
SL9C3905R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3023 | 3/4 | 3/8 | 4
SL9C3907R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3024 | 3/4 | 3/8 | 4
SL9C3910R | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-454B) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3025 | 3/4 | 3/8 | 4
SM211800A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 4
SM211805A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 3 | 3/4 | 3/8 | 4
SM211807A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 4 | 3/4 | 3/8 | 4
SM211810A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 5 | 3/4 | 3/8 | 4
SM211900A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 6 | 3/4 | 3/8 | 4
SM211905A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 7 | 3/4 | 3/8 | 4
SM211907A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 8 | 3/4 | 3/8 | 4
SM211910A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 9 | 3/4 | 3/8 | 4
SM212400A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 10 | 3/4 | 3/8 | 4
SM212405A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 11 | 3/4 | 3/8 | 4
SM212407A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 12 | 3/4 | 3/8 | 4
SM212410A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 13 | 3/4 | 3/8 | 4
SM212500A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 14 | 3/4 | 3/8 | 4
SM212505A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 15 | 3/4 | 3/8 | 4
SM212507A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 16 | 3/4 | 3/8 | 4
SM212510A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 17 | 3/4 | 3/8 | 4
SM213000A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 18 | 3/4 | 3/8 | 4
SM213005A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 19 | 3/4 | 3/8 | 4
SM213007A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 20 | 3/4 | 3/8 | 4
SM213010A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 21 | 3/4 | 3/8 | 4
SM213100A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 22 | 3/4 | 3/8 | 4
SM213105A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 23 | 3/4 | 3/8 | 4
SM213107A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 24 | 3/4 | 3/8 | 4
SM213110A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 25 | 3/4 | 3/8 | 4
SM213600A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 26 | 3/4 | 3/8 | 4
SM213605A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 27 | 3/4 | 3/8 | 4
SM213607A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 28 | 3/4 | 3/8 | 4
SM213610A | S Series | 3-speed PSC motor | Upflow | M2 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 29 | 3/4 | 3/8 | 4
SM213700A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 30 | 3/4 | 3/8 | 4
SM213705A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 31 | 3/4 | 3/8 | 4
SM213707A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 32 | 3/4 | 3/8 | 4
SM213710A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 33 | 3/4 | 3/8 | 4
SM271800A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 38 | 3/4 | 3/8 | 4
SM271805A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 39 | 3/4 | 3/8 | 4
SM271807A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 40 | 3/4 | 3/8 | 4
SM271810A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 41 | 3/4 | 3/8 | 4
SM271900A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 42 | 3/4 | 3/8 | 4
SM271905A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 43 | 3/4 | 3/8 | 4
SM271907A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 44 | 3/4 | 3/8 | 4
SM271910A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 45 | 3/4 | 3/8 | 4
SM272400A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 46 | 3/4 | 3/8 | 4
SM272405A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 47 | 3/4 | 3/8 | 4
SM272407A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 48 | 3/4 | 3/8 | 4
SM272410A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 49 | 3/4 | 3/8 | 4
SM272500A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 50 | 3/4 | 3/8 | 4
SM272505A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 51 | 3/4 | 3/8 | 4
SM272507A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 52 | 3/4 | 3/8 | 4
SM272510A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 53 | 3/4 | 3/8 | 4
SM273000A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 54 | 3/4 | 3/8 | 4
SM273005A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 55 | 3/4 | 3/8 | 4
SM273007A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 56 | 3/4 | 3/8 | 4
SM273010A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 57 | 3/4 | 3/8 | 4
SM273100A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 58 | 3/4 | 3/8 | 4
SM273105A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 59 | 3/4 | 3/8 | 4
SM273107A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 60 | 3/4 | 3/8 | 4
SM273110A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 61 | 3/4 | 3/8 | 4
SM273600A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 62 | 3/4 | 3/8 | 4
SM273605A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 63 | 3/4 | 3/8 | 4
SM273607A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 64 | 3/4 | 3/8 | 4
SM273610A | S Series | 3-speed PSC motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 65 | 3/4 | 3/8 | 4
SM273700A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 66 | 3/4 | 3/8 | 4
SM273705A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 67 | 3/4 | 3/8 | 4
SM273707A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 68 | 3/4 | 3/8 | 4
SM273710A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 69 | 3/4 | 3/8 | 4
SM291800A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 74 | 3/4 | 3/8 | 4
SM291805A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 75 | 3/4 | 3/8 | 4
SM291807A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 76 | 3/4 | 3/8 | 4
SM291810A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 77 | 3/4 | 3/8 | 4
SM291900A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 78 | 3/4 | 3/8 | 4
SM291905A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 79 | 3/4 | 3/8 | 4
SM291907A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 80 | 3/4 | 3/8 | 4
SM291910A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 81 | 3/4 | 3/8 | 4
SM292400A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 82 | 3/4 | 3/8 | 4
SM292405A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 83 | 3/4 | 3/8 | 4
SM292407A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 84 | 3/4 | 3/8 | 4
SM292410A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 85 | 3/4 | 3/8 | 4
SM292500A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 86 | 3/4 | 3/8 | 4
SM292505A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 87 | 3/4 | 3/8 | 4
SM292507A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 88 | 3/4 | 3/8 | 4
SM292510A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 89 | 3/4 | 3/8 | 4
SM293000A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 90 | 3/4 | 3/8 | 4
SM293005A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 91 | 3/4 | 3/8 | 4
SM293007A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 92 | 3/4 | 3/8 | 4
SM293010A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 93 | 3/4 | 3/8 | 4
SM293100A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 94 | 3/4 | 3/8 | 4
SM293105A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 95 | 3/4 | 3/8 | 4
SM293107A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 96 | 3/4 | 3/8 | 4
SM293110A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 97 | 3/4 | 3/8 | 4
SM293600A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 98 | 3/4 | 3/8 | 4
SM293605A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 99 | 3/4 | 3/8 | 4
SM293607A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 100 | 3/4 | 3/8 | 4
SM293610A | S Series | 3-speed PSC motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 101 | 3/4 | 3/8 | 4
SM293700A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 102 | 3/4 | 3/8 | 4
SM293705A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 103 | 3/4 | 3/8 | 4
SM293707A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 104 | 3/4 | 3/8 | 4
SM293710A | S Series | 5-speed high eff. ECM motor | Upflow | M2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 105 | 3/4 | 3/8 | 4
SM311800A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 110 | 3/4 | 3/8 | 4
SM311805A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 111 | 3/4 | 3/8 | 4
SM311807A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 112 | 3/4 | 3/8 | 4
SM311810A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 113 | 3/4 | 3/8 | 4
SM311900A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 114 | 3/4 | 3/8 | 4
SM311905A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 115 | 3/4 | 3/8 | 4
SM311907A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 116 | 3/4 | 3/8 | 4
SM311910A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 117 | 3/4 | 3/8 | 4
SM312400A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 118 | 3/4 | 3/8 | 4
SM312405A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 119 | 3/4 | 3/8 | 4
SM312407A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 120 | 3/4 | 3/8 | 4
SM312410A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 121 | 3/4 | 3/8 | 4
SM312500A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 122 | 3/4 | 3/8 | 4
SM312505A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 123 | 3/4 | 3/8 | 4
SM312507A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 124 | 3/4 | 3/8 | 4
SM312510A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 125 | 3/4 | 3/8 | 4
SM313000A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 126 | 3/4 | 3/8 | 4
SM313005A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 127 | 3/4 | 3/8 | 4
SM313007A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 128 | 3/4 | 3/8 | 4
SM313010A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 129 | 3/4 | 3/8 | 4
SM313100A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 130 | 3/4 | 3/8 | 4
SM313105A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 131 | 3/4 | 3/8 | 4
SM313107A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 132 | 3/4 | 3/8 | 4
SM313110A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 133 | 3/4 | 3/8 | 4
SM313600A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 134 | 3/4 | 3/8 | 4
SM313605A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 135 | 3/4 | 3/8 | 4
SM313607A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 136 | 3/4 | 3/8 | 4
SM313610A | S Series | 3-speed PSC motor | Upflow | M3 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 137 | 3/4 | 3/8 | 4
SM313700A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 138 | 3/4 | 3/8 | 4
SM313705A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 139 | 3/4 | 3/8 | 4
SM313707A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 140 | 3/4 | 3/8 | 4
SM313710A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 141 | 3/4 | 3/8 | 4
SM371800A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 146 | 3/4 | 3/8 | 4
SM371805A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 147 | 3/4 | 3/8 | 4
SM371807A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 148 | 3/4 | 3/8 | 4
SM371810A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 149 | 3/4 | 3/8 | 4
SM371900A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 150 | 3/4 | 3/8 | 4
SM371905A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 151 | 3/4 | 3/8 | 4
SM371907A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 152 | 3/4 | 3/8 | 4
SM371910A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 153 | 3/4 | 3/8 | 4
SM372400A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 154 | 3/4 | 3/8 | 4
SM372405A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 155 | 3/4 | 3/8 | 4
SM372407A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 156 | 3/4 | 3/8 | 4
SM372410A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 157 | 3/4 | 3/8 | 4
SM372500A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 158 | 3/4 | 3/8 | 4
SM372505A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 159 | 3/4 | 3/8 | 4
SM372507A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 160 | 3/4 | 3/8 | 4
SM372510A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 161 | 3/4 | 3/8 | 4
SM373000A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 162 | 3/4 | 3/8 | 4
SM373005A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 163 | 3/4 | 3/8 | 4
SM373007A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 164 | 3/4 | 3/8 | 4
SM373010A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 165 | 3/4 | 3/8 | 4
SM373100A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 166 | 3/4 | 3/8 | 4
SM373105A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 167 | 3/4 | 3/8 | 4
SM373107A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 168 | 3/4 | 3/8 | 4
SM373110A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 169 | 3/4 | 3/8 | 4
SM373600A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 170 | 3/4 | 3/8 | 4
SM373605A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 171 | 3/4 | 3/8 | 4
SM373607A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 172 | 3/4 | 3/8 | 4
SM373610A | S Series | 3-speed PSC motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 173 | 3/4 | 3/8 | 4
SM373700A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 174 | 3/4 | 3/8 | 4
SM373705A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 175 | 3/4 | 3/8 | 4
SM373707A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 176 | 3/4 | 3/8 | 4
SM373710A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 177 | 3/4 | 3/8 | 4
SM391800A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 182 | 3/4 | 3/8 | 4
SM391805A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 183 | 3/4 | 3/8 | 4
SM391807A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 184 | 3/4 | 3/8 | 4
SM391810A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 185 | 3/4 | 3/8 | 4
SM391900A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 186 | 3/4 | 3/8 | 4
SM391905A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 187 | 3/4 | 3/8 | 4
SM391907A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 188 | 3/4 | 3/8 | 4
SM391910A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 189 | 3/4 | 3/8 | 4
SM392400A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 190 | 3/4 | 3/8 | 4
SM392405A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 191 | 3/4 | 3/8 | 4
SM392407A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 192 | 3/4 | 3/8 | 4
SM392410A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 193 | 3/4 | 3/8 | 4
SM392500A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 194 | 3/4 | 3/8 | 4
SM392505A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 195 | 3/4 | 3/8 | 4
SM392507A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 196 | 3/4 | 3/8 | 4
SM392510A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 197 | 3/4 | 3/8 | 4
SM393000A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 198 | 3/4 | 3/8 | 4
SM393005A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 199 | 3/4 | 3/8 | 4
SM393007A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 200 | 3/4 | 3/8 | 4
SM393010A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 201 | 3/4 | 3/8 | 4
SM393100A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 202 | 3/4 | 3/8 | 4
SM393105A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 203 | 3/4 | 3/8 | 4
SM393107A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 204 | 3/4 | 3/8 | 4
SM393110A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 205 | 3/4 | 3/8 | 4
SM393600A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 206 | 3/4 | 3/8 | 4
SM393605A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 207 | 3/4 | 3/8 | 4
SM393607A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 208 | 3/4 | 3/8 | 4
SM393610A | S Series | 3-speed PSC motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 209 | 3/4 | 3/8 | 4
SM393700A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 210 | 3/4 | 3/8 | 4
SM393705A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 211 | 3/4 | 3/8 | 4
SM393707A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 212 | 3/4 | 3/8 | 4
SM393710A | S Series | 5-speed high eff. ECM motor | Upflow | M3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 213 | 3/4 | 3/8 | 4
SM511800A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 218 | 3/4 | 3/8 | 4
SM511805A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 219 | 3/4 | 3/8 | 4
SM511807A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 220 | 3/4 | 3/8 | 4
SM511810A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 221 | 3/4 | 3/8 | 4
SM511900A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 222 | 3/4 | 3/8 | 4
SM511905A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 223 | 3/4 | 3/8 | 4
SM511907A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 224 | 3/4 | 3/8 | 4
SM511910A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 225 | 3/4 | 3/8 | 4
SM512400A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 226 | 3/4 | 3/8 | 4
SM512405A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 227 | 3/4 | 3/8 | 4
SM512407A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 228 | 3/4 | 3/8 | 4
SM512410A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 229 | 3/4 | 3/8 | 4
SM512500A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 230 | 3/4 | 3/8 | 4
SM512505A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 231 | 3/4 | 3/8 | 4
SM512507A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 232 | 3/4 | 3/8 | 4
SM512510A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 233 | 3/4 | 3/8 | 4
SM513000A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 234 | 3/4 | 3/8 | 4
SM513005A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 235 | 3/4 | 3/8 | 4
SM513007A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 236 | 3/4 | 3/8 | 4
SM513010A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 237 | 3/4 | 3/8 | 4
SM513100A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 238 | 3/4 | 3/8 | 4
SM513105A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 239 | 3/4 | 3/8 | 4
SM513107A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 240 | 3/4 | 3/8 | 4
SM513110A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 241 | 3/4 | 3/8 | 4
SM513600A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 242 | 3/4 | 3/8 | 4
SM513605A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 243 | 3/4 | 3/8 | 4
SM513607A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 244 | 3/4 | 3/8 | 4
SM513610A | S Series | 3-speed PSC motor | Upflow | M5 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 245 | 3/4 | 3/8 | 4
SM513700A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 246 | 3/4 | 3/8 | 4
SM513705A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 247 | 3/4 | 3/8 | 4
SM513707A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 248 | 3/4 | 3/8 | 4
SM513710A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 249 | 3/4 | 3/8 | 4
SM571800A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 254 | 3/4 | 3/8 | 4
SM571805A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 255 | 3/4 | 3/8 | 4
SM571807A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 256 | 3/4 | 3/8 | 4
SM571810A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 257 | 3/4 | 3/8 | 4
SM571900A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 258 | 3/4 | 3/8 | 4
SM571905A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 259 | 3/4 | 3/8 | 4
SM571907A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 260 | 3/4 | 3/8 | 4
SM571910A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 261 | 3/4 | 3/8 | 4
SM572400A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 262 | 3/4 | 3/8 | 4
SM572405A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 263 | 3/4 | 3/8 | 4
SM572407A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 264 | 3/4 | 3/8 | 4
SM572410A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 265 | 3/4 | 3/8 | 4
SM572500A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 266 | 3/4 | 3/8 | 4
SM572505A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 267 | 3/4 | 3/8 | 4
SM572507A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 268 | 3/4 | 3/8 | 4
SM572510A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 269 | 3/4 | 3/8 | 4
SM573000A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 270 | 3/4 | 3/8 | 4
SM573005A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 271 | 3/4 | 3/8 | 4
SM573007A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 272 | 3/4 | 3/8 | 4
SM573010A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 273 | 3/4 | 3/8 | 4
SM573100A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 274 | 3/4 | 3/8 | 4
SM573105A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 275 | 3/4 | 3/8 | 4
SM573107A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 276 | 3/4 | 3/8 | 4
SM573110A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 277 | 3/4 | 3/8 | 4
SM573600A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 278 | 3/4 | 3/8 | 4
SM573605A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 279 | 3/4 | 3/8 | 4
SM573607A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 280 | 3/4 | 3/8 | 4
SM573610A | S Series | 3-speed PSC motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 281 | 3/4 | 3/8 | 4
SM573700A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 282 | 3/4 | 3/8 | 4
SM573705A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 283 | 3/4 | 3/8 | 4
SM573707A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 284 | 3/4 | 3/8 | 4
SM573710A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 285 | 3/4 | 3/8 | 4
SM591800A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 290 | 3/4 | 3/8 | 4
SM591805A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 291 | 3/4 | 3/8 | 4
SM591807A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 292 | 3/4 | 3/8 | 4
SM591810A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 293 | 3/4 | 3/8 | 4
SM591900A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 294 | 3/4 | 3/8 | 4
SM591905A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 295 | 3/4 | 3/8 | 4
SM591907A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 296 | 3/4 | 3/8 | 4
SM591910A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 297 | 3/4 | 3/8 | 4
SM592400A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 298 | 3/4 | 3/8 | 4
SM592405A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 299 | 3/4 | 3/8 | 4
SM592407A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 300 | 3/4 | 3/8 | 4
SM592410A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 301 | 3/4 | 3/8 | 4
SM592500A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 302 | 3/4 | 3/8 | 4
SM592505A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 303 | 3/4 | 3/8 | 4
SM592507A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 304 | 3/4 | 3/8 | 4
SM592510A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 305 | 3/4 | 3/8 | 4
SM593000A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 306 | 3/4 | 3/8 | 4
SM593005A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 307 | 3/4 | 3/8 | 4
SM593007A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 308 | 3/4 | 3/8 | 4
SM593010A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 309 | 3/4 | 3/8 | 4
SM593100A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 310 | 3/4 | 3/8 | 4
SM593105A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 311 | 3/4 | 3/8 | 4
SM593107A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 312 | 3/4 | 3/8 | 4
SM593110A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 313 | 3/4 | 3/8 | 4
SM593600A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 314 | 3/4 | 3/8 | 4
SM593605A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 315 | 3/4 | 3/8 | 4
SM593607A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 316 | 3/4 | 3/8 | 4
SM593610A | S Series | 3-speed PSC motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 317 | 3/4 | 3/8 | 4
SM593700A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 318 | 3/4 | 3/8 | 4
SM593705A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 319 | 3/4 | 3/8 | 4
SM593707A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 320 | 3/4 | 3/8 | 4
SM593710A | S Series | 5-speed high eff. ECM motor | Upflow | M5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 321 | 3/4 | 3/8 | 4
SM611800A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 326 | 3/4 | 3/8 | 4
SM611805A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 327 | 3/4 | 3/8 | 4
SM611807A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 328 | 3/4 | 3/8 | 4
SM611810A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 329 | 3/4 | 3/8 | 4
SM611900A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 330 | 3/4 | 3/8 | 4
SM611905A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 331 | 3/4 | 3/8 | 4
SM611907A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 332 | 3/4 | 3/8 | 4
SM611910A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 333 | 3/4 | 3/8 | 4
SM612400A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 334 | 3/4 | 3/8 | 4
SM612405A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 335 | 3/4 | 3/8 | 4
SM612407A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 336 | 3/4 | 3/8 | 4
SM612410A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 337 | 3/4 | 3/8 | 4
SM612500A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 338 | 3/4 | 3/8 | 4
SM612505A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 339 | 3/4 | 3/8 | 4
SM612507A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 340 | 3/4 | 3/8 | 4
SM612510A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 341 | 3/4 | 3/8 | 4
SM613000A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 342 | 3/4 | 3/8 | 4
SM613005A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 343 | 3/4 | 3/8 | 4
SM613007A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 344 | 3/4 | 3/8 | 4
SM613010A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 345 | 3/4 | 3/8 | 4
SM613100A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 346 | 3/4 | 3/8 | 4
SM613105A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 347 | 3/4 | 3/8 | 4
SM613107A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 348 | 3/4 | 3/8 | 4
SM613110A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 349 | 3/4 | 3/8 | 4
SM613600A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 350 | 3/4 | 3/8 | 4
SM613605A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 351 | 3/4 | 3/8 | 4
SM613607A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 352 | 3/4 | 3/8 | 4
SM613610A | S Series | 3-speed PSC motor | Upflow | M6 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 353 | 3/4 | 3/8 | 4
SM613700A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 354 | 3/4 | 3/8 | 4
SM613705A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 355 | 3/4 | 3/8 | 4
SM613707A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 356 | 3/4 | 3/8 | 4
SM613710A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 357 | 3/4 | 3/8 | 4
SM671800A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 362 | 3/4 | 3/8 | 4
SM671805A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 363 | 3/4 | 3/8 | 4
SM671807A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 364 | 3/4 | 3/8 | 4
SM671810A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 365 | 3/4 | 3/8 | 4
SM671900A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 366 | 3/4 | 3/8 | 4
SM671905A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 367 | 3/4 | 3/8 | 4
SM671907A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 368 | 3/4 | 3/8 | 4
SM671910A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 369 | 3/4 | 3/8 | 4
SM672400A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 370 | 3/4 | 3/8 | 4
SM672405A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 371 | 3/4 | 3/8 | 4
SM672407A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 372 | 3/4 | 3/8 | 4
SM672410A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 373 | 3/4 | 3/8 | 4
SM672500A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 374 | 3/4 | 3/8 | 4
SM672505A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 375 | 3/4 | 3/8 | 4
SM672507A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 376 | 3/4 | 3/8 | 4
SM672510A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 377 | 3/4 | 3/8 | 4
SM673000A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 378 | 3/4 | 3/8 | 4
SM673005A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 379 | 3/4 | 3/8 | 4
SM673007A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 380 | 3/4 | 3/8 | 4
SM673010A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 381 | 3/4 | 3/8 | 4
SM673100A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 382 | 3/4 | 3/8 | 4
SM673105A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 383 | 3/4 | 3/8 | 4
SM673107A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 384 | 3/4 | 3/8 | 4
SM673110A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 385 | 3/4 | 3/8 | 4
SM673600A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 386 | 3/4 | 3/8 | 4
SM673605A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 387 | 3/4 | 3/8 | 4
SM673607A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 388 | 3/4 | 3/8 | 4
SM673610A | S Series | 3-speed PSC motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 389 | 3/4 | 3/8 | 4
SM673700A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 390 | 3/4 | 3/8 | 4
SM673705A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 391 | 3/4 | 3/8 | 4
SM673707A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 392 | 3/4 | 3/8 | 4
SM673710A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 393 | 3/4 | 3/8 | 4
SM691800A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 398 | 3/4 | 3/8 | 4
SM691805A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 399 | 3/4 | 3/8 | 4
SM691807A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 400 | 3/4 | 3/8 | 4
SM691810A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 401 | 3/4 | 3/8 | 4
SM691900A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 402 | 3/4 | 3/8 | 4
SM691905A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 403 | 3/4 | 3/8 | 4
SM691907A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 404 | 3/4 | 3/8 | 4
SM691910A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 405 | 3/4 | 3/8 | 4
SM692400A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 406 | 3/4 | 3/8 | 4
SM692405A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 407 | 3/4 | 3/8 | 4
SM692407A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 408 | 3/4 | 3/8 | 4
SM692410A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 409 | 3/4 | 3/8 | 4
SM692500A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 410 | 3/4 | 3/8 | 4
SM692505A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 411 | 3/4 | 3/8 | 4
SM692507A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 412 | 3/4 | 3/8 | 4
SM692510A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 413 | 3/4 | 3/8 | 4
SM693000A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 414 | 3/4 | 3/8 | 4
SM693005A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 415 | 3/4 | 3/8 | 4
SM693007A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 416 | 3/4 | 3/8 | 4
SM693010A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 417 | 3/4 | 3/8 | 4
SM693100A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 418 | 3/4 | 3/8 | 4
SM693105A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 419 | 3/4 | 3/8 | 4
SM693107A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 420 | 3/4 | 3/8 | 4
SM693110A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 421 | 3/4 | 3/8 | 4
SM693600A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 422 | 3/4 | 3/8 | 4
SM693605A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 423 | 3/4 | 3/8 | 4
SM693607A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 424 | 3/4 | 3/8 | 4
SM693610A | S Series | 3-speed PSC motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 425 | 3/4 | 3/8 | 4
SM693700A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 426 | 3/4 | 3/8 | 4
SM693705A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 427 | 3/4 | 3/8 | 4
SM693707A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 428 | 3/4 | 3/8 | 4
SM693710A | S Series | 5-speed high eff. ECM motor | Upflow | M6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 429 | 3/4 | 3/8 | 4
SM711800A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 434 | 3/4 | 3/8 | 4
SM711805A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 435 | 3/4 | 3/8 | 4
SM711807A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 436 | 3/4 | 3/8 | 4
SM711810A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 437 | 3/4 | 3/8 | 4
SM711900A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 438 | 3/4 | 3/8 | 4
SM711905A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 439 | 3/4 | 3/8 | 4
SM711907A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 440 | 3/4 | 3/8 | 4
SM711910A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 441 | 3/4 | 3/8 | 4
SM712400A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 442 | 3/4 | 3/8 | 4
SM712405A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 443 | 3/4 | 3/8 | 4
SM712407A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 444 | 3/4 | 3/8 | 4
SM712410A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 445 | 3/4 | 3/8 | 4
SM712500A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 446 | 3/4 | 3/8 | 4
SM712505A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 447 | 3/4 | 3/8 | 4
SM712507A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 448 | 3/4 | 3/8 | 4
SM712510A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 449 | 3/4 | 3/8 | 4
SM713000A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 450 | 3/4 | 3/8 | 4
SM713005A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 451 | 3/4 | 3/8 | 4
SM713007A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 452 | 3/4 | 3/8 | 4
SM713010A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 453 | 3/4 | 3/8 | 4
SM713100A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 454 | 3/4 | 3/8 | 4
SM713105A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 455 | 3/4 | 3/8 | 4
SM713107A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 456 | 3/4 | 3/8 | 4
SM713110A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 457 | 3/4 | 3/8 | 4
SM713600A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 458 | 3/4 | 3/8 | 4
SM713605A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 459 | 3/4 | 3/8 | 4
SM713607A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 460 | 3/4 | 3/8 | 4
SM713610A | S Series | 3-speed PSC motor | Upflow | M7 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 461 | 3/4 | 3/8 | 4
SM713700A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 462 | 3/4 | 3/8 | 4
SM713705A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 463 | 3/4 | 3/8 | 4
SM713707A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 464 | 3/4 | 3/8 | 4
SM713710A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 465 | 3/4 | 3/8 | 4
SM771800A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 470 | 3/4 | 3/8 | 4
SM771805A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 471 | 3/4 | 3/8 | 4
SM771807A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 472 | 3/4 | 3/8 | 4
SM771810A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 473 | 3/4 | 3/8 | 4
SM771900A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 474 | 3/4 | 3/8 | 4
SM771905A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 475 | 3/4 | 3/8 | 4
SM771907A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 476 | 3/4 | 3/8 | 4
SM771910A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 477 | 3/4 | 3/8 | 4
SM772400A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 478 | 3/4 | 3/8 | 4
SM772405A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 479 | 3/4 | 3/8 | 4
SM772407A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 480 | 3/4 | 3/8 | 4
SM772410A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 481 | 3/4 | 3/8 | 4
SM772500A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 482 | 3/4 | 3/8 | 4
SM772505A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 483 | 3/4 | 3/8 | 4
SM772507A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 484 | 3/4 | 3/8 | 4
SM772510A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 485 | 3/4 | 3/8 | 4
SM773000A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 486 | 3/4 | 3/8 | 4
SM773005A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 487 | 3/4 | 3/8 | 4
SM773007A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 488 | 3/4 | 3/8 | 4
SM773010A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 489 | 3/4 | 3/8 | 4
SM773100A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 490 | 3/4 | 3/8 | 4
SM773105A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 491 | 3/4 | 3/8 | 4
SM773107A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 492 | 3/4 | 3/8 | 4
SM773110A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 493 | 3/4 | 3/8 | 4
SM773600A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 494 | 3/4 | 3/8 | 4
SM773605A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 495 | 3/4 | 3/8 | 4
SM773607A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 496 | 3/4 | 3/8 | 4
SM773610A | S Series | 3-speed PSC motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 497 | 3/4 | 3/8 | 4
SM773700A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 498 | 3/4 | 3/8 | 4
SM773705A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 499 | 3/4 | 3/8 | 4
SM773707A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 500 | 3/4 | 3/8 | 4
SM773710A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 501 | 3/4 | 3/8 | 4
SM791800A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 506 | 3/4 | 3/8 | 4
SM791805A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 507 | 3/4 | 3/8 | 4
SM791807A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 508 | 3/4 | 3/8 | 4
SM791810A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 509 | 3/4 | 3/8 | 4
SM791900A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 510 | 3/4 | 3/8 | 4
SM791905A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 511 | 3/4 | 3/8 | 4
SM791907A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 512 | 3/4 | 3/8 | 4
SM791910A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 513 | 3/4 | 3/8 | 4
SM792400A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 514 | 3/4 | 3/8 | 4
SM792405A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 515 | 3/4 | 3/8 | 4
SM792407A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 516 | 3/4 | 3/8 | 4
SM792410A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 517 | 3/4 | 3/8 | 4
SM792500A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 518 | 3/4 | 3/8 | 4
SM792505A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 519 | 3/4 | 3/8 | 4
SM792507A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 520 | 3/4 | 3/8 | 4
SM792510A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 521 | 3/4 | 3/8 | 4
SM793000A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 522 | 3/4 | 3/8 | 4
SM793005A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 523 | 3/4 | 3/8 | 4
SM793007A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 524 | 3/4 | 3/8 | 4
SM793010A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 525 | 3/4 | 3/8 | 4
SM793100A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 526 | 3/4 | 3/8 | 4
SM793105A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 527 | 3/4 | 3/8 | 4
SM793107A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 528 | 3/4 | 3/8 | 4
SM793110A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 529 | 3/4 | 3/8 | 4
SM793600A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 530 | 3/4 | 3/8 | 4
SM793605A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 531 | 3/4 | 3/8 | 4
SM793607A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 532 | 3/4 | 3/8 | 4
SM793610A | S Series | 3-speed PSC motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 76 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 533 | 3/4 | 3/8 | 4
SM793700A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 534 | 3/4 | 3/8 | 4
SM793705A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 535 | 3/4 | 3/8 | 4
SM793707A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 536 | 3/4 | 3/8 | 4
SM793710A | S Series | 5-speed high eff. ECM motor | Upflow | M7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 79 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 537 | 3/4 | 3/8 | 4
SK111800A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 650 | 3/4 | 3/8 | 4
SK111805A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 651 | 3/4 | 3/8 | 4
SK111807A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 652 | 3/4 | 3/8 | 4
SK111810A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 653 | 3/4 | 3/8 | 4
SK111900A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 654 | 3/4 | 3/8 | 4
SK111905A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 655 | 3/4 | 3/8 | 4
SK111907A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 656 | 3/4 | 3/8 | 4
SK111910A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 657 | 3/4 | 3/8 | 4
SK112400A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 658 | 3/4 | 3/8 | 4
SK112405A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 659 | 3/4 | 3/8 | 4
SK112407A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 660 | 3/4 | 3/8 | 4
SK112410A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 661 | 3/4 | 3/8 | 4
SK112500A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 662 | 3/4 | 3/8 | 4
SK112505A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 663 | 3/4 | 3/8 | 4
SK112507A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 664 | 3/4 | 3/8 | 4
SK112510A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 665 | 3/4 | 3/8 | 4
SK113000A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 666 | 3/4 | 3/8 | 4
SK113005A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 667 | 3/4 | 3/8 | 4
SK113007A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 668 | 3/4 | 3/8 | 4
SK113010A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 669 | 3/4 | 3/8 | 4
SK113100A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 670 | 3/4 | 3/8 | 4
SK113105A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 671 | 3/4 | 3/8 | 4
SK113107A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 672 | 3/4 | 3/8 | 4
SK113110A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 673 | 3/4 | 3/8 | 4
SK113600A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 674 | 3/4 | 3/8 | 4
SK113605A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 675 | 3/4 | 3/8 | 4
SK113607A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 676 | 3/4 | 3/8 | 4
SK113610A | S Series | 3-speed PSC motor | Upflow | K1 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 677 | 3/4 | 3/8 | 4
SK113700A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 678 | 3/4 | 3/8 | 4
SK113705A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 679 | 3/4 | 3/8 | 4
SK113707A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 680 | 3/4 | 3/8 | 4
SK113710A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 681 | 3/4 | 3/8 | 4
SK113900A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 682 | 3/4 | 3/8 | 4
SK113905A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 683 | 3/4 | 3/8 | 4
SK113907A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 684 | 3/4 | 3/8 | 4
SK113910A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 685 | 3/4 | 3/8 | 4
SK171800A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 686 | 3/4 | 3/8 | 4
SK171805A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 687 | 3/4 | 3/8 | 4
SK171807A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 688 | 3/4 | 3/8 | 4
SK171810A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 689 | 3/4 | 3/8 | 4
SK171900A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 690 | 3/4 | 3/8 | 4
SK171905A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 691 | 3/4 | 3/8 | 4
SK171907A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 692 | 3/4 | 3/8 | 4
SK171910A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 693 | 3/4 | 3/8 | 4
SK172400A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 694 | 3/4 | 3/8 | 4
SK172405A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 695 | 3/4 | 3/8 | 4
SK172407A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 696 | 3/4 | 3/8 | 4
SK172410A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 697 | 3/4 | 3/8 | 4
SK172500A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 698 | 3/4 | 3/8 | 4
SK172505A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 699 | 3/4 | 3/8 | 4
SK172507A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 700 | 3/4 | 3/8 | 4
SK172510A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 701 | 3/4 | 3/8 | 4
SK173000A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 702 | 3/4 | 3/8 | 4
SK173005A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 703 | 3/4 | 3/8 | 4
SK173007A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 704 | 3/4 | 3/8 | 4
SK173010A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 705 | 3/4 | 3/8 | 4
SK173100A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 706 | 3/4 | 3/8 | 4
SK173105A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 707 | 3/4 | 3/8 | 4
SK173107A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 708 | 3/4 | 3/8 | 4
SK173110A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 709 | 3/4 | 3/8 | 4
SK173600A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 710 | 3/4 | 3/8 | 4
SK173605A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 711 | 3/4 | 3/8 | 4
SK173607A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 712 | 3/4 | 3/8 | 4
SK173610A | S Series | 3-speed PSC motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 713 | 3/4 | 3/8 | 4
SK173700A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 714 | 3/4 | 3/8 | 4
SK173705A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 715 | 3/4 | 3/8 | 4
SK173707A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 716 | 3/4 | 3/8 | 4
SK173710A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 717 | 3/4 | 3/8 | 4
SK173900A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 718 | 3/4 | 3/8 | 4
SK173905A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 719 | 3/4 | 3/8 | 4
SK173907A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 720 | 3/4 | 3/8 | 4
SK173910A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 721 | 3/4 | 3/8 | 4
SK191800A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 722 | 3/4 | 3/8 | 4
SK191805A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 723 | 3/4 | 3/8 | 4
SK191807A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 724 | 3/4 | 3/8 | 4
SK191810A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 725 | 3/4 | 3/8 | 4
SK191900A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 726 | 3/4 | 3/8 | 4
SK191905A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 727 | 3/4 | 3/8 | 4
SK191907A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 728 | 3/4 | 3/8 | 4
SK191910A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 729 | 3/4 | 3/8 | 4
SK192400A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 730 | 3/4 | 3/8 | 4
SK192405A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 731 | 3/4 | 3/8 | 4
SK192407A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 732 | 3/4 | 3/8 | 4
SK192410A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 733 | 3/4 | 3/8 | 4
SK192500A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 734 | 3/4 | 3/8 | 4
SK192505A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 735 | 3/4 | 3/8 | 4
SK192507A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 736 | 3/4 | 3/8 | 4
SK192510A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 737 | 3/4 | 3/8 | 4
SK193000A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 738 | 3/4 | 3/8 | 4
SK193005A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 739 | 3/4 | 3/8 | 4
SK193007A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 740 | 3/4 | 3/8 | 4
SK193010A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 741 | 3/4 | 3/8 | 4
SK193100A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 742 | 3/4 | 3/8 | 4
SK193105A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 743 | 3/4 | 3/8 | 4
SK193107A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 744 | 3/4 | 3/8 | 4
SK193110A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 745 | 3/4 | 3/8 | 4
SK193600A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 746 | 3/4 | 3/8 | 4
SK193605A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 747 | 3/4 | 3/8 | 4
SK193607A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 748 | 3/4 | 3/8 | 4
SK193610A | S Series | 3-speed PSC motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 749 | 3/4 | 3/8 | 4
SK193700A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 750 | 3/4 | 3/8 | 4
SK193705A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 751 | 3/4 | 3/8 | 4
SK193707A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 752 | 3/4 | 3/8 | 4
SK193710A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 753 | 3/4 | 3/8 | 4
SK193900A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 754 | 3/4 | 3/8 | 4
SK193905A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 755 | 3/4 | 3/8 | 4
SK193907A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 756 | 3/4 | 3/8 | 4
SK193910A | S Series | 5-speed high eff. ECM motor | Upflow | K1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 757 | 3/4 | 3/8 | 4
SK211800A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 758 | 3/4 | 3/8 | 4
SK211805A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 759 | 3/4 | 3/8 | 4
SK211807A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 760 | 3/4 | 3/8 | 4
SK211810A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 761 | 3/4 | 3/8 | 4
SK211900A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 762 | 3/4 | 3/8 | 4
SK211905A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 763 | 3/4 | 3/8 | 4
SK211907A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 764 | 3/4 | 3/8 | 4
SK211910A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 765 | 3/4 | 3/8 | 4
SK212400A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 766 | 3/4 | 3/8 | 4
SK212405A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 767 | 3/4 | 3/8 | 4
SK212407A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 768 | 3/4 | 3/8 | 4
SK212410A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 769 | 3/4 | 3/8 | 4
SK212500A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 770 | 3/4 | 3/8 | 4
SK212505A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 771 | 3/4 | 3/8 | 4
SK212507A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 772 | 3/4 | 3/8 | 4
SK212510A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 773 | 3/4 | 3/8 | 4
SK213000A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 774 | 3/4 | 3/8 | 4
SK213005A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 775 | 3/4 | 3/8 | 4
SK213007A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 776 | 3/4 | 3/8 | 4
SK213010A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 777 | 3/4 | 3/8 | 4
SK213100A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 778 | 3/4 | 3/8 | 4
SK213105A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 779 | 3/4 | 3/8 | 4
SK213107A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 780 | 3/4 | 3/8 | 4
SK213110A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 781 | 3/4 | 3/8 | 4
SK213600A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 782 | 3/4 | 3/8 | 4
SK213605A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 783 | 3/4 | 3/8 | 4
SK213607A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 784 | 3/4 | 3/8 | 4
SK213610A | S Series | 3-speed PSC motor | Upflow | K2 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 785 | 3/4 | 3/8 | 4
SK213700A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 786 | 3/4 | 3/8 | 4
SK213705A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 787 | 3/4 | 3/8 | 4
SK213707A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 788 | 3/4 | 3/8 | 4
SK213710A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 789 | 3/4 | 3/8 | 4
SK213900A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 790 | 3/4 | 3/8 | 4
SK213905A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 791 | 3/4 | 3/8 | 4
SK213907A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 792 | 3/4 | 3/8 | 4
SK213910A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 793 | 3/4 | 3/8 | 4
SK271800A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 794 | 3/4 | 3/8 | 4
SK271805A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 795 | 3/4 | 3/8 | 4
SK271807A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 796 | 3/4 | 3/8 | 4
SK271810A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 797 | 3/4 | 3/8 | 4
SK271900A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 798 | 3/4 | 3/8 | 4
SK271905A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 799 | 3/4 | 3/8 | 4
SK271907A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 800 | 3/4 | 3/8 | 4
SK271910A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 801 | 3/4 | 3/8 | 4
SK272400A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 802 | 3/4 | 3/8 | 4
SK272405A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 803 | 3/4 | 3/8 | 4
SK272407A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 804 | 3/4 | 3/8 | 4
SK272410A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 805 | 3/4 | 3/8 | 4
SK272500A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 806 | 3/4 | 3/8 | 4
SK272505A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 807 | 3/4 | 3/8 | 4
SK272507A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 808 | 3/4 | 3/8 | 4
SK272510A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 809 | 3/4 | 3/8 | 4
SK273000A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 810 | 3/4 | 3/8 | 4
SK273005A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 811 | 3/4 | 3/8 | 4
SK273007A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 812 | 3/4 | 3/8 | 4
SK273010A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 813 | 3/4 | 3/8 | 4
SK273100A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 814 | 3/4 | 3/8 | 4
SK273105A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 815 | 3/4 | 3/8 | 4
SK273107A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 816 | 3/4 | 3/8 | 4
SK273110A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 817 | 3/4 | 3/8 | 4
SK273600A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 818 | 3/4 | 3/8 | 4
SK273605A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 819 | 3/4 | 3/8 | 4
SK273607A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 820 | 3/4 | 3/8 | 4
SK273610A | S Series | 3-speed PSC motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 821 | 3/4 | 3/8 | 4
SK273700A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 822 | 3/4 | 3/8 | 4
SK273705A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 823 | 3/4 | 3/8 | 4
SK273707A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 824 | 3/4 | 3/8 | 4
SK273710A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 825 | 3/4 | 3/8 | 4
SK273900A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 826 | 3/4 | 3/8 | 4
SK273905A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 827 | 3/4 | 3/8 | 4
SK273907A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 828 | 3/4 | 3/8 | 4
SK273910A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 829 | 3/4 | 3/8 | 4
SK291800A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 830 | 3/4 | 3/8 | 4
SK291805A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 831 | 3/4 | 3/8 | 4
SK291807A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 832 | 3/4 | 3/8 | 4
SK291810A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 833 | 3/4 | 3/8 | 4
SK291900A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 834 | 3/4 | 3/8 | 4
SK291905A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 835 | 3/4 | 3/8 | 4
SK291907A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 836 | 3/4 | 3/8 | 4
SK291910A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 837 | 3/4 | 3/8 | 4
SK292400A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 838 | 3/4 | 3/8 | 4
SK292405A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 839 | 3/4 | 3/8 | 4
SK292407A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 840 | 3/4 | 3/8 | 4
SK292410A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 841 | 3/4 | 3/8 | 4
SK292500A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 842 | 3/4 | 3/8 | 4
SK292505A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 843 | 3/4 | 3/8 | 4
SK292507A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 844 | 3/4 | 3/8 | 4
SK292510A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 845 | 3/4 | 3/8 | 4
SK293000A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 846 | 3/4 | 3/8 | 4
SK293005A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 847 | 3/4 | 3/8 | 4
SK293007A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 848 | 3/4 | 3/8 | 4
SK293010A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 849 | 3/4 | 3/8 | 4
SK293100A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 850 | 3/4 | 3/8 | 4
SK293105A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 851 | 3/4 | 3/8 | 4
SK293107A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 852 | 3/4 | 3/8 | 4
SK293110A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 853 | 3/4 | 3/8 | 4
SK293600A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 854 | 3/4 | 3/8 | 4
SK293605A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 855 | 3/4 | 3/8 | 4
SK293607A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 856 | 3/4 | 3/8 | 4
SK293610A | S Series | 3-speed PSC motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 857 | 3/4 | 3/8 | 4
SK293700A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 858 | 3/4 | 3/8 | 4
SK293705A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 859 | 3/4 | 3/8 | 4
SK293707A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 860 | 3/4 | 3/8 | 4
SK293710A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 861 | 3/4 | 3/8 | 4
SK293900A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 862 | 3/4 | 3/8 | 4
SK293905A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 863 | 3/4 | 3/8 | 4
SK293907A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 864 | 3/4 | 3/8 | 4
SK293910A | S Series | 5-speed high eff. ECM motor | Upflow | K2 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 865 | 3/4 | 3/8 | 4
SK311800A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 866 | 3/4 | 3/8 | 4
SK311805A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 867 | 3/4 | 3/8 | 4
SK311807A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 868 | 3/4 | 3/8 | 4
SK311810A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 869 | 3/4 | 3/8 | 4
SK311900A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 870 | 3/4 | 3/8 | 4
SK311905A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 871 | 3/4 | 3/8 | 4
SK311907A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 872 | 3/4 | 3/8 | 4
SK311910A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 873 | 3/4 | 3/8 | 4
SK312400A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 874 | 3/4 | 3/8 | 4
SK312405A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 875 | 3/4 | 3/8 | 4
SK312407A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 876 | 3/4 | 3/8 | 4
SK312410A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 877 | 3/4 | 3/8 | 4
SK312500A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 878 | 3/4 | 3/8 | 4
SK312505A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 879 | 3/4 | 3/8 | 4
SK312507A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 880 | 3/4 | 3/8 | 4
SK312510A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 881 | 3/4 | 3/8 | 4
SK313000A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 882 | 3/4 | 3/8 | 4
SK313005A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 883 | 3/4 | 3/8 | 4
SK313007A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 884 | 3/4 | 3/8 | 4
SK313010A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 885 | 3/4 | 3/8 | 4
SK313100A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 886 | 3/4 | 3/8 | 4
SK313105A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 887 | 3/4 | 3/8 | 4
SK313107A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 888 | 3/4 | 3/8 | 4
SK313110A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 889 | 3/4 | 3/8 | 4
SK313600A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 890 | 3/4 | 3/8 | 4
SK313605A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 891 | 3/4 | 3/8 | 4
SK313607A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 892 | 3/4 | 3/8 | 4
SK313610A | S Series | 3-speed PSC motor | Upflow | K3 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 893 | 3/4 | 3/8 | 4
SK313700A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 894 | 3/4 | 3/8 | 4
SK313705A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 895 | 3/4 | 3/8 | 4
SK313707A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 896 | 3/4 | 3/8 | 4
SK313710A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 897 | 3/4 | 3/8 | 4
SK313900A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 898 | 3/4 | 3/8 | 4
SK313905A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 899 | 3/4 | 3/8 | 4
SK313907A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 900 | 3/4 | 3/8 | 4
SK313910A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 901 | 3/4 | 3/8 | 4
SK371800A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 902 | 3/4 | 3/8 | 4
SK371805A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 903 | 3/4 | 3/8 | 4
SK371807A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 904 | 3/4 | 3/8 | 4
SK371810A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 905 | 3/4 | 3/8 | 4
SK371900A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 906 | 3/4 | 3/8 | 4
SK371905A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 907 | 3/4 | 3/8 | 4
SK371907A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 908 | 3/4 | 3/8 | 4
SK371910A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 909 | 3/4 | 3/8 | 4
SK372400A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 910 | 3/4 | 3/8 | 4
SK372405A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 911 | 3/4 | 3/8 | 4
SK372407A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 912 | 3/4 | 3/8 | 4
SK372410A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 913 | 3/4 | 3/8 | 4
SK372500A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 914 | 3/4 | 3/8 | 4
SK372505A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 915 | 3/4 | 3/8 | 4
SK372507A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 916 | 3/4 | 3/8 | 4
SK372510A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 917 | 3/4 | 3/8 | 4
SK373000A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 918 | 3/4 | 3/8 | 4
SK373005A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 919 | 3/4 | 3/8 | 4
SK373007A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 920 | 3/4 | 3/8 | 4
SK373010A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 921 | 3/4 | 3/8 | 4
SK373100A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 922 | 3/4 | 3/8 | 4
SK373105A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 923 | 3/4 | 3/8 | 4
SK373107A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 924 | 3/4 | 3/8 | 4
SK373110A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 925 | 3/4 | 3/8 | 4
SK373600A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 926 | 3/4 | 3/8 | 4
SK373605A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 927 | 3/4 | 3/8 | 4
SK373607A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 928 | 3/4 | 3/8 | 4
SK373610A | S Series | 3-speed PSC motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 929 | 3/4 | 3/8 | 4
SK373700A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 930 | 3/4 | 3/8 | 4
SK373705A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 931 | 3/4 | 3/8 | 4
SK373707A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 932 | 3/4 | 3/8 | 4
SK373710A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 933 | 3/4 | 3/8 | 4
SK373900A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 934 | 3/4 | 3/8 | 4
SK373905A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 935 | 3/4 | 3/8 | 4
SK373907A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 936 | 3/4 | 3/8 | 4
SK373910A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 937 | 3/4 | 3/8 | 4
SK391800A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 938 | 3/4 | 3/8 | 4
SK391805A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 939 | 3/4 | 3/8 | 4
SK391807A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 940 | 3/4 | 3/8 | 4
SK391810A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 941 | 3/4 | 3/8 | 4
SK391900A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 942 | 3/4 | 3/8 | 4
SK391905A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 943 | 3/4 | 3/8 | 4
SK391907A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 944 | 3/4 | 3/8 | 4
SK391910A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 945 | 3/4 | 3/8 | 4
SK392400A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 946 | 3/4 | 3/8 | 4
SK392405A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 947 | 3/4 | 3/8 | 4
SK392407A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 948 | 3/4 | 3/8 | 4
SK392410A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 949 | 3/4 | 3/8 | 4
SK392500A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 950 | 3/4 | 3/8 | 4
SK392505A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 951 | 3/4 | 3/8 | 4
SK392507A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 952 | 3/4 | 3/8 | 4
SK392510A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 953 | 3/4 | 3/8 | 4
SK393000A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 954 | 3/4 | 3/8 | 4
SK393005A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 955 | 3/4 | 3/8 | 4
SK393007A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 956 | 3/4 | 3/8 | 4
SK393010A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 957 | 3/4 | 3/8 | 4
SK393100A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 958 | 3/4 | 3/8 | 4
SK393105A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 959 | 3/4 | 3/8 | 4
SK393107A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 960 | 3/4 | 3/8 | 4
SK393110A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 961 | 3/4 | 3/8 | 4
SK393600A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 962 | 3/4 | 3/8 | 4
SK393605A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 963 | 3/4 | 3/8 | 4
SK393607A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 964 | 3/4 | 3/8 | 4
SK393610A | S Series | 3-speed PSC motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 965 | 3/4 | 3/8 | 4
SK393700A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 966 | 3/4 | 3/8 | 4
SK393705A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 967 | 3/4 | 3/8 | 4
SK393707A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 968 | 3/4 | 3/8 | 4
SK393710A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 969 | 3/4 | 3/8 | 4
SK393900A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 970 | 3/4 | 3/8 | 4
SK393905A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 971 | 3/4 | 3/8 | 4
SK393907A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 972 | 3/4 | 3/8 | 4
SK393910A | S Series | 5-speed high eff. ECM motor | Upflow | K3 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 973 | 3/4 | 3/8 | 4
SK611800A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1082 | 3/4 | 3/8 | 4
SK611805A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1083 | 3/4 | 3/8 | 4
SK611807A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1084 | 3/4 | 3/8 | 4
SK611810A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1085 | 3/4 | 3/8 | 4
SK611900A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1086 | 3/4 | 3/8 | 4
SK611905A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1087 | 3/4 | 3/8 | 4
SK611907A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1088 | 3/4 | 3/8 | 4
SK611910A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1089 | 3/4 | 3/8 | 4
SK612400A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1090 | 3/4 | 3/8 | 4
SK612405A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1091 | 3/4 | 3/8 | 4
SK612407A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1092 | 3/4 | 3/8 | 4
SK612410A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1093 | 3/4 | 3/8 | 4
SK612500A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1094 | 3/4 | 3/8 | 4
SK612505A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1095 | 3/4 | 3/8 | 4
SK612507A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1096 | 3/4 | 3/8 | 4
SK612510A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1097 | 3/4 | 3/8 | 4
SK613000A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1098 | 3/4 | 3/8 | 4
SK613005A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1099 | 3/4 | 3/8 | 4
SK613007A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1100 | 3/4 | 3/8 | 4
SK613010A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1101 | 3/4 | 3/8 | 4
SK613100A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1102 | 3/4 | 3/8 | 4
SK613105A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1103 | 3/4 | 3/8 | 4
SK613107A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1104 | 3/4 | 3/8 | 4
SK613110A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1105 | 3/4 | 3/8 | 4
SK613600A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1106 | 3/4 | 3/8 | 4
SK613605A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1107 | 3/4 | 3/8 | 4
SK613607A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1108 | 3/4 | 3/8 | 4
SK613610A | S Series | 3-speed PSC motor | Upflow | K6 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1109 | 3/4 | 3/8 | 4
SK613700A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1110 | 3/4 | 3/8 | 4
SK613705A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1111 | 3/4 | 3/8 | 4
SK613707A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1112 | 3/4 | 3/8 | 4
SK613710A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1113 | 3/4 | 3/8 | 4
SK613900A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1114 | 3/4 | 3/8 | 4
SK613905A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1115 | 3/4 | 3/8 | 4
SK613907A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1116 | 3/4 | 3/8 | 4
SK613910A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1117 | 3/4 | 3/8 | 4
SK671800A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1118 | 3/4 | 3/8 | 4
SK671805A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1119 | 3/4 | 3/8 | 4
SK671807A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1120 | 3/4 | 3/8 | 4
SK671810A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1121 | 3/4 | 3/8 | 4
SK671900A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1122 | 3/4 | 3/8 | 4
SK671905A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1123 | 3/4 | 3/8 | 4
SK671907A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1124 | 3/4 | 3/8 | 4
SK671910A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1125 | 3/4 | 3/8 | 4
SK672400A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1126 | 3/4 | 3/8 | 4
SK672405A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1127 | 3/4 | 3/8 | 4
SK672407A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1128 | 3/4 | 3/8 | 4
SK672410A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1129 | 3/4 | 3/8 | 4
SK672500A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1130 | 3/4 | 3/8 | 4
SK672505A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1131 | 3/4 | 3/8 | 4
SK672507A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1132 | 3/4 | 3/8 | 4
SK672510A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1133 | 3/4 | 3/8 | 4
SK673000A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1134 | 3/4 | 3/8 | 4
SK673005A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1135 | 3/4 | 3/8 | 4
SK673007A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1136 | 3/4 | 3/8 | 4
SK673010A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1137 | 3/4 | 3/8 | 4
SK673100A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1138 | 3/4 | 3/8 | 4
SK673105A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1139 | 3/4 | 3/8 | 4
SK673107A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1140 | 3/4 | 3/8 | 4
SK673110A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1141 | 3/4 | 3/8 | 4
SK673600A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1142 | 3/4 | 3/8 | 4
SK673605A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1143 | 3/4 | 3/8 | 4
SK673607A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1144 | 3/4 | 3/8 | 4
SK673610A | S Series | 3-speed PSC motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1145 | 3/4 | 3/8 | 4
SK673700A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1146 | 3/4 | 3/8 | 4
SK673705A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1147 | 3/4 | 3/8 | 4
SK673707A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1148 | 3/4 | 3/8 | 4
SK673710A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1149 | 3/4 | 3/8 | 4
SK673900A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1150 | 3/4 | 3/8 | 4
SK673905A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1151 | 3/4 | 3/8 | 4
SK673907A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1152 | 3/4 | 3/8 | 4
SK673910A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1153 | 3/4 | 3/8 | 4
SK691800A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1154 | 3/4 | 3/8 | 4
SK691805A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1155 | 3/4 | 3/8 | 4
SK691807A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1156 | 3/4 | 3/8 | 4
SK691810A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1157 | 3/4 | 3/8 | 4
SK691900A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1158 | 3/4 | 3/8 | 4
SK691905A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1159 | 3/4 | 3/8 | 4
SK691907A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1160 | 3/4 | 3/8 | 4
SK691910A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1161 | 3/4 | 3/8 | 4
SK692400A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1162 | 3/4 | 3/8 | 4
SK692405A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1163 | 3/4 | 3/8 | 4
SK692407A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1164 | 3/4 | 3/8 | 4
SK692410A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1165 | 3/4 | 3/8 | 4
SK692500A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1166 | 3/4 | 3/8 | 4
SK692505A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1167 | 3/4 | 3/8 | 4
SK692507A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1168 | 3/4 | 3/8 | 4
SK692510A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1169 | 3/4 | 3/8 | 4
SK693000A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1170 | 3/4 | 3/8 | 4
SK693005A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1171 | 3/4 | 3/8 | 4
SK693007A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1172 | 3/4 | 3/8 | 4
SK693010A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1173 | 3/4 | 3/8 | 4
SK693100A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1174 | 3/4 | 3/8 | 4
SK693105A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1175 | 3/4 | 3/8 | 4
SK693107A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1176 | 3/4 | 3/8 | 4
SK693110A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1177 | 3/4 | 3/8 | 4
SK693600A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1178 | 3/4 | 3/8 | 4
SK693605A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1179 | 3/4 | 3/8 | 4
SK693607A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1180 | 3/4 | 3/8 | 4
SK693610A | S Series | 3-speed PSC motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1181 | 3/4 | 3/8 | 4
SK693700A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1182 | 3/4 | 3/8 | 4
SK693705A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1183 | 3/4 | 3/8 | 4
SK693707A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1184 | 3/4 | 3/8 | 4
SK693710A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1185 | 3/4 | 3/8 | 4
SK693900A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1186 | 3/4 | 3/8 | 4
SK693905A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1187 | 3/4 | 3/8 | 4
SK693907A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1188 | 3/4 | 3/8 | 4
SK693910A | S Series | 5-speed high eff. ECM motor | Upflow | K6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1189 | 3/4 | 3/8 | 4
SK711800A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1190 | 3/4 | 3/8 | 4
SK711805A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1191 | 3/4 | 3/8 | 4
SK711807A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1192 | 3/4 | 3/8 | 4
SK711810A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1193 | 3/4 | 3/8 | 4
SK711900A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1194 | 3/4 | 3/8 | 4
SK711905A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1195 | 3/4 | 3/8 | 4
SK711907A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1196 | 3/4 | 3/8 | 4
SK711910A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1197 | 3/4 | 3/8 | 4
SK712400A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1198 | 3/4 | 3/8 | 4
SK712405A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1199 | 3/4 | 3/8 | 4
SK712407A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1200 | 3/4 | 3/8 | 4
SK712410A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1201 | 3/4 | 3/8 | 4
SK712500A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1202 | 3/4 | 3/8 | 4
SK712505A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1203 | 3/4 | 3/8 | 4
SK712507A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1204 | 3/4 | 3/8 | 4
SK712510A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1205 | 3/4 | 3/8 | 4
SK713000A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1206 | 3/4 | 3/8 | 4
SK713005A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1207 | 3/4 | 3/8 | 4
SK713007A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1208 | 3/4 | 3/8 | 4
SK713010A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1209 | 3/4 | 3/8 | 4
SK713100A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1210 | 3/4 | 3/8 | 4
SK713105A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1211 | 3/4 | 3/8 | 4
SK713107A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1212 | 3/4 | 3/8 | 4
SK713110A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1213 | 3/4 | 3/8 | 4
SK713600A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1214 | 3/4 | 3/8 | 4
SK713605A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1215 | 3/4 | 3/8 | 4
SK713607A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1216 | 3/4 | 3/8 | 4
SK713610A | S Series | 3-speed PSC motor | Upflow | K7 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1217 | 3/4 | 3/8 | 4
SK713700A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1218 | 3/4 | 3/8 | 4
SK713705A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1219 | 3/4 | 3/8 | 4
SK713707A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1220 | 3/4 | 3/8 | 4
SK713710A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1221 | 3/4 | 3/8 | 4
SK713900A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1222 | 3/4 | 3/8 | 4
SK713905A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1223 | 3/4 | 3/8 | 4
SK713907A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1224 | 3/4 | 3/8 | 4
SK713910A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1225 | 3/4 | 3/8 | 4
SK771800A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1226 | 3/4 | 3/8 | 4
SK771805A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1227 | 3/4 | 3/8 | 4
SK771807A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1228 | 3/4 | 3/8 | 4
SK771810A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1229 | 3/4 | 3/8 | 4
SK771900A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1230 | 3/4 | 3/8 | 4
SK771905A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1231 | 3/4 | 3/8 | 4
SK771907A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1232 | 3/4 | 3/8 | 4
SK771910A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1233 | 3/4 | 3/8 | 4
SK772400A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1234 | 3/4 | 3/8 | 4
SK772405A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1235 | 3/4 | 3/8 | 4
SK772407A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1236 | 3/4 | 3/8 | 4
SK772410A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1237 | 3/4 | 3/8 | 4
SK772500A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1238 | 3/4 | 3/8 | 4
SK772505A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1239 | 3/4 | 3/8 | 4
SK772507A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1240 | 3/4 | 3/8 | 4
SK772510A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1241 | 3/4 | 3/8 | 4
SK773000A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1242 | 3/4 | 3/8 | 4
SK773005A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1243 | 3/4 | 3/8 | 4
SK773007A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1244 | 3/4 | 3/8 | 4
SK773010A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1245 | 3/4 | 3/8 | 4
SK773100A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1246 | 3/4 | 3/8 | 4
SK773105A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1247 | 3/4 | 3/8 | 4
SK773107A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1248 | 3/4 | 3/8 | 4
SK773110A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1249 | 3/4 | 3/8 | 4
SK773600A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1250 | 3/4 | 3/8 | 4
SK773605A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1251 | 3/4 | 3/8 | 4
SK773607A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1252 | 3/4 | 3/8 | 4
SK773610A | S Series | 3-speed PSC motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1253 | 3/4 | 3/8 | 4
SK773700A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1254 | 3/4 | 3/8 | 4
SK773705A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1255 | 3/4 | 3/8 | 4
SK773707A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1256 | 3/4 | 3/8 | 4
SK773710A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1257 | 3/4 | 3/8 | 4
SK773900A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1258 | 3/4 | 3/8 | 4
SK773905A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1259 | 3/4 | 3/8 | 4
SK773907A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1260 | 3/4 | 3/8 | 4
SK773910A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1261 | 3/4 | 3/8 | 4
SK791800A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1262 | 3/4 | 3/8 | 4
SK791805A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1263 | 3/4 | 3/8 | 4
SK791807A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1264 | 3/4 | 3/8 | 4
SK791810A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1265 | 3/4 | 3/8 | 4
SK791900A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1266 | 3/4 | 3/8 | 4
SK791905A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1267 | 3/4 | 3/8 | 4
SK791907A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1268 | 3/4 | 3/8 | 4
SK791910A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1269 | 3/4 | 3/8 | 4
SK792400A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1270 | 3/4 | 3/8 | 4
SK792405A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1271 | 3/4 | 3/8 | 4
SK792407A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1272 | 3/4 | 3/8 | 4
SK792410A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1273 | 3/4 | 3/8 | 4
SK792500A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1274 | 3/4 | 3/8 | 4
SK792505A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1275 | 3/4 | 3/8 | 4
SK792507A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1276 | 3/4 | 3/8 | 4
SK792510A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1277 | 3/4 | 3/8 | 4
SK793000A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1278 | 3/4 | 3/8 | 4
SK793005A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1279 | 3/4 | 3/8 | 4
SK793007A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1280 | 3/4 | 3/8 | 4
SK793010A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1281 | 3/4 | 3/8 | 4
SK793100A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1282 | 3/4 | 3/8 | 4
SK793105A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1283 | 3/4 | 3/8 | 4
SK793107A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1284 | 3/4 | 3/8 | 4
SK793110A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1285 | 3/4 | 3/8 | 4
SK793600A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1286 | 3/4 | 3/8 | 4
SK793605A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1287 | 3/4 | 3/8 | 4
SK793607A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1288 | 3/4 | 3/8 | 4
SK793610A | S Series | 3-speed PSC motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1289 | 3/4 | 3/8 | 4
SK793700A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1290 | 3/4 | 3/8 | 4
SK793705A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1291 | 3/4 | 3/8 | 4
SK793707A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1292 | 3/4 | 3/8 | 4
SK793710A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1293 | 3/4 | 3/8 | 4
SK793900A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1294 | 3/4 | 3/8 | 4
SK793905A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1295 | 3/4 | 3/8 | 4
SK793907A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1296 | 3/4 | 3/8 | 4
SK793910A | S Series | 5-speed high eff. ECM motor | Upflow | K7 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1297 | 3/4 | 3/8 | 4
SL111800A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1406 | 3/4 | 3/8 | 4
SL111805A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1407 | 3/4 | 3/8 | 4
SL111807A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1408 | 3/4 | 3/8 | 4
SL111810A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1409 | 3/4 | 3/8 | 4
SL111900A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1410 | 3/4 | 3/8 | 4
SL111905A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1411 | 3/4 | 3/8 | 4
SL111907A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1412 | 3/4 | 3/8 | 4
SL111910A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1413 | 3/4 | 3/8 | 4
SL112400A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1414 | 3/4 | 3/8 | 4
SL112405A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1415 | 3/4 | 3/8 | 4
SL112407A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1416 | 3/4 | 3/8 | 4
SL112410A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1417 | 3/4 | 3/8 | 4
SL112500A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1418 | 3/4 | 3/8 | 4
SL112505A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1419 | 3/4 | 3/8 | 4
SL112507A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1420 | 3/4 | 3/8 | 4
SL112510A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1421 | 3/4 | 3/8 | 4
SL113000A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1422 | 3/4 | 3/8 | 4
SL113005A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1423 | 3/4 | 3/8 | 4
SL113007A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1424 | 3/4 | 3/8 | 4
SL113010A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1425 | 3/4 | 3/8 | 4
SL113100A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1426 | 3/4 | 3/8 | 4
SL113105A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1427 | 3/4 | 3/8 | 4
SL113107A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1428 | 3/4 | 3/8 | 4
SL113110A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1429 | 3/4 | 3/8 | 4
SL113600A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1430 | 3/4 | 3/8 | 4
SL113605A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1431 | 3/4 | 3/8 | 4
SL113607A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1432 | 3/4 | 3/8 | 4
SL113610A | S Series | 3-speed PSC motor | Upflow | L1 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1433 | 3/4 | 3/8 | 4
SL113700A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1434 | 3/4 | 3/8 | 4
SL113705A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1435 | 3/4 | 3/8 | 4
SL113707A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1436 | 3/4 | 3/8 | 4
SL113710A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1437 | 3/4 | 3/8 | 4
SL113900A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1438 | 3/4 | 3/8 | 4
SL113905A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1439 | 3/4 | 3/8 | 4
SL113907A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1440 | 3/4 | 3/8 | 4
SL113910A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1441 | 3/4 | 3/8 | 4
SL171800A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1442 | 3/4 | 3/8 | 4
SL171805A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1443 | 3/4 | 3/8 | 4
SL171807A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1444 | 3/4 | 3/8 | 4
SL171810A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1445 | 3/4 | 3/8 | 4
SL171900A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1446 | 3/4 | 3/8 | 4
SL171905A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1447 | 3/4 | 3/8 | 4
SL171907A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1448 | 3/4 | 3/8 | 4
SL171910A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1449 | 3/4 | 3/8 | 4
SL172400A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1450 | 3/4 | 3/8 | 4
SL172405A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1451 | 3/4 | 3/8 | 4
SL172407A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1452 | 3/4 | 3/8 | 4
SL172410A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1453 | 3/4 | 3/8 | 4
SL172500A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1454 | 3/4 | 3/8 | 4
SL172505A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1455 | 3/4 | 3/8 | 4
SL172507A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1456 | 3/4 | 3/8 | 4
SL172510A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1457 | 3/4 | 3/8 | 4
SL173000A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1458 | 3/4 | 3/8 | 4
SL173005A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1459 | 3/4 | 3/8 | 4
SL173007A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1460 | 3/4 | 3/8 | 4
SL173010A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1461 | 3/4 | 3/8 | 4
SL173100A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1462 | 3/4 | 3/8 | 4
SL173105A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1463 | 3/4 | 3/8 | 4
SL173107A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1464 | 3/4 | 3/8 | 4
SL173110A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1465 | 3/4 | 3/8 | 4
SL173600A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1466 | 3/4 | 3/8 | 4
SL173605A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1467 | 3/4 | 3/8 | 4
SL173607A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1468 | 3/4 | 3/8 | 4
SL173610A | S Series | 3-speed PSC motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1469 | 3/4 | 3/8 | 4
SL173700A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1470 | 3/4 | 3/8 | 4
SL173705A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1471 | 3/4 | 3/8 | 4
SL173707A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1472 | 3/4 | 3/8 | 4
SL173710A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1473 | 3/4 | 3/8 | 4
SL173900A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1474 | 3/4 | 3/8 | 4
SL173905A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1475 | 3/4 | 3/8 | 4
SL173907A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1476 | 3/4 | 3/8 | 4
SL173910A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1477 | 3/4 | 3/8 | 4
SL191800A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1478 | 3/4 | 3/8 | 4
SL191805A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1479 | 3/4 | 3/8 | 4
SL191807A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1480 | 3/4 | 3/8 | 4
SL191810A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1481 | 3/4 | 3/8 | 4
SL191900A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1482 | 3/4 | 3/8 | 4
SL191905A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1483 | 3/4 | 3/8 | 4
SL191907A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1484 | 3/4 | 3/8 | 4
SL191910A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1485 | 3/4 | 3/8 | 4
SL192400A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1486 | 3/4 | 3/8 | 4
SL192405A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1487 | 3/4 | 3/8 | 4
SL192407A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1488 | 3/4 | 3/8 | 4
SL192410A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1489 | 3/4 | 3/8 | 4
SL192500A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1490 | 3/4 | 3/8 | 4
SL192505A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1491 | 3/4 | 3/8 | 4
SL192507A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1492 | 3/4 | 3/8 | 4
SL192510A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1493 | 3/4 | 3/8 | 4
SL193000A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1494 | 3/4 | 3/8 | 4
SL193005A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1495 | 3/4 | 3/8 | 4
SL193007A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1496 | 3/4 | 3/8 | 4
SL193010A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1497 | 3/4 | 3/8 | 4
SL193100A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1498 | 3/4 | 3/8 | 4
SL193105A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1499 | 3/4 | 3/8 | 4
SL193107A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1500 | 3/4 | 3/8 | 4
SL193110A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1501 | 3/4 | 3/8 | 4
SL193600A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1502 | 3/4 | 3/8 | 4
SL193605A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1503 | 3/4 | 3/8 | 4
SL193607A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1504 | 3/4 | 3/8 | 4
SL193610A | S Series | 3-speed PSC motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1505 | 3/4 | 3/8 | 4
SL193700A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1506 | 3/4 | 3/8 | 4
SL193705A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1507 | 3/4 | 3/8 | 4
SL193707A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1508 | 3/4 | 3/8 | 4
SL193710A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1509 | 3/4 | 3/8 | 4
SL193900A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1510 | 3/4 | 3/8 | 4
SL193905A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1511 | 3/4 | 3/8 | 4
SL193907A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1512 | 3/4 | 3/8 | 4
SL193910A | S Series | 5-speed high eff. ECM motor | Upflow | L1 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1513 | 3/4 | 3/8 | 4
SL511800A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1730 | 3/4 | 3/8 | 4
SL511805A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1731 | 3/4 | 3/8 | 4
SL511807A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1732 | 3/4 | 3/8 | 4
SL511810A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1733 | 3/4 | 3/8 | 4
SL511900A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1734 | 3/4 | 3/8 | 4
SL511905A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1735 | 3/4 | 3/8 | 4
SL511907A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1736 | 3/4 | 3/8 | 4
SL511910A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1737 | 3/4 | 3/8 | 4
SL512400A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1738 | 3/4 | 3/8 | 4
SL512405A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1739 | 3/4 | 3/8 | 4
SL512407A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1740 | 3/4 | 3/8 | 4
SL512410A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1741 | 3/4 | 3/8 | 4
SL512500A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1742 | 3/4 | 3/8 | 4
SL512505A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1743 | 3/4 | 3/8 | 4
SL512507A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1744 | 3/4 | 3/8 | 4
SL512510A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1745 | 3/4 | 3/8 | 4
SL513000A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1746 | 3/4 | 3/8 | 4
SL513005A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1747 | 3/4 | 3/8 | 4
SL513007A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1748 | 3/4 | 3/8 | 4
SL513010A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1749 | 3/4 | 3/8 | 4
SL513100A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1750 | 3/4 | 3/8 | 4
SL513105A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1751 | 3/4 | 3/8 | 4
SL513107A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1752 | 3/4 | 3/8 | 4
SL513110A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1753 | 3/4 | 3/8 | 4
SL513600A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1754 | 3/4 | 3/8 | 4
SL513605A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1755 | 3/4 | 3/8 | 4
SL513607A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1756 | 3/4 | 3/8 | 4
SL513610A | S Series | 3-speed PSC motor | Upflow | L5 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1757 | 3/4 | 3/8 | 4
SL513700A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1758 | 3/4 | 3/8 | 4
SL513705A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1759 | 3/4 | 3/8 | 4
SL513707A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1760 | 3/4 | 3/8 | 4
SL513710A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1761 | 3/4 | 3/8 | 4
SL513900A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1762 | 3/4 | 3/8 | 4
SL513905A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1763 | 3/4 | 3/8 | 4
SL513907A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1764 | 3/4 | 3/8 | 4
SL513910A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1765 | 3/4 | 3/8 | 4
SL571800A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1766 | 3/4 | 3/8 | 4
SL571805A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1767 | 3/4 | 3/8 | 4
SL571807A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1768 | 3/4 | 3/8 | 4
SL571810A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1769 | 3/4 | 3/8 | 4
SL571900A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1770 | 3/4 | 3/8 | 4
SL571905A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1771 | 3/4 | 3/8 | 4
SL571907A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1772 | 3/4 | 3/8 | 4
SL571910A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1773 | 3/4 | 3/8 | 4
SL572400A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1774 | 3/4 | 3/8 | 4
SL572405A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1775 | 3/4 | 3/8 | 4
SL572407A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1776 | 3/4 | 3/8 | 4
SL572410A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1777 | 3/4 | 3/8 | 4
SL572500A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1778 | 3/4 | 3/8 | 4
SL572505A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1779 | 3/4 | 3/8 | 4
SL572507A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1780 | 3/4 | 3/8 | 4
SL572510A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1781 | 3/4 | 3/8 | 4
SL573000A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1782 | 3/4 | 3/8 | 4
SL573005A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1783 | 3/4 | 3/8 | 4
SL573007A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1784 | 3/4 | 3/8 | 4
SL573010A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1785 | 3/4 | 3/8 | 4
SL573100A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1786 | 3/4 | 3/8 | 4
SL573105A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1787 | 3/4 | 3/8 | 4
SL573107A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1788 | 3/4 | 3/8 | 4
SL573110A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1789 | 3/4 | 3/8 | 4
SL573600A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1790 | 3/4 | 3/8 | 4
SL573605A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1791 | 3/4 | 3/8 | 4
SL573607A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1792 | 3/4 | 3/8 | 4
SL573610A | S Series | 3-speed PSC motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1793 | 3/4 | 3/8 | 4
SL573700A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1794 | 3/4 | 3/8 | 4
SL573705A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1795 | 3/4 | 3/8 | 4
SL573707A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1796 | 3/4 | 3/8 | 4
SL573710A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1797 | 3/4 | 3/8 | 4
SL573900A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1798 | 3/4 | 3/8 | 4
SL573905A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1799 | 3/4 | 3/8 | 4
SL573907A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1800 | 3/4 | 3/8 | 4
SL573910A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1801 | 3/4 | 3/8 | 4
SL591800A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1802 | 3/4 | 3/8 | 4
SL591805A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1803 | 3/4 | 3/8 | 4
SL591807A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1804 | 3/4 | 3/8 | 4
SL591810A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1805 | 3/4 | 3/8 | 4
SL591900A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1806 | 3/4 | 3/8 | 4
SL591905A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1807 | 3/4 | 3/8 | 4
SL591907A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1808 | 3/4 | 3/8 | 4
SL591910A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1809 | 3/4 | 3/8 | 4
SL592400A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1810 | 3/4 | 3/8 | 4
SL592405A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1811 | 3/4 | 3/8 | 4
SL592407A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1812 | 3/4 | 3/8 | 4
SL592410A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1813 | 3/4 | 3/8 | 4
SL592500A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1814 | 3/4 | 3/8 | 4
SL592505A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1815 | 3/4 | 3/8 | 4
SL592507A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1816 | 3/4 | 3/8 | 4
SL592510A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1817 | 3/4 | 3/8 | 4
SL593000A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1818 | 3/4 | 3/8 | 4
SL593005A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1819 | 3/4 | 3/8 | 4
SL593007A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1820 | 3/4 | 3/8 | 4
SL593010A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1821 | 3/4 | 3/8 | 4
SL593100A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1822 | 3/4 | 3/8 | 4
SL593105A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1823 | 3/4 | 3/8 | 4
SL593107A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1824 | 3/4 | 3/8 | 4
SL593110A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1825 | 3/4 | 3/8 | 4
SL593600A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1826 | 3/4 | 3/8 | 4
SL593605A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1827 | 3/4 | 3/8 | 4
SL593607A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1828 | 3/4 | 3/8 | 4
SL593610A | S Series | 3-speed PSC motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1829 | 3/4 | 3/8 | 4
SL593700A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1830 | 3/4 | 3/8 | 4
SL593705A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1831 | 3/4 | 3/8 | 4
SL593707A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1832 | 3/4 | 3/8 | 4
SL593710A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1833 | 3/4 | 3/8 | 4
SL593900A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1834 | 3/4 | 3/8 | 4
SL593905A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1835 | 3/4 | 3/8 | 4
SL593907A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1836 | 3/4 | 3/8 | 4
SL593910A | S Series | 5-speed high eff. ECM motor | Upflow | L5 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1837 | 3/4 | 3/8 | 4
SL611800A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1838 | 3/4 | 3/8 | 4
SL611805A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1839 | 3/4 | 3/8 | 4
SL611807A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1840 | 3/4 | 3/8 | 4
SL611810A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1841 | 3/4 | 3/8 | 4
SL611900A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1842 | 3/4 | 3/8 | 4
SL611905A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1843 | 3/4 | 3/8 | 4
SL611907A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1844 | 3/4 | 3/8 | 4
SL611910A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1845 | 3/4 | 3/8 | 4
SL612400A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1846 | 3/4 | 3/8 | 4
SL612405A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1847 | 3/4 | 3/8 | 4
SL612407A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1848 | 3/4 | 3/8 | 4
SL612410A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1849 | 3/4 | 3/8 | 4
SL612500A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1850 | 3/4 | 3/8 | 4
SL612505A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1851 | 3/4 | 3/8 | 4
SL612507A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1852 | 3/4 | 3/8 | 4
SL612510A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1853 | 3/4 | 3/8 | 4
SL613000A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1854 | 3/4 | 3/8 | 4
SL613005A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1855 | 3/4 | 3/8 | 4
SL613007A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1856 | 3/4 | 3/8 | 4
SL613010A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1857 | 3/4 | 3/8 | 4
SL613100A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1858 | 3/4 | 3/8 | 4
SL613105A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1859 | 3/4 | 3/8 | 4
SL613107A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1860 | 3/4 | 3/8 | 4
SL613110A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1861 | 3/4 | 3/8 | 4
SL613600A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1862 | 3/4 | 3/8 | 4
SL613605A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1863 | 3/4 | 3/8 | 4
SL613607A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1864 | 3/4 | 3/8 | 4
SL613610A | S Series | 3-speed PSC motor | Upflow | L6 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1865 | 3/4 | 3/8 | 4
SL613700A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1866 | 3/4 | 3/8 | 4
SL613705A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1867 | 3/4 | 3/8 | 4
SL613707A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1868 | 3/4 | 3/8 | 4
SL613710A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1869 | 3/4 | 3/8 | 4
SL613900A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1870 | 3/4 | 3/8 | 4
SL613905A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1871 | 3/4 | 3/8 | 4
SL613907A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1872 | 3/4 | 3/8 | 4
SL613910A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1873 | 3/4 | 3/8 | 4
SL671800A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1874 | 3/4 | 3/8 | 4
SL671805A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1875 | 3/4 | 3/8 | 4
SL671807A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1876 | 3/4 | 3/8 | 4
SL671810A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1877 | 3/4 | 3/8 | 4
SL671900A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1878 | 3/4 | 3/8 | 4
SL671905A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1879 | 3/4 | 3/8 | 4
SL671907A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1880 | 3/4 | 3/8 | 4
SL671910A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1881 | 3/4 | 3/8 | 4
SL672400A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1882 | 3/4 | 3/8 | 4
SL672405A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1883 | 3/4 | 3/8 | 4
SL672407A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1884 | 3/4 | 3/8 | 4
SL672410A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1885 | 3/4 | 3/8 | 4
SL672500A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1886 | 3/4 | 3/8 | 4
SL672505A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1887 | 3/4 | 3/8 | 4
SL672507A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1888 | 3/4 | 3/8 | 4
SL672510A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1889 | 3/4 | 3/8 | 4
SL673000A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1890 | 3/4 | 3/8 | 4
SL673005A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1891 | 3/4 | 3/8 | 4
SL673007A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1892 | 3/4 | 3/8 | 4
SL673010A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1893 | 3/4 | 3/8 | 4
SL673100A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1894 | 3/4 | 3/8 | 4
SL673105A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1895 | 3/4 | 3/8 | 4
SL673107A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1896 | 3/4 | 3/8 | 4
SL673110A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1897 | 3/4 | 3/8 | 4
SL673600A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1898 | 3/4 | 3/8 | 4
SL673605A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1899 | 3/4 | 3/8 | 4
SL673607A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1900 | 3/4 | 3/8 | 4
SL673610A | S Series | 3-speed PSC motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1901 | 3/4 | 3/8 | 4
SL673700A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1902 | 3/4 | 3/8 | 4
SL673705A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1903 | 3/4 | 3/8 | 4
SL673707A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1904 | 3/4 | 3/8 | 4
SL673710A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1905 | 3/4 | 3/8 | 4
SL673900A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1906 | 3/4 | 3/8 | 4
SL673905A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1907 | 3/4 | 3/8 | 4
SL673907A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1908 | 3/4 | 3/8 | 4
SL673910A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1909 | 3/4 | 3/8 | 4
SL691800A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1910 | 3/4 | 3/8 | 4
SL691805A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1911 | 3/4 | 3/8 | 4
SL691807A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1912 | 3/4 | 3/8 | 4
SL691810A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1913 | 3/4 | 3/8 | 4
SL691900A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1914 | 3/4 | 3/8 | 4
SL691905A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1915 | 3/4 | 3/8 | 4
SL691907A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1916 | 3/4 | 3/8 | 4
SL691910A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1917 | 3/4 | 3/8 | 4
SL692400A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1918 | 3/4 | 3/8 | 4
SL692405A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1919 | 3/4 | 3/8 | 4
SL692407A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1920 | 3/4 | 3/8 | 4
SL692410A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1921 | 3/4 | 3/8 | 4
SL692500A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1922 | 3/4 | 3/8 | 4
SL692505A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1923 | 3/4 | 3/8 | 4
SL692507A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1924 | 3/4 | 3/8 | 4
SL692510A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1925 | 3/4 | 3/8 | 4
SL693000A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1926 | 3/4 | 3/8 | 4
SL693005A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1927 | 3/4 | 3/8 | 4
SL693007A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1928 | 3/4 | 3/8 | 4
SL693010A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1929 | 3/4 | 3/8 | 4
SL693100A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1930 | 3/4 | 3/8 | 4
SL693105A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1931 | 3/4 | 3/8 | 4
SL693107A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1932 | 3/4 | 3/8 | 4
SL693110A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1933 | 3/4 | 3/8 | 4
SL693600A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1934 | 3/4 | 3/8 | 4
SL693605A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1935 | 3/4 | 3/8 | 4
SL693607A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1936 | 3/4 | 3/8 | 4
SL693610A | S Series | 3-speed PSC motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1937 | 3/4 | 3/8 | 4
SL693700A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1938 | 3/4 | 3/8 | 4
SL693705A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1939 | 3/4 | 3/8 | 4
SL693707A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1940 | 3/4 | 3/8 | 4
SL693710A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1941 | 3/4 | 3/8 | 4
SL693900A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1942 | 3/4 | 3/8 | 4
SL693905A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1943 | 3/4 | 3/8 | 4
SL693907A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1944 | 3/4 | 3/8 | 4
SL693910A | S Series | 5-speed high eff. ECM motor | Upflow | L6 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 1945 | 3/4 | 3/8 | 4
SL911800A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2162 | 3/4 | 3/8 | 4
SL911805A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2163 | 3/4 | 3/8 | 4
SL911807A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2164 | 3/4 | 3/8 | 4
SL911810A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2165 | 3/4 | 3/8 | 4
SL911900A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2166 | 3/4 | 3/8 | 4
SL911905A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2167 | 3/4 | 3/8 | 4
SL911907A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2168 | 3/4 | 3/8 | 4
SL911910A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2169 | 3/4 | 3/8 | 4
SL912400A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2170 | 3/4 | 3/8 | 4
SL912405A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2171 | 3/4 | 3/8 | 4
SL912407A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2172 | 3/4 | 3/8 | 4
SL912410A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2173 | 3/4 | 3/8 | 4
SL912500A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2174 | 3/4 | 3/8 | 4
SL912505A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2175 | 3/4 | 3/8 | 4
SL912507A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2176 | 3/4 | 3/8 | 4
SL912510A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2177 | 3/4 | 3/8 | 4
SL913000A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2178 | 3/4 | 3/8 | 4
SL913005A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2179 | 3/4 | 3/8 | 4
SL913007A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2180 | 3/4 | 3/8 | 4
SL913010A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2181 | 3/4 | 3/8 | 4
SL913100A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2182 | 3/4 | 3/8 | 4
SL913105A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2183 | 3/4 | 3/8 | 4
SL913107A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2184 | 3/4 | 3/8 | 4
SL913110A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2185 | 3/4 | 3/8 | 4
SL913600A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2186 | 3/4 | 3/8 | 4
SL913605A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2187 | 3/4 | 3/8 | 4
SL913607A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2188 | 3/4 | 3/8 | 4
SL913610A | S Series | 3-speed PSC motor | Upflow | L9 | Piston (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2189 | 3/4 | 3/8 | 4
SL913700A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2190 | 3/4 | 3/8 | 4
SL913705A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2191 | 3/4 | 3/8 | 4
SL913707A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2192 | 3/4 | 3/8 | 4
SL913710A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2193 | 3/4 | 3/8 | 4
SL913900A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2194 | 3/4 | 3/8 | 4
SL913905A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2195 | 3/4 | 3/8 | 4
SL913907A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2196 | 3/4 | 3/8 | 4
SL913910A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Piston (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2197 | 3/4 | 3/8 | 4
SL971800A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2198 | 3/4 | 3/8 | 4
SL971805A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2199 | 3/4 | 3/8 | 4
SL971807A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2200 | 3/4 | 3/8 | 4
SL971810A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2201 | 3/4 | 3/8 | 4
SL971900A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2202 | 3/4 | 3/8 | 4
SL971905A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2203 | 3/4 | 3/8 | 4
SL971907A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2204 | 3/4 | 3/8 | 4
SL971910A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2205 | 3/4 | 3/8 | 4
SL972400A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2206 | 3/4 | 3/8 | 4
SL972405A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2207 | 3/4 | 3/8 | 4
SL972407A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2208 | 3/4 | 3/8 | 4
SL972410A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2209 | 3/4 | 3/8 | 4
SL972500A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2210 | 3/4 | 3/8 | 4
SL972505A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2211 | 3/4 | 3/8 | 4
SL972507A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2212 | 3/4 | 3/8 | 4
SL972510A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2213 | 3/4 | 3/8 | 4
SL973000A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2214 | 3/4 | 3/8 | 4
SL973005A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2215 | 3/4 | 3/8 | 4
SL973007A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2216 | 3/4 | 3/8 | 4
SL973010A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2217 | 3/4 | 3/8 | 4
SL973100A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2218 | 3/4 | 3/8 | 4
SL973105A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2219 | 3/4 | 3/8 | 4
SL973107A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2220 | 3/4 | 3/8 | 4
SL973110A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2221 | 3/4 | 3/8 | 4
SL973600A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2222 | 3/4 | 3/8 | 4
SL973605A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2223 | 3/4 | 3/8 | 4
SL973607A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2224 | 3/4 | 3/8 | 4
SL973610A | S Series | 3-speed PSC motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2225 | 3/4 | 3/8 | 4
SL973700A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2226 | 3/4 | 3/8 | 4
SL973705A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2227 | 3/4 | 3/8 | 4
SL973707A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2228 | 3/4 | 3/8 | 4
SL973710A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2229 | 3/4 | 3/8 | 4
SL973900A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2230 | 3/4 | 3/8 | 4
SL973905A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2231 | 3/4 | 3/8 | 4
SL973907A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2232 | 3/4 | 3/8 | 4
SL973910A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2233 | 3/4 | 3/8 | 4
SL991800A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2234 | 3/4 | 3/8 | 4
SL991805A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2235 | 3/4 | 3/8 | 4
SL991807A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2236 | 3/4 | 3/8 | 4
SL991810A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 18 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 600 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2237 | 3/4 | 3/8 | 4
SL991900A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2238 | 3/4 | 3/8 | 4
SL991905A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2239 | 3/4 | 3/8 | 4
SL991907A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2240 | 3/4 | 3/8 | 4
SL991910A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 19 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 0.8 | 600 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2241 | 3/4 | 3/8 | 4
SL992400A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2242 | 3/4 | 3/8 | 4
SL992405A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2243 | 3/4 | 3/8 | 4
SL992407A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2244 | 3/4 | 3/8 | 4
SL992410A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 24 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 1.7 | 800 | 78 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2245 | 3/4 | 3/8 | 4
SL992500A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2246 | 3/4 | 3/8 | 4
SL992505A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2247 | 3/4 | 3/8 | 4
SL992507A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2248 | 3/4 | 3/8 | 4
SL992510A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 25 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.7 | 800 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2249 | 3/4 | 3/8 | 4
SL993000A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2250 | 3/4 | 3/8 | 4
SL993005A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2251 | 3/4 | 3/8 | 4
SL993007A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2252 | 3/4 | 3/8 | 4
SL993010A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 30 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1000 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2253 | 3/4 | 3/8 | 4
SL993100A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2254 | 3/4 | 3/8 | 4
SL993105A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2255 | 3/4 | 3/8 | 4
SL993107A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2256 | 3/4 | 3/8 | 4
SL993110A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 31 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2.2 | 1000 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2257 | 3/4 | 3/8 | 4
SL993600A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2258 | 3/4 | 3/8 | 4
SL993605A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2259 | 3/4 | 3/8 | 4
SL993607A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2260 | 3/4 | 3/8 | 4
SL993610A | S Series | 3-speed PSC motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 36 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 2 | 1200 | 81 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2261 | 3/4 | 3/8 | 4
SL993700A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2262 | 3/4 | 3/8 | 4
SL993705A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2263 | 3/4 | 3/8 | 4
SL993707A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2264 | 3/4 | 3/8 | 4
SL993710A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 37 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 84 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2265 | 3/4 | 3/8 | 4
SL993900A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2266 | 3/4 | 3/8 | 4
SL993905A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2267 | 3/4 | 3/8 | 4
SL993907A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 7.5kw | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2268 | 3/4 | 3/8 | 4
SL993910A | S Series | 5-speed high eff. ECM motor | Upflow | L9 | Non-bleed HP-A/C TXV (R-410A) | 39 | N/A | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/2 | 2.9 | 1200 | 87 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2269 | 3/4 | 3/8 | 4

## Airflow (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  | Airflow (CFM) vs. External Static Pressure (inches W.C.) | [6 empty] | Airflow (CFM) vs. External Static Pressure (inches W.C.)
ID | Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | Size | Tap | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
18_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 18 | * ^ Low - Red | 606 | 591 | 576 | 559 | 529 | 18 | * ^ Low - Red | 606 | 591 | 576 | 559 | 529 | 19 | Tap 1 | 547 | 484 | 366 | 309 | 268
18_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 18 | Med - Blue | 802 | 784 | 751 | 722 | 693 | 18 | Med - Blue | 802 | 784 | 751 | 722 | 693 | 19 | * Tap 2 | 651 | 600 | 566 | 516 | 466
18_208/240 V, 60 Hz, 1 ph. (PSC only)_3 | 18 | High -Black | 1046 | 1013 | 987 | 943 | 885 | 18 | High -Black | 1046 | 1013 | 987 | 943 | 885 | 19 | Tap 3 | 695 | 646 | 617 | 566 | 544
24_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 24 | Low - Red | 606 | 591 | 576 | 559 | 529 | 24 | Low - Red | 606 | 591 | 576 | 559 | 529 | 19 | ^ Tap 4 | 742 | 700 | 669 | 627 | 600
24_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 24 | * ^ Med - Blue | 802 | 784 | 751 | 722 | 693 | 24 | * ^ Med - Blue | 802 | 784 | 751 | 722 | 693 | 19 | Tap 5 | 758 | 712 | 682 | 641 | 625
24_208/240 V, 60 Hz, 1 ph. (PSC only)_3 | 24 | High -Black | 1046 | 1013 | 987 | 943 | 885 | 24 | High -Black | 1046 | 1013 | 987 | 943 | 885 | 25 | Tap 1 | 569 | 453 | 347 | 264 | 264
30_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 30 | Low - Red | 816 | 809 | 802 | 775 | 752 | 30 | Low - Red | 816 | 809 | 802 | 775 | 752 | 25 | Tap 2 | 659 | 600 | 569 | 518 | 475
30_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 30 | * ^ Med - Blue | 1000 | 985 | 970 | 935 | 889 | 30 | * ^ Med - Blue | 1000 | 985 | 970 | 935 | 889 | 25 | * Tap 3 | 847 | 800 | 787 | 744 | 722
30_208/240 V, 60 Hz, 1 ph. (PSC only)_3 | 30 | High -Black | 1218 | 1175 | 1122 | 1070 | 1008 | 30 | High -Black | 1218 | 1175 | 1122 | 1070 | 1008 | 25 | ^ Tap 4 | 928 | 901 | 883 | 846 | 802
36_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 36 | Low - Red | 816 | 809 | 802 | 775 | 752 | 36 | Low - Red | 816 | 809 | 802 | 775 | 752 | 25 | Tap 5 | 970 | 944 | 927 | 891 | 864
36_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 36 | Med - Blue | 1000 | 985 | 970 | 935 | 889 | 36 | Med - Blue | 1000 | 985 | 970 | 935 | 889 | 31 | Tap 1 | 656 | 600 | 567 | 522 | 473
36_208/240 V, 60 Hz, 1 ph. (PSC only)_3 | 36 | * ^ High -Black | 1218 | 1175 | 1122 | 1070 | 1008 | 36 | * ^ High -Black | 1218 | 1175 | 1122 | 1070 | 1008 | 31 | Tap 2 | 842 | 800 | 782 | 739 | 716
19_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 19 | Tap 1 | 547 | 484 | 366 | 309 | 268 | * Factory setting for cooling. | [6 empty] | 31 | * Tap 3 | 1059 | 1028 | 1004 | 972 | 946
19_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 19 | * Tap 2 | 651 | 600 | 566 | 516 | 466 | ^ Factory setting for heating. | [6 empty] | 31 | ^ Tap 4 | 1106 | 1084 | 1053 | 1030 | 1000
19_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 19 | Tap 3 | 695 | 646 | 617 | 566 | 544 | *** All airflow data is with a dry coil, filter, & electric heat. | [6 empty] | 31 | Tap 5 | 1137 | 1108 | 1085 | 1055 | 1031
19_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 19 | ^ Tap 4 | 742 | 700 | 669 | 627 | 600 | [7 empty] | 37 | Tap 1 | 848 | 800 | 769 | 726 | 692
19_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 19 | Tap 5 | 758 | 712 | 682 | 641 | 625 | [7 empty] | 37 | Tap 2 | 1051 | 1028 | 1000 | 956 | 930
25_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 25 | Tap 1 | 569 | 453 | 347 | 264 | 264 | [7 empty] | 37 | * Tap 3 | 1247 | 1215 | 1188 | 1161 | 1126
25_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 25 | Tap 2 | 659 | 600 | 569 | 518 | 475 | [7 empty] | 37 | ^ Tap 4 | 1310 | 1279 | 1254 | 1228 | 1200
25_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 25 | * Tap 3 | 847 | 800 | 787 | 744 | 722 | [7 empty] | 37 | Tap 5 | 1364 | 1334 | 1304 | 1279 | 1250
25_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 25 | ^ Tap 4 | 928 | 901 | 883 | 846 | 802 | [7 empty] | 39 | Tap 1 | 800.4 | 782.8 | 747.3 | 724.9 | 688.8
25_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 25 | Tap 5 | 970 | 944 | 927 | 891 | 864 | [7 empty] | 39 | Tap 2 | 1034.2 | 1003.1 | 987.1 | 959 | 936.7
31_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 31 | Tap 1 | 656 | 600 | 567 | 522 | 473 | [7 empty] | 39 | * Tap 3 | 1280.9 | 1253 | 1228.2 | 1206.7 | 1186.2
31_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 31 | Tap 2 | 842 | 800 | 782 | 739 | 716 | [7 empty] | 39 | ^ Tap 4 | 1342.6 | 1314.4 | 1290.3 | 1261.1 | 1226.2
31_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 31 | * Tap 3 | 1059 | 1028 | 1004 | 972 | 946 | [7 empty] | 39 | Tap 5 | 1366.5 | 1341.6 | 1312.4 | 1276.7 | 1239.4
31_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 31 | ^ Tap 4 | 1106 | 1084 | 1053 | 1030 | 1000 | [7 empty] | * Factory setting for cooling.
31_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 31 | Tap 5 | 1137 | 1108 | 1085 | 1055 | 1031 | [7 empty] | ^ Factory setting for heating.
37_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 37 | Tap 1 | 848 | 800 | 769 | 726 | 692 | [7 empty] | *** All airflow data is with a dry coil, filter, & electric heat.
37_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 37 | Tap 2 | 1051 | 1028 | 1000 | 956 | 930
37_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 37 | * Tap 3 | 1247 | 1215 | 1188 | 1161 | 1126
37_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 37 | ^ Tap 4 | 1310 | 1279 | 1254 | 1228 | 1200
37_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 37 | Tap 5 | 1364 | 1334 | 1304 | 1279 | 1250
39_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 39 | Tap 1 | 800.4 | 782.8 | 747.3 | 724.9 | 688.8
39_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 39 | Tap 2 | 1034.2 | 1003.1 | 987.1 | 959 | 936.7
39_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 39 | * Tap 3 | 1280.9 | 1253 | 1228.2 | 1206.7 | 1186.2
39_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 39 | ^ Tap 4 | 1342.6 | 1314.4 | 1290.3 | 1261.1 | 1226.2
39_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 39 | Tap 5 | 1366.5 | 1341.6 | 1312.4 | 1276.7 | 1239.4

## Electrial data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
| (All have electric heat) | kW | BTUH | [6 empty] | Per Stage (A)
|  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
3-speed PSC motor_18_none | 18 | 0 | 0 | 1.8 | 1.7 | 1.8 | 1.7 | 2.25 | 2.125 | 15 | 15
3-speed PSC motor_18_5kW | 18 | 5 | 17060.71 | 1.8 | 1.7 | 19.8556 | 22.5333 | 24.8194 | 28.1667 | 25 | 30
3-speed PSC motor_18_7.5kw | 18 | 7.5 | 25591.065 | 1.8 | 1.7 | 28.8833 | 32.95 | 36.1042 | 41.1875 | 40 | 45
3-speed PSC motor_18_10kW | 18 | 10 | 34121.42 | 1.8 | 1.7 | 37.9111 | 43.3667 | 47.3889 | 54.2083 | 50 | 60
3-speed PSC motor_24_none | 24 | 0 | 0 | 1.8 | 1.7 | 1.8 | 1.7 | 2.25 | 2.125 | 15 | 15
3-speed PSC motor_24_5kW | 24 | 5 | 17060.71 | 1.8 | 1.7 | 19.8556 | 22.5333 | 24.8194 | 28.1667 | 25 | 30
3-speed PSC motor_24_7.5kw | 24 | 7.5 | 25591.065 | 1.8 | 1.7 | 28.8833 | 32.95 | 36.1042 | 41.1875 | 40 | 45
3-speed PSC motor_24_10kW | 24 | 10 | 34121.42 | 1.8 | 1.7 | 37.9111 | 43.3667 | 47.3889 | 54.2083 | 50 | 60
3-speed PSC motor_30_none | 30 | 0 | 0 | 2.1 | 2 | 2.1 | 2 | 2.625 | 2.5 | 15 | 15
3-speed PSC motor_30_5kW | 30 | 5 | 17060.71 | 2.1 | 2 | 20.1556 | 22.8333 | 25.1944 | 28.5417 | 30 | 30
3-speed PSC motor_30_7.5kw | 30 | 7.5 | 25591.065 | 2.1 | 2 | 29.1833 | 33.25 | 36.4792 | 41.5625 | 40 | 45
3-speed PSC motor_30_10kW | 30 | 10 | 34121.42 | 2.1 | 2 | 38.2111 | 43.6667 | 47.7639 | 54.5833 | 50 | 60
3-speed PSC motor_36_none | 36 | 0 | 0 | 2.1 | 2 | 2.1 | 2 | 2.625 | 2.5 | 15 | 15
3-speed PSC motor_36_5kW | 36 | 5 | 17060.71 | 2.1 | 2 | 20.1556 | 22.8333 | 25.1944 | 28.5417 | 30 | 30
3-speed PSC motor_36_7.5kw | 36 | 7.5 | 25591.065 | 2.1 | 2 | 29.1833 | 33.25 | 36.4792 | 41.5625 | 40 | 45
3-speed PSC motor_36_10kW | 36 | 10 | 34121.42 | 2.1 | 2 | 38.2111 | 43.6667 | 47.7639 | 54.5833 | 50 | 60
5-speed high eff. ECM motor_19_none | 19 | 0 | 0 | 0.9 | 0.8 | 0.9 | 0.8 | 1.125 | 1 | 15 | 15
5-speed high eff. ECM motor_19_5kW | 19 | 5 | 17060.71 | 0.9 | 0.8 | 18.9556 | 21.6333 | 23.6944 | 27.0417 | 25 | 30
5-speed high eff. ECM motor_19_7.5kw | 19 | 7.5 | 25591.065 | 0.9 | 0.8 | 27.9833 | 32.05 | 34.9792 | 40.0625 | 35 | 45
5-speed high eff. ECM motor_19_10kW | 19 | 10 | 34121.42 | 0.9 | 0.8 | 37.0111 | 42.4667 | 46.2639 | 53.0833 | 50 | 60
5-speed high eff. ECM motor_25_none | 25 | 0 | 0 | 1.8 | 1.7 | 1.8 | 1.7 | 2.25 | 2.125 | 15 | 15
5-speed high eff. ECM motor_25_5kW | 25 | 5 | 17060.71 | 1.8 | 1.7 | 19.8556 | 22.5333 | 24.8194 | 28.1667 | 25 | 30
5-speed high eff. ECM motor_25_7.5kw | 25 | 7.5 | 25591.065 | 1.8 | 1.7 | 28.8833 | 32.95 | 36.1042 | 41.1875 | 40 | 45
5-speed high eff. ECM motor_25_10kW | 25 | 10 | 34121.42 | 1.8 | 1.7 | 37.9111 | 43.3667 | 47.3889 | 54.2083 | 50 | 60
5-speed high eff. ECM motor_31_none | 31 | 0 | 0 | 2.4 | 2.2 | 2.4 | 2.2 | 3 | 2.75 | 15 | 15
5-speed high eff. ECM motor_31_5kW | 31 | 5 | 17060.71 | 2.4 | 2.2 | 20.4556 | 23.0333 | 25.5694 | 28.7917 | 30 | 30
5-speed high eff. ECM motor_31_7.5kw | 31 | 7.5 | 25591.065 | 2.4 | 2.2 | 29.4833 | 33.45 | 36.8542 | 41.8125 | 40 | 45
5-speed high eff. ECM motor_31_10kW | 31 | 10 | 34121.42 | 2.4 | 2.2 | 38.5111 | 43.8667 | 48.1389 | 54.8333 | 50 | 60
5-speed high eff. ECM motor_37_none | 37 | 0 | 0 | 3.1 | 2.9 | 3.1 | 2.9 | 3.875 | 3.625 | 15 | 15
5-speed high eff. ECM motor_37_5kW | 37 | 5 | 17060.71 | 3.1 | 2.9 | 21.1556 | 23.7333 | 26.4444 | 29.6667 | 30 | 30
5-speed high eff. ECM motor_37_7.5kw | 37 | 7.5 | 25591.065 | 3.1 | 2.9 | 30.1833 | 34.15 | 37.7292 | 42.6875 | 40 | 45
5-speed high eff. ECM motor_37_10kW | 37 | 10 | 34121.42 | 3.1 | 2.9 | 39.2111 | 44.5667 | 49.0139 | 55.7083 | 50 | 60
5-speed high eff. ECM motor_39_none | 39 | 0 | 0 | 3.1 | 2.9 | 3.1 | 2.9 | 3.875 | 3.625 | 15 | 15
5-speed high eff. ECM motor_39_5kW | 39 | 5 | 17060.71 | 3.1 | 2.9 | 21.1556 | 23.7333 | 26.4444 | 29.6667 | 30 | 30
5-speed high eff. ECM motor_39_7.5kw | 39 | 7.5 | 25591.065 | 3.1 | 2.9 | 30.1833 | 34.15 | 37.7292 | 42.6875 | 40 | 45
5-speed high eff. ECM motor_39_10kW | 39 | 10 | 34121.42 | 3.1 | 2.9 | 39.2111 | 44.5667 | 49.0139 | 55.7083 | 50 | 60
[1] For 208 Volts use .751 correction factor for kW & BTUH.
[2] Breaker supplied with heat kit may need to be changed. Verify breaker sizing based on min, circuit ampacity.

## Dim (hidden)
Unit size | A (in) | B (in) | C (in)
18 | 22 | 18.75 | 31
19 | 22 | 18.75 | 31
24 | 22 | 18.75 | 31
35 | 22 | 18.75 | 31
30 | 22 | 18.75 | 31
31 | 22 | 18.75 | 31
36 | 22 | 18.75 | 31
37 | 22 | 18.75 | 31
39 | 22 | 18.75 | 35.5