## Front
SUBMITTAL DATA
CP / CE SERIES SOFFIT MOUNT AIR HANDLER
Job: |  |  |  | Engineer:
Location: |  |  |  | Architect:
Schedule No.: |  |  |  | Date:
System Designation: |  |  |  | For:
FEATURES
Product Warranty
Optional Accessories
Unit Size
|  | CP1801C1HS001CA | CE2301C1HS001CA | CP2301ABHP031UR | CE1801A1HP031UR
Factory Installed Heat (kW) |  | none | none | 3kW | 3kW
Refrigerant |  | R-410A | R-410A | R-32 | R-454B
Factory Installed metering device |  | Piston | Piston | Non-bleed HP-A/C TXV | Piston
Blower Data: | Motor Type | 2-speed PSC motor | ECM Constant Torque Motor | 2-speed PSC motor | ECM Constant Torque Motor
| Motor H.P. | 1/8 | 1/4 | 1/3 | 1/4
| F.L.A. | 1.25 | 2 | 1.9 | 2
Nominal CFM |  | 600 | 800 | 800 | 600
Max Unit Weight (lbs) |  | 92 | 92 | 63 | 63
Available Voltages |  | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph | 208/240 V, 60 Hz, 1 Ph
Maximum Elec. Heat available (kW) |  | 8kW | 8kW | 8kW | 8kW
Transformer Size and Type |  | 40VA, Class 2 | 40VA, Class 2 | 40VA, Class 2 | 40VA, Class 2
Refrigerant Conn. (IDS) Suction |  | 3/4 | 3/4 | 3/4 | 3/4
Refrigerant Conn. (IDS) Liquid |  | 3/8 | 3/8 | 3/8 | 3/8
Pallet Quantity (min order per model) |  | 8 | 8 | 8 | 8
NOTES:
Cooling capacities subject to outdoor unit matchup. See http://www.adpnow.com/extratings/ for individual capacities by OEM
Cooling and Heating capacity data is rated at the following conditions:
Cooling: 80 FDB / 67 FWB Indoor, 95 FDB Outdoor
Heating: 70 FDB / 47 FWB Indoor, 43 FDB Outdoor
| A1 Refrigerants Product Nomenclature |  |  | A2L Refrigerants Product Nomenclature
2140 Lake Park Blvd., Richardson, TX 75080
www.adpnow.com
Available in uncased or factory-installed cased configurations.
A1 model Suitable for use with R-410A.
A2L model Suitable for use with R-32 and R-454B.
A2L model include factory installed Refrigerant Detections System (RDS).
Designed for installation in a furred down area.
Fits industry standard footprints.
Optional field or factory installed heat 3-10kW.
Optional factory installed TXV w/threaded connections.
Decorative panel
Heat pump relay
Float switch
10-year limited warranty available.
Product registration required.
Product improvement is a continuous process at Advanced Distributor Products. Therefore, product specifications are subject to change without notice and without obligation on our part. Please contact your ADP representative or distributor to verify details.
© 2025 by Advanced Distributor Products. All rights reserved.

## Back
SUBMITTAL DATA
CP / CE SERIES SOFFIT MOUNT AIR HANDLER
Dimensions
Air Handler Size | [5 empty] | A (in) | B (in) | C (in) | D (in) |  | E (in) |  | Case Type
CP1801C1HS001CA | [5 empty] | 39.7 | 24 | 11 | 30.5 |  | 7 |  | Cased
CE2301C1HS001CA | [5 empty] | 39.7 | 24 | 11 | 30.5 |  | 7 |  | Cased
CP2301ABHP031UR | [5 empty] | 37 | 19.5 | 10.5 | N/A |  | N/A |  | Uncased
CE1801A1HP031UR | [5 empty] | 37 | 19.5 | 10.5 | N/A |  | N/A |  | Uncased
| Airflow (CFM) vs. External Static Pressure (inches W.C.) | [6 empty] | Electric Data
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
CP1801C1HS001CA | Low - Red | 609.9 | 536.4 | 467.5 | 392.4 | 315.7 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| High -Black | 680 | 607.4 | 532.3 | 456.2 | 367.6 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
[8 empty] | CP1801C1HS001CA | 0 | 0 | 1.25 | 1.25 | 1.25 | 1.25 | 1.5625 | 1.5625 | 15 | 15
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
CE2301C1HS001CA | Tap 1 (G) | 617.8 | 547.4 | 464.3 | 343.8 | 270.1 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| Tap 2 (DS) | 617.2 | 546.9 | 469.4 | 351.3 | 272.8 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| Tap 3 (Y1) | 778.5 | 719.8 | 632.8 | 549.1 | 441.1 |  | CE2301C1HS001CA | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
| Tap 4 (Y2) | 939.7 | 876.4 | 811.9 | 750.1 | 675.3
| ^ Tap 5 (W1) | 937 | 874.6 | 812 | 749.9 | 674.4
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
CP2301ABHP031UR | Low - Red | 845.9 | 776.8 | 701.8 | 626.6 | 545.9 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| High -Black | 902.3 | 830.3 | 754.7 | 667.3 | 588.7 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
[8 empty] | CP2301ABHP031UR | 3[2] | 10236.426 | 1.9 | 1.9 | 12.7333 | 14.4 | 15.9167 | 18 | 20 | 20
Unit Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 |  | Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
CE1801A1HP031UR | Tap 1 (G) | 603.9 | 514.1 | 452.8 | 437.1 | 301.3 |  |  | kW | BTUH | [6 empty] | Per Stage (A)
| Tap 2 (DS) | 603.9 | 514.1 | 452.8 | 437.1 | 301.3 |  |  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
| Tap 3 (Y1) | 734.5 | 651.4 | 576.9 | 506.1 | 443.9 |  | CE1801A1HP031UR | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
| Tap 4 (Y2) | 890.3 | 826.2 | 764.4 | 699.6 | 604.9
| ^ Tap 5 (W1) | 890.3 | 826.2 | 764.4 | 699.6 | 604.9
* Factory setting for cooling. | [7 empty] | [1] For 208 Volts use .751 correction factor for kW & BTUH.
^ Factory setting for heating. | [7 empty] | [2] Breaker supplied with heat kit may need to be changed. Verify breaker sizing based on min, circuit ampacity.
*** All airflow data is with a dry coil, filter, & electric heat.

## Nomenclature (hidden)
C | P |  | 18 | 01C |  | 9 |  | H |  | P |  | 03 |  | 1 |  | C |  | A | C | P |  | 18 | 01C |  | 9 |  | H |  | P |  | 03 |  | 1 |  | C |  | R
Series | Blower Motor |  | Unit Size | Slan No. |  | Metering Device |  | Airflow Config. |  | Line Connection |  | Heat |  | Voltage |  | Case |  | Revision | Series | Blower Motor |  | Unit Size | Slan No. |  | Metering Device |  | Airflow Config. |  | Line Connection |  | Heat |  | Voltage |  | Case |  | Refrigerant Detection System
C | P: | 2-Speed PSC | 18 19 23 24 25 29 30 | ##C: | Copper | 1: | Piston (R-410A) | H: | Horizontal only | S: | Stripped Wire (No heat Only) | 00: | No Heat | 1: | 208/240V, 60Hz, 1ph | C: | Cased |  | C | P: | 2-Speed PSC | 18 19 23 24 25 29 30 | ##C: | Copper | 1: | Piston (R-454B & R-32) | H: | Horizontal only | S: | Stripped Wire (No heat Only) | 00: | No Heat | 1: | 208/240V, 60Hz, 1ph | C: | Cased | R: | Included (Factory installed)
| E: | ECM Constant Torque |  | ##A: | Alumium | 7: | Bleed HP-A/C TXV (R-410A) |  |  | P: | Pull Disconnect | 03: | 3 kW (18-24) |  |  | U: | Uncased |  |  | E: | ECM Constant Torque |  | ##A: | Alumium | A: | Non-bleed HP-A/C TXV (R-454B) |  |  | P: | Pull Disconnect | 03: | 3 kW (18-24) |  |  | U: | Uncased
[6 empty] | 9: | Non-bleed HP-A/C TXV (R-410A) |  |  |  |  | 05: | 5 kW (all sizes) | [11 empty] | B: | Non-bleed HP-A/C TXV (R-32) |  |  |  |  | 05: | 5 kW (all sizes)
[12 empty] | 06: | 6 kW (all sizes) | [11 empty] | C: | Bleed HP-A/C TXV (R-454B) |  |  |  |  | 06: | 6 kW (all sizes)
[12 empty] | 08: | 8 kW (all sizes) | [17 empty] | 08: | 8 kW (all sizes)
[12 empty] | 10: | 10 kW (24-30) | [17 empty] | 10: | 10 kW (24-30)

## Data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model) | Case
CP1801C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CBHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CBHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403CCHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403CCHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403AAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403AAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ABHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ABHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403ACHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403ACHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CBHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CBHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505CCHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505CCHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505AAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505AAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ABHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ABHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505ACHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505ACHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CBHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CBHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903CCHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903CCHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903AAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903AAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ABHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ABHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903ACHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903ACHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CBHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CBHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005CCHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005CCHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005AAHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005AAHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ABHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ABHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005ACHP101CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005ACHP101UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased

## Airflow (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
ID | Size | Speed | 0.1 | 0.2 | 0.3 | 0.4 | 0.5
18_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 18 | Low - Red | 609.9 | 536.4 | 467.5 | 392.4 | 315.7
18_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 18 | High -Black | 680 | 607.4 | 532.3 | 456.2 | 367.6
19_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 19 | Low - Red | 609.9 | 536.4 | 467.5 | 392.4 | 315.7
19_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 19 | High -Black | 680 | 607.4 | 532.3 | 456.2 | 367.6
23_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 23 | Low - Red | 845.9 | 776.8 | 701.8 | 626.6 | 545.9
23_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 23 | High -Black | 902.3 | 830.3 | 754.7 | 667.3 | 588.7
24_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 24 | Low - Red | 832.8 | 780.8 | 724.9 | 658.3 | 580.4
24_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 24 | High -Black | 1038.8 | 975.5 | 903.3 | 824.8 | 727.7
29_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 29 | Low - Red | 832.8 | 780.8 | 724.9 | 658.3 | 580.4
29_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 29 | High -Black | 1038.8 | 975.5 | 903.3 | 824.8 | 727.7
25_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 25 | Low - Red | 838.5 | 771.2 | 705.6 | 643.9 | 553.3
25_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 25 | High -Black | 1050.4 | 974.7 | 900.7 | 820.1 | 743.9
30_208/240 V, 60 Hz, 1 ph. (PSC only)_1 | 30 | Low - Red | 838.5 | 771.2 | 705.6 | 643.9 | 553.3
30_208/240 V, 60 Hz, 1 ph. (PSC only)_2 | 30 | High -Black | 1050.4 | 974.7 | 900.7 | 820.1 | 743.9
18_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 18 | Tap 1 (G) | 603.9 | 514.1 | 452.8 | 437.1 | 301.3
18_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 18 | Tap 2 (DS) | 603.9 | 514.1 | 452.8 | 437.1 | 301.3
18_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 18 | Tap 3 (Y1) | 734.5 | 651.4 | 576.9 | 506.1 | 443.9
18_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 18 | Tap 4 (Y2) | 890.3 | 826.2 | 764.4 | 699.6 | 604.9
18_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 18 | ^ Tap 5 (W1) | 890.3 | 826.2 | 764.4 | 699.6 | 604.9
19_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 19 | Tap 1 (G) | 603.9 | 514.1 | 452.8 | 437.1 | 301.3
19_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 19 | Tap 2 (DS) | 603.9 | 514.1 | 452.8 | 437.1 | 301.3
19_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 19 | Tap 3 (Y1) | 734.5 | 651.4 | 576.9 | 506.1 | 443.9
19_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 19 | Tap 4 (Y2) | 890.3 | 826.2 | 764.4 | 699.6 | 604.9
19_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 19 | ^ Tap 5 (W1) | 890.3 | 826.2 | 764.4 | 699.6 | 604.9
23_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 23 | Tap 1 (G) | 617.8 | 547.4 | 464.3 | 343.8 | 270.1
23_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 23 | Tap 2 (DS) | 617.2 | 546.9 | 469.4 | 351.3 | 272.8
23_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 23 | Tap 3 (Y1) | 778.5 | 719.8 | 632.8 | 549.1 | 441.1
23_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 23 | Tap 4 (Y2) | 939.7 | 876.4 | 811.9 | 750.1 | 675.3
23_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 23 | ^ Tap 5 (W1) | 937 | 874.6 | 812 | 749.9 | 674.4
24_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 24 | Tap 1 (G) | 617.8 | 547.4 | 464.3 | 343.8 | 270.1
24_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 24 | Tap 2 (DS) | 617.2 | 546.9 | 469.4 | 351.3 | 272.8
24_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 24 | Tap 3 (Y1) | 778.5 | 719.8 | 632.8 | 549.1 | 441.1
24_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 24 | Tap 4 (Y2) | 939.7 | 876.4 | 811.9 | 750.1 | 675.3
24_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 24 | ^ Tap 5 (W1) | 937 | 874.6 | 812 | 749.9 | 674.4
29_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 29 | Tap 1 (G) | 617.8 | 547.4 | 464.3 | 343.8 | 270.1
29_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 29 | Tap 2 (DS) | 617.2 | 546.9 | 469.4 | 351.3 | 272.8
29_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 29 | Tap 3 (Y1) | 778.5 | 719.8 | 632.8 | 549.1 | 441.1
29_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 29 | Tap 4 (Y2) | 939.7 | 876.4 | 811.9 | 750.1 | 675.3
29_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 29 | ^ Tap 5 (W1) | 937 | 874.6 | 812 | 749.9 | 674.4
25_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 25 | Tap 1 (G) | 629.7 | 557.3 | 485.4 | 380.3 | 276.7
25_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 25 | Tap 2 (DS) | 629.6 | 555.9 | 483.1 | 378.3 | 277.4
25_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 25 | Tap 3 (Y1) | 803 | 718.8 | 639.6 | 576.2 | 521.3
25_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 25 | Tap 4 (Y2) | 981.3 | 909.2 | 832.7 | 765.7 | 705.4
25_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 25 | ^ Tap 5 (W1) | 984.3 | 908.7 | 836.7 | 768.9 | 709.3
30_208/240 V, 60 Hz, 1 ph. (ECM only)_1 | 30 | Tap 1 (G) | 629.7 | 557.3 | 485.4 | 380.3 | 276.7
30_208/240 V, 60 Hz, 1 ph. (ECM only)_2 | 30 | Tap 2 (DS) | 629.6 | 555.9 | 483.1 | 378.3 | 277.4
30_208/240 V, 60 Hz, 1 ph. (ECM only)_3 | 30 | Tap 3 (Y1) | 803 | 718.8 | 639.6 | 576.2 | 521.3
30_208/240 V, 60 Hz, 1 ph. (ECM only)_4 | 30 | Tap 4 (Y2) | 981.3 | 909.2 | 832.7 | 765.7 | 705.4
30_208/240 V, 60 Hz, 1 ph. (ECM only)_5 | 30 | ^ Tap 5 (W1) | 984.3 | 908.7 | 836.7 | 768.9 | 709.3
^ Factory setting for heating.

## Electrial data (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Unit Size | Electric Heating Capacity |  | Blower Amps (A) |  | Total Current (A) |  | Minimum Circuit Ampacity (A) |  | Maximum Circuit Breaker Size[2]
| (All have electric heat) | kW | BTUH | [6 empty] | Per Stage (A)
|  | 240[1] | 240[1] | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V | 208 V | 240 V
2-speed PSC motor_18_none | 18 | 0 | 0 | 1.25 | 1.25 | 1.25 | 1.25 | 1.5625 | 1.5625 | 15 | 15
2-speed PSC motor_18_3kW | 18 | 3 | 10236.426 | 1.25 | 1.25 | 12.0833 | 13.75 | 15.1042 | 17.1875 | 20 | 20
2-speed PSC motor_18_5kW | 18 | 5 | 17060.71 | 1.25 | 1.25 | 19.3056 | 22.0833 | 24.1319 | 27.6042 | 25 | 30
2-speed PSC motor_18_6kW | 18 | 6 | 20472.852 | 1.25 | 1.25 | 22.9167 | 26.25 | 28.6458 | 32.8125 | 30 | 35
2-speed PSC motor_18_8kW | 18 | 8 | 27297.136 | 1.25 | 1.25 | 30.1389 | 34.5833 | 37.6736 | 43.2292 | 40 | 45
2-speed PSC motor_19_none | 19 | 0 | 0 | 1.25 | 1.25 | 1.25 | 1.25 | 1.5625 | 1.5625 | 15 | 15
2-speed PSC motor_19_3kW | 19 | 3 | 10236.426 | 1.25 | 1.25 | 12.0833 | 13.75 | 15.1042 | 17.1875 | 20 | 20
2-speed PSC motor_19_5kW | 19 | 5 | 17060.71 | 1.25 | 1.25 | 19.3056 | 22.0833 | 24.1319 | 27.6042 | 25 | 30
2-speed PSC motor_19_6kW | 19 | 6 | 20472.852 | 1.25 | 1.25 | 22.9167 | 26.25 | 28.6458 | 32.8125 | 30 | 35
2-speed PSC motor_19_8kW | 19 | 8 | 27297.136 | 1.25 | 1.25 | 30.1389 | 34.5833 | 37.6736 | 43.2292 | 40 | 45
2-speed PSC motor_23_none | 23 | 0 | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 2.375 | 2.375 | 15 | 15
2-speed PSC motor_23_3kW | 23 | 3[2] | 10236.426 | 1.9 | 1.9 | 12.7333 | 14.4 | 15.9167 | 18 | 20 | 20
2-speed PSC motor_23_5kW | 23 | 5 | 17060.71 | 1.9 | 1.9 | 19.9556 | 22.7333 | 24.9444 | 28.4167 | 25 | 30
2-speed PSC motor_23_6kW | 23 | 6 | 20472.852 | 1.9 | 1.9 | 23.5667 | 26.9 | 29.4583 | 33.625 | 30 | 35
2-speed PSC motor_23_8kW | 23 | 8 | 27297.136 | 1.9 | 1.9 | 30.7889 | 35.2333 | 38.4861 | 44.0417 | 40 | 45
2-speed PSC motor_23_10kW | 23 | 10[3] | 34121.42 | 1.9 | 1.9 | 38.0111 | 43.5667 | 47.5139 | 54.4583 | 50 | 60
2-speed PSC motor_24_none | 24 | 0 | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 2.375 | 2.375 | 15 | 15
2-speed PSC motor_24_3kW | 24 | 3[2] | 10236.426 | 1.9 | 1.9 | 12.7333 | 14.4 | 15.9167 | 18 | 20 | 20
2-speed PSC motor_24_5kW | 24 | 5 | 17060.71 | 1.9 | 1.9 | 19.9556 | 22.7333 | 24.9444 | 28.4167 | 25 | 30
2-speed PSC motor_24_6kW | 24 | 6 | 20472.852 | 1.9 | 1.9 | 23.5667 | 26.9 | 29.4583 | 33.625 | 30 | 35
2-speed PSC motor_24_8kW | 24 | 8 | 27297.136 | 1.9 | 1.9 | 30.7889 | 35.2333 | 38.4861 | 44.0417 | 40 | 45
2-speed PSC motor_24_10kW | 24 | 10[3] | 34121.42 | 1.9 | 1.9 | 38.0111 | 43.5667 | 47.5139 | 54.4583 | 50 | 60
2-speed PSC motor_25_none | 25 | 0 | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 2.375 | 2.375 | 15 | 15
2-speed PSC motor_25_3kW | 25 | 3[2] | 10236.426 | 1.9 | 1.9 | 12.7333 | 14.4 | 15.9167 | 18 | 20 | 20
2-speed PSC motor_25_5kW | 25 | 5 | 17060.71 | 1.9 | 1.9 | 19.9556 | 22.7333 | 24.9444 | 28.4167 | 25 | 30
2-speed PSC motor_25_6kW | 25 | 6 | 20472.852 | 1.9 | 1.9 | 23.5667 | 26.9 | 29.4583 | 33.625 | 30 | 35
2-speed PSC motor_25_8kW | 25 | 8 | 27297.136 | 1.9 | 1.9 | 30.7889 | 35.2333 | 38.4861 | 44.0417 | 40 | 45
2-speed PSC motor_25_10kW | 25 | 10[3] | 34121.42 | 1.9 | 1.9 | 38.0111 | 43.5667 | 47.5139 | 54.4583 | 50 | 60
2-speed PSC motor_29_none | 29 | 0 | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 2.375 | 2.375 | 15 | 15
2-speed PSC motor_29_3kW | 29 | 3[2] | 10236.426 | 1.9 | 1.9 | 12.7333 | 14.4 | 15.9167 | 18 | 20 | 20
2-speed PSC motor_29_5kW | 29 | 5 | 17060.71 | 1.9 | 1.9 | 19.9556 | 22.7333 | 24.9444 | 28.4167 | 25 | 30
2-speed PSC motor_29_6kW | 29 | 6 | 20472.852 | 1.9 | 1.9 | 23.5667 | 26.9 | 29.4583 | 33.625 | 30 | 35
2-speed PSC motor_29_8kW | 29 | 8 | 27297.136 | 1.9 | 1.9 | 30.7889 | 35.2333 | 38.4861 | 44.0417 | 40 | 45
2-speed PSC motor_29_10kW | 29 | 10[3] | 34121.42 | 1.9 | 1.9 | 38.0111 | 43.5667 | 47.5139 | 54.4583 | 50 | 60
2-speed PSC motor_30_none | 30 | 0 | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 2.375 | 2.375 | 15 | 15
2-speed PSC motor_30_3kW | 30 | 3[2] | 10236.426 | 1.9 | 1.9 | 12.7333 | 14.4 | 15.9167 | 18 | 20 | 20
2-speed PSC motor_30_5kW | 30 | 5 | 17060.71 | 1.9 | 1.9 | 19.9556 | 22.7333 | 24.9444 | 28.4167 | 25 | 30
2-speed PSC motor_30_6kW | 30 | 6 | 20472.852 | 1.9 | 1.9 | 23.5667 | 26.9 | 29.4583 | 33.625 | 30 | 35
2-speed PSC motor_30_8kW | 30 | 8 | 27297.136 | 1.9 | 1.9 | 30.7889 | 35.2333 | 38.4861 | 44.0417 | 40 | 45
2-speed PSC motor_30_10kW | 30 | 10[3] | 34121.42 | 1.9 | 1.9 | 38.0111 | 43.5667 | 47.5139 | 54.4583 | 50 | 60
ECM Constant Torque Motor_18_none | 18 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_18_3kW | 18 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_18_5kW | 18 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_18_6kW | 18 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_18_8kW | 18 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_18_10kW | 18 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
ECM Constant Torque Motor_19_none | 19 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_19_3kW | 19 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_19_5kW | 19 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_19_6kW | 19 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_19_8kW | 19 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_19_10kW | 19 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
ECM Constant Torque Motor_23_none | 23 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_23_3kW | 23 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_23_5kW | 23 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_23_6kW | 23 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_23_8kW | 23 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_23_10kW | 23 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
ECM Constant Torque Motor_24_none | 24 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_24_3kW | 24 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_24_5kW | 24 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_24_6kW | 24 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_24_8kW | 24 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_24_10kW | 24 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
ECM Constant Torque Motor_25_none | 25 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_25_3kW | 25 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_25_5kW | 25 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_25_6kW | 25 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_25_8kW | 25 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_25_10kW | 25 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
ECM Constant Torque Motor_29_none | 29 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_29_3kW | 29 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_29_5kW | 29 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_29_6kW | 29 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_29_8kW | 29 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_29_10kW | 29 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
ECM Constant Torque Motor_30_none | 30 | 0 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 15 | 15
ECM Constant Torque Motor_30_3kW | 30 | 3[2] | 10236.426 | 2 | 2 | 12.8333 | 14.5 | 16.0417 | 18.125 | 20 | 20
ECM Constant Torque Motor_30_5kW | 30 | 5 | 17060.71 | 2 | 2 | 20.0556 | 22.8333 | 25.0694 | 28.5417 | 30 | 30
ECM Constant Torque Motor_30_6kW | 30 | 6 | 20472.852 | 2 | 2 | 23.6667 | 27 | 29.5833 | 33.75 | 30 | 35
ECM Constant Torque Motor_30_8kW | 30 | 8 | 27297.136 | 2 | 2 | 30.8889 | 35.3333 | 38.6111 | 44.1667 | 40 | 45
ECM Constant Torque Motor_30_10kW | 30 | 10[3] | 34121.42 | 2 | 2 | 38.1111 | 43.6667 | 47.6389 | 54.5833 | 50 | 60
[1] For 208 Volts use .751 correction factor for kW & MBTUH.
[2] 3 kW is not available in 25, 30 model
[3] 10 kW is not available in 18, 23 model

## Dim (hidden)
Unit size | A (in) | B (in) | C (in) | D (in) | E (in)
18_Uncased | 37 | 19.5 | 10.5 | N/A | N/A
23_Uncased | 37 | 19.5 | 10.5 | N/A | N/A
19_Uncased | 43 | 20.5 | 10.5 | N/A | N/A
24_Uncased | 43 | 20.5 | 10.5 | N/A | N/A
29_Uncased | 43 | 20.5 | 10.5 | N/A | N/A
25_Uncased | 49 | 20.5 | 10.5 | N/A | N/A
30_Uncased | 49 | 20.5 | 10.5 | N/A | N/A
18_Cased | 39.7 | 24 | 11 | 30.5 | 7
23_Cased | 39.7 | 24 | 11 | 30.5 | 7
19_Cased | 45.7 | 24 | 11 | 36.5 | 7
24_Cased | 45.7 | 24 | 11 | 36.5 | 7
29_Cased | 45.7 | 24 | 11 | 36.5 | 7
25_Cased | 51.7 | 24 | 11 | 42.5 | 7
30_Cased | 51.7 | 24 | 11 | 42.5 | 7

## All Slab (hidden)
Part Number | Series | Blower Motor | Airflow Config. | Slab No. | Metering Device | Unit Size | Line Voltage Connection | Electric Heat | Voltage | Revision | Refrigerant (R22 or R-410A) | Factory Installed metering device | Blower Data: Motor H.P. | Blower Data: F.L.A. @ 240 V | Nominal CFM | Max Unit Weight (lbs) | Available Voltages | Maximum Elec. Heat available (kW) | Transformer Size and Type | Refrigerant Conn. (IDS) Suction | Refrigerant Conn. (IDS) Liquid | Pallet Quantity (min order per model) | Custom.Case
CP1801C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HP031CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HP031UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A7HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A7HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HS001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HS001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP001CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP001UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP051CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP051UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP061CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP061UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP081CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP081UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A9HP101CA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A9HP101UA | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | A | R-410A | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2401A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2401A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2402A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2402A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2403A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2403A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2404A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2404A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HP031CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HP031UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2405A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2405A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2501A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2501A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2502A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2502A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2503A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2503A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2504A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2504A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2505A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2505A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2901A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2901A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2902A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2902A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2903A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2903A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2904A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2904A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2905A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2905A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005C9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005C9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3001A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3001A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3002A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3002A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3003A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3003A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3004A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3004A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A1HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A1HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Piston | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A7HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A7HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HS001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HS001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP001CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP001UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP051CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP051UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP061CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP061UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP081CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP081UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE3005A9HP101CA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE3005A9HP101UA | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-410A) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | A | R-410A | Non-bleed HP-A/C TXV | 1/4 | 2 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1801ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1801ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1802ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1802ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1803ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1803ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1804ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1804ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1805ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1805ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1901ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1901ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1902ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1902ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1903ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1903ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1904ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1904ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP1905ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP1905ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/8 | 1.25 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2301ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2301ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2302ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2302ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2303ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2303ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2304ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2304ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2305ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2305ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2401ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2401ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2402ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2402ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2403ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2403ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2404ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2404ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHP031CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHP031UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2405ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 100 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2405ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 24 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 38 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2501ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2501ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2502ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2502ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2503ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2503ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2504ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2504ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2505ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2505ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 25 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 800 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2901ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2901ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2902ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2902ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2903ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2903ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2904ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2904ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP2905ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 105 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP2905ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 29 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 70 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005C1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005C1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CBHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CBHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005CCHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005CCHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3001ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3001ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3002ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3002ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3003ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3003ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3004ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3004ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005A1HP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005A1HP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Piston (R-454B & R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Piston | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005AAHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005AAHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ABHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ABHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHS001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHS001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP001CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP001UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP051CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP051UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP061CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP061UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP081CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP081UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CP3005ACHP101CR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 108 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CP3005ACHP101UR | Sofit mount Series | 2-speed PSC motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 30 | Pull Disconnect | 10kW | 208/240 V, 60 Hz, 1 ph. (PSC only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/3 | 1.9 | 1000 | 73 | 208/240 V, 60 Hz, 1 Ph | 10kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1801ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1801ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1802ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1802ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1803ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1803ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1804ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1804ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1805ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1805ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 18 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1901ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1901ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1902ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1902ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1903ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1903ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1904ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1904ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-32) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE1905ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 100 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE1905ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Bleed HP-A/C TXV (R-454B) | 19 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 600 | 68 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305C1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305C1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CBHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CBHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CBHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CBHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CBHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CBHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CBHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CBHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CBHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CBHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CBHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CBHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CCHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CCHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CCHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CCHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CCHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CCHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CCHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CCHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CCHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CCHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305CCHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305CCHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05C | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2301ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2301ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 01A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2302ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2302ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 02A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2303ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2303ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 03A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304AAHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304AAHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304AAHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304AAHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304AAHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304AAHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304AAHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304AAHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304AAHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304AAHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ABHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ABHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ABHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ABHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ABHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ABHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ABHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ABHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ABHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ABHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ABHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ABHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Non-bleed HP-A/C TXV (R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-32 | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ACHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ACHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ACHP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ACHP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ACHP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ACHP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ACHP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ACHP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ACHP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ACHP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2304ACHP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2304ACHP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 04A | Bleed HP-A/C TXV (R-454B) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP031CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP031UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 3kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP051CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP051UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 5kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP061CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP061UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 6kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305A1HP081CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305A1HP081UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Piston (R-454B & R-32) | 23 | Pull Disconnect | 8kW | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Piston | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased
CE2305AAHS001CR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 92 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Cased
CE2305AAHS001UR | Sofit mount Series | ECM Constant Torque Motor | Horizontal | 05A | Non-bleed HP-A/C TXV (R-454B) | 23 | Stripped Wire | none | 208/240 V, 60 Hz, 1 ph. (ECM only) | Refrigerant Detection System | R-454B | Non-bleed HP-A/C TXV | 1/4 | 2 | 800 | 63 | 208/240 V, 60 Hz, 1 Ph | 8kW | 40VA, Class 2 | 3/4 | 3/8 | 8 | Uncased